## Update Information
Working Database and Model
Revision Status
Last Revision: |  | 2001-05-21
Todays Date: |  | 2014-03-12
Please Contact NZWWA for a Replacement Working Version
Total Detn = | 0.2269 |  | x Sample Age
Surge Pressure = | 1.5 |  | x Operating Pressure

## Database
| Working Database |  |  | Enter the data in here and then refer to The Lifetime prediction model tab for the results.
Local Authority | Location Description | City/Town | Pipe DN (mm) | Mean Pipe OD (mm) | Min. Pipe Wall Thickness (mm) | Pipe Specific Gravity | Working Pressure (m) | Max. External Det'n (mm) | Max. Internal Det'n (mm) | Total Det'n (mm) | Water Absorp. (%) | Bench Burst Press. (m) | Average Ext. Barcol Hardness | Average Int. Barcol Hardness | Year of installation | Year of Appraisal | Sample Age
Example 1 | Street 1 | Town 1 | 100 | 127 | 17.7 | 1.98 | 58 | 2 | 1 | 3 | 7.9 | 826.2335 | 20 | 30 | 1961 | 1999 | 38
Example 2 | Street 2 | Town 2 | 100 | 124.1 | 11 | 1.56 | 47 | 3 | 3.5 | 6.5 | 24.6 | 214.833 | 40 | 0 | 1960 | 1999 | 39
|  |  | 600 | 667 | 45.7 |  | 91 | 8.2 | 5.1 | 13.3 | WA | BBP | Ext BH | Int BH | 1968 | 2011 | 43
|  |  | 600 | 673 | 48.6 |  | 91 | 8.2 | 5.1 | 13.3 | WA | BBP | Ext BH | Int BH | 1968 | 2011 | 43
|  |  | 525 | 588 | 42 |  | 20 | 7 | 5 | 12 | WA | BBP | Ext BH | Int BH | 1968 | 2011 | 43
|  |  | 525 | 588 | 42 |  | 40 | 7 | 5 | 12 | WA | BBP | Ext BH | Int BH | 1968 | 2011 | 43
NOTE
Refer Section 2 - National AC Watermain Database and Lifetime Prediction Model - Development and Application, page 2.5, for using the Working Database and Model
Copy spreadsheets from CD to utilise the Working Database and Model

## Lifetime Prediction Model
| Lifetime Prediction Model | [10 empty] | Note: The Formula in Column N is: | (M6*F6)/((2*23.5)+M6) |  |  | The term 23.5MPa in (2*23.5) relates to Pipes to NZS 3202:1977. For pipes between 1959 and 1976 use 22.1MPa and for pre 1959 pipes use 15.5MPa
| Note; the spreadsheet does not allow for lifetimes of over 100 years. Change the formula in column S to change this condition | [9 empty] | Working Pressure + Surge (MPa) in column M uses the default factor of 1.5 in cell 11D on the update information tab. If you have datalogged information on pressures, reduce the factor to suit - if there is a reasonably long record and few "surges" then the factor can be reduced as low as 1.2.
Input from National Data Base | [9 empty] | Calculations Based on Sample Data |  |  |  | Deterioration Model Output |  |  | Lifetime Prediction Model Output
Local Authority | Location Description | City/Town | Pipe DN (mm) | Mean Pipe OD (mm) | Min. Pipe Wall Thickness (mm) | Working Pressure (m) | Total Det'n (mm) | Year of installation | Year of Appraisal | Sample Age (years) | Working Pressure + Surge (MPa) | Minimum Undeteriorated Wt before failure (mm) | Total Det'n Causing Failure (mm) | Sample Det'n Rate (mm/year) | Modelled Det'n (mm) | Comparison with National Average | Estimated Pipe Life (years) | Estimated Year of First Det'n Failure
Example 1 | Street 1 | Town 1 | 100 | 127 | 17.7 | 58 | 3 | 1961 | 1999 | 38 | 0.85164 | 2.2603 | 15.4397 | 0.078947 | 8.6222 | -65.21% | 100 | 2061
Example 2 | Street 2 | Town 2 | 100 | 124.1 | 11 | 47 | 6.5 | 1960 | 1999 | 39 | 0.69012 | 1.7959 | 9.2041 | 0.16667 | 8.8491 | -26.55% | 55.2249 | 2015.2249
0 | 0 | 0 | 600 | 667 | 45.7 | 91 | 13.3 | 1968 | 2011 | 43 | 1.0244 | 15.1088 | 30.5912 | 0.3093 | 9.7567 | 36.32% | 98.9038 | 2066.9038
0 | 0 | 0 | 600 | 673 | 48.6 | 91 | 13.3 | 1968 | 2011 | 43 | 1.0244 | 15.2447 | 33.3553 | 0.3093 | 9.7567 | 36.32% | 107.8404 | 2075.8404
0 | 0 | 0 | 525 | 588 | 42 | 20 | 12 | 1968 | 2011 | 43 | 0.23494 | 2.9246 | 39.0754 | 0.27907 | 9.7567 | 22.99% | 140.0203 | 2108.0203
0 | 0 | 0 | 525 | 588 | 42 | 40 | 12 | 1968 | 2011 | 43 | 0.46987 | 5.8202 | 36.1798 | 0.27907 | 9.7567 | 22.99% | 129.6442 | 2097.6442
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!