## Workshop 3 3-Waters Vol 1
NZAMS - Sector Feedback - Final Version (Workshop 3 3-Waters Vol 1) | [7 empty] | #REF!
ID | Standard | Volume | Feedback | Status Included, Excluded, Sector discussion, Noted: no action required | Final Comments for Publication | Section Reference in Final Version - per Contents page | Additional Work | Proposed Codelists / Attributes | Workshop Outcome LINZ notes 1/2 MAY | Notes / Updates | Ref | Workshop Outcomelinz notes 23/24 MAY | Who to do | Actions taken By whom and when | ACTION TAKEN
1 | Potable water | Vol 2 | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Completed with Metaconnect | No Specific Reference | No action
2 | Potable water | Vol 2 | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Included | Completed with Metaconnect | No Specific Reference | No action
3 | Potable water | Vol 2 | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Included | Completed with Metaconnect | No Specific Reference | No action
4 | Buildings | Vol 2 | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Included | Completed with Metaconnect | No Specific Reference | No action
5 | Stormwater | Vol 2 | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | Completed with Metaconnect | No Specific Reference | No action
6 | Stormwater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
7 | Wastewater | Vol 2 | Should be "coordinate reference system" as in ISO 19111 | Included | Standards are OGC spatial attribution compliant | Use of the Specification | No action
8 | Wastewater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
9 | Potable water | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | not required in this section, covered in later sections | Use of the Specification | No action
10 | Potable water | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
11 | Potable water | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
12 | Potable water | Vol 1 | or vertical datum | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
13 | Potable water | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | changed precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | Change made document updated
14 | Buildings | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
15 | Buildings | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
16 | Stormwater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
17 | Stormwater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
18 | Stormwater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
19 | Stormwater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
20 | Wastewater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Updated in draft standards | Use of the Specification | No action
21 | Wastewater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
22 | Wastewater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
23 | Wastewater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Updated in draft standards | 2.1.2 Projections and Datums | Change made document updated
24 | Wastewater | Vol 1 | Update to NZVD2016 | Included | Updated in draft standards | Glossary | Change made document updated
25 | 3-Waters | Vol 1 & Vol 2 | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General | No action
26 | 3-Waters | Vol 1 & Vol 2 | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Noted: no action required | Reviewed and Noted only | General | No action
27 | 3-Waters | Vol 1 & Vol 2 | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference | No action
28 | 3-Waters | Vol 1 & Vol 2 | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | Included | The drafts have now had a full publishing edit | General | Change made document updated
29 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Noted: no action required | The adoption of extents of fields is determined by each organisation To be also reviewed during pilot implementation phase | General | No action
30 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General | No action
31 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General | No action
32 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | Noted: no action required | Future work is yet to be determined | General | No action
33 | 3-Waters | Vol 1 & Vol 2 | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | Included | The classification has been defined in the Standards. Modifications have been made to resolve inconsistencies | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
34 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | Included | The classification has been defined in the Standards Code Lists included | General | No action
35 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | Included | The classification has been defined in the Standards | General | No action
36 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | Included | Asset Classifications have been defined in the Standards. The Group classification is at a high level the asset classes have then been identified under the groups Code Lists included | General | No action
37 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy | No action
38 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Noted: no action required | The adoption of extents of fields is determined by each organisation Each and every organisation can apply their specific requirements after the data is received. | General for Hierarchy | No action
39 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference | No action
40 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference | No action
41 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics | No action
42 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums | No action
44 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Included | Suggestion adopted. Change made documents updated | General | Change made document updated
45 | 3-Waters | Vol 1 & Vol 2 | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Noted: no action required | Organisations may map the full name into their systems from the Code lists supplied | General | No action
46 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Noted: no action required | Reviewed and Noted only | General | No action
47 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Included | Photographic Evidence is an optional attribute | General | change made document updated
48 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Sector Discussion | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General | New Code List proposed | Health & Safety Type | Codelist proposed | Modified 'Hlth_Sfty' from a free text field to a codelist To be modified in all the 3 Waters and BH documents
49 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Included | Suggestion adopted. Change made documents updated | General | Change made document updated
50 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | No action
51 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | No action
52 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | Included | Code lists included in standards | 2.3.3 Retaining Structure | No action
53 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Sector Discussion | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | No action |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required
54 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | refer notes volume 2 | GISSA Remove Valves from Mechanical Equipment asset class code list Create updated valve table from discussion with Michael | Valve removed from codelists of mechanical equipment in WW - GH 25/6/17 SW - GH 25/6/17 PW - GH 25/6/17 Updated Valve table in all 3W docs MW 23/06/2017 | Changes made to all 3Waters documents Valve removed from codelist of Mechanical equipment Purpose - Attribute and Codelist already exists Valve table modified with new attributes and associated codelists Attribute - Valve Powered By Codelist - Valve Power Attibute - Valve Configuration Codelist - Valve Configuration
55 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Noted: no action required | These standards have not considered Treatment Plants | General | No action
56 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | Included | Code lists included in standards Pump has been removed from Mechanical Equipment as it is an asset class in its own right | General Equipment | Gauge input from next review |  |  | No further action required
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | refer notes volume 2 | Michael to add new codes from Tauranga email No other action required for the additional attributes | Email from Tauranga followed. - Some attributes included - new codes added New codes added - MW 23/06/2017 | Attributes added Mechanical Equipment Asset Class - Weight - Current Maximum Rating - Output Rating - Power Rating - IP Rating Instrument Asset Class - Capacity Time - IP Rating - Current Maximum Rating Electrical Equipmentr Asset Class - Current Maximum Rating - Capacity Time - Output Rating - Power Rating - IP Rating - Weight New codes added Operation/redundancy strategy - out of scope of Volume 1
58 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments | No action
59 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | Gauge input from next review
60 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General | No action
61 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | Change made document updated
62 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | Change made document updated
63 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA) |  | Created new attribute field and code list OMA To be included in all the 3 Waters documents
64 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | Noted: no action required | Resolved in updated version | 2.5.1 Equipment | Change made document updated
65 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option | include as optional | Created new attribute field Rig_Flex To be included in all the 3 Waters documents
66 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision |  | include the testing types as optional (new code list) | Created new attribute field and code list Testing Type To be included in all the 3 Waters documents
67 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision |  | include the testing types as optional (new code list) | see above
68 | Stormwater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | AddCCTV & Laser Profiling testing to code list testing type | General | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling |  | Duplicate
69 | Stormwater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Sector Discussion | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | New attribute proposed | Installer of Asset | include | Created new attributes for Installer, Installer Warranty, Manufacturer Warranty To be included in all the 3 Waters documents
70 | Stormwater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Sector Discussion | Reviewed and Noted for Inclusion | 2.3.4 Pipe | More information required for a decision |  | yes, include code lists | Added to new code list Test Type
71 | Stormwater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | General | New Code List entry for Condition Assessment Type proposed | Deflection Test |  | DUPLICATE see ID66
72 | Stormwater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
73 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation | yes, include code lists | Added to new code list Test Type
74 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation | yes, include code lists | Added to new code list Test Type
75 | Stormwater | Vol 1 | Deflection Test result | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | New Code List entry for Condition Assessment Type proposed | Compaction Test |  | DUPLICATE see ID66
76 | Stormwater | Vol 1 | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | include as optional | Created new attributes and associated codelists Frame Class Cover Class Seal Type To be included in all the 3 Waters documents
77 | Stormwater | Vol 1 | Seal Access Safety | Sector Discussion | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber | New Code List & entries proposed | Health & Safety Type | close | DUPLICATE
78 | Stormwater | Vol 1 | Manufacturer Manufacturing Standard Third Party QA Accreditation | Sector Discussion | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion | include as optional | Created new attributes Manufacturer Manufacturing Standard Third Party QA Accreditation The year of the standard is recorded as party of the Standard used To be included in all the 3 Waters documents
79 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.4.4 Pipe | New attribute proposed | Rigid or Flexible as option | close | DUPLICATE
80 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling |  | Created attribute field "Observed" to enable recording of results To include in all the 3 Waters documents
81 | Stormwater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | Additional entries included in Code list Condition Assessment Type |  | close | Create attribute field "Observation" to enable recording of results To include in all the 3 Waters documents
82 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling |  | DUPLICATE see 80
83 | Stormwater | Vol 1 | Rigid material standard and QA Separate Flexible material standard and it's QA | Sector Discussion | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA | close | Created new attributes Rigid Materil Standard Rigid Material Accreditation Flexible Material Standard Flexible Material Quality Accreditation To be included in all the 3 Waters documents
84 | Stormwater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test |  | DUPLICATE see 75
85 | Stormwater | Vol 1 | Compaction strength per NZS4566.2 | Sector Discussion | More information required for a way forward | 2.4.4 Pipe | More information required for a decision |  | observation | Created attribute field "Observation" to enable recording of results To include in all the 3 Waters documents
86 | Stormwater | Vol 1 | Third Party QA for pipe material manufacturer | Sector Discussion | Third Party QA Accreditation to code lists | 2.4.4 Pipe | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list | close | DUPLICATE
87 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option |  | DUPLICATE see 65
88 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing |  | DUPLICATE see 80
89 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing |  | DUPLICATE see 80
90 | Wastewater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling |  | DUPLICATE see 68
91 | Wastewater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments | New attribute proposed | Installer of Asset |  | DUPLICATE see 69
92 | Wastewater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | New attribute created 'Observed' Includes results from - Deflection testing - Laser profiling |  | DUPLICATE see 80
93 | Wastewater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | 1.7 Heirarchy | Create entries Desktop Visual cctv laser etc |  |  | DUPLICATE see 92
94 | Wastewater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
95 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
96 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
97 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option | Close | DUPLICATE
98 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
99 | Wastewater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | More information is required to inform a way forward | 2.3.4 Pipe | More information required for a decision |  | Close | DUPLICATE
100 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling |  | DUPLICATE
101 | Wastewater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Reulsts to be included in attribute 'Observed' Compaction Test per NZ4566.2 Foundation strength pre-install
102 | Wastewater | Vol 1 | Compaction strength per NZS4566.2 or NZS3725 | Sector Discussion | More information required for a way forward | 2.3.4 Pipe | More information required for a decision |  | Close | see #85
103 | Wastewater | Vol 1 | Third Party QA for pipe material manufacturer | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion |  | DUPLICATE
104 | Stormwater | Vol 1 | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure | More information required for a decision |  | chase up to get pdf (Haydn) | Morphum Environmental Ltd provided this feedback. Auckland Stormwater have been heavily involved in the standard from Day 1, and the compromises made made have been agreed to by all parties. | N/A
105 | Stormwater | Vol 1 | Spillway should be its own Asset Class | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure | More information required for a decision |  | Close | Discussed during the May 1-3 workshops Determined that this can be addressed by the asset owner as a post process
106 | Stormwater | Vol 1 | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles | More information required for a decision |  | close, refer to Roading Standards Gissa to follow up on Giabon | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - Nina to provide a codelist for incorporation into the standards. George needs to check that any update is consistent with how the Roading Standard treats this area. Graeme to check ChCh information on this. | GISSA George to call | Email sent for conference call btn Nina, Graham and Mark Watercourse - out of scope Forebay bund - included as Embankment type Bridge - part of Roading Maintenance track - - part of Roading Fence - part of Roading Viewing platform - part of Roading Gabion basket- part of Roading (retaining wall type) Roading standard refer to TAGG | Email sent for conference call btn Nina, Graham and Mark Watercourse - out of scope Forebay bund - included as Embankment type Bridge - part of Roading Maintenance track - - part of Roading Fence - part of Roading Viewing platform - part of Roading Gabion basket- part of Roading (retaining wall type) Roading standard refer to TAGG
107 | Stormwater | Vol 1 | Source for what? This should have more detail. | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | Change made document updated
108 | Stormwater | Vol 1 | Does this include forebay bunds and pond banks associated with ponds? | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks | include new code list | Added Forebay Bund and Pond Bank to code list EMBANKMENT TYPE Weir spelling corrected Carried out post publication of 23 MAY documents
109 | Stormwater | Vol 1 | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure | More information required for a decision |  | close | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: -
110 | Stormwater | Vol 1 | Bathymetry Attribute? | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | Haydn suggest this is excluded as I think it can be sourced from LINZ
111 | Buildings | Vol 1 | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable | Noted: no action required | Reviewed and Noted only | General | No action
112 | Buildings | Vol 1 | The Hierarchy table works well | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy | No action
113 | Buildings | Vol 1 | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. | Sector Discussion | Reviewed and Noted only for discussion | General | No action
114 | Buildings | Vol 1 | Complex requirement for such a large property portfolio | Noted: no action required | Reviewed and Noted only | General | No action
115 | Buildings | Vol 1 | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles | No action
116 | Buildings | Vol 1 | This is a huge task for as constructed / as built for a large portfolio | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
117 | Buildings | Vol 1 | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | Reviewed and Noted only | General | No action
118 | Buildings | Vol 1 | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General | No action
119 | Buildings | Vol 1 | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | No action
120 | Buildings | Vol 1 | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes | More information required for a decision
121 | Buildings | Vol 1 | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) | Noted: no action required | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General | No action
122 | Buildings | Vol 1 | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
123 | Buildings | Vol 1 | V_Proc  what is this and what is it to relate to? | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
124 | Buildings | Vol 1 | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? | Included | Tables will be referenced in Final Versions | General | No action
125 | Buildings | Vol 1 | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 | More information required for a decision
126 | Buildings | Vol 1 | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof | More information required for a decision
127 | Buildings | Vol 1 | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision
128 | Buildings | Vol 1 | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision
129 | Buildings | Vol 1 | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone | Noted: no action required | This detail is to be provided at the time it was built not at time of capture This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint | No action
130 | Buildings | Vol 1 | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
131 | Buildings | Vol 1 | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint | Change made document updated
132 | Buildings | Vol 1 | Graffiti  irrelevant | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint | No action
133 | Buildings | Vol 1 | Flood  applicable only in related areas, and this information is on local council records | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint | No action
134 | Buildings | Vol 1 | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint | No action
135 | Buildings | Vol 1 | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint | No action
136 | Buildings | Vol 1 | Design life how is this applied to existing property | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
137 | Buildings | Vol 1 | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling | No action
138 | Buildings | Vol 1 |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
139 | Buildings | Vol 1 | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling | No action
140 | Buildings | Vol 1 | Finish  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
141 | Buildings | Vol 1 | Finish condition assessment, condition and repairs  ✓ The rest is superfluous | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
142 | Buildings | Vol 1 | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satisfy both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling | No action
143 | Buildings | Vol 1 | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
144 | Buildings | Vol 1 | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
145 | Buildings | Vol 1 | Design life  If new = Ok | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
146 | Buildings | Vol 1 | Cost  Not needed? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
147 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
148 | Buildings | Vol 1 | Too much detail required for ceilings. Condition, material, surface finish = Yes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
149 | Buildings | Vol 1 | Risk, Resilience, and Financial performance  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
150 | Buildings | Vol 1 | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
151 | Buildings | Vol 1 | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling | More information required for a decision
152 | Buildings | Vol 1 | Smoke_Barr  Smoke relevant to multiunit development only. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
153 | Buildings | Vol 1 | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling | Change made document updated
154 | Buildings | Vol 1 | Des_Life - ? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
155 | Buildings | Vol 1 | Cost ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
156 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
157 | Buildings | Vol 1 | Whole page  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
158 | Buildings | Vol 1 | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor | No action
159 | Buildings | Vol 1 | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
160 | Buildings | Vol 1 | Live load rating of floor à too difficult to define | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
161 | Buildings | Vol 1 | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
162 | Buildings | Vol 1 | Repairs and Maintenance à what’s the need for this? | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema | No action
163 | Buildings | Vol 1 | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference | No action
164 | Buildings | Vol 1 | First 5 rows à Very detailed for residential use. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
165 | Buildings | Vol 1 | Bracing is as per ceiling notes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
166 | Buildings | Vol 1 | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision
167 | Buildings | Vol 1 | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision
168 | Buildings | Vol 1 | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
169 | Buildings | Vol 1 | Third row à Maybe | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
170 | Buildings | Vol 1 | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
171 | Buildings | Vol 1 | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
172 | Buildings | Vol 1 | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
173 | Buildings | Vol 1 | Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
174 | Buildings | Vol 1 | - Multi storey application only. Too much detail required. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
175 | Buildings | Vol 1 | Last 5 yellow rows à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
176 | Buildings | Vol 1 | - 2nd row à ? Building Code complaint for new works. Unknown for much existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
177 | Buildings | Vol 1 | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
178 | Buildings | Vol 1 | Thermal barrier à ? Floor insulation is all that is relevant in residential. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
179 | Buildings | Vol 1 | All pages à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
180 | Buildings | Vol 1 | Whole page à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
181 | Buildings | Vol 1 | Acoustic row, content  maybe Cost  X Rest of page  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
182 | Buildings | Vol 1 | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
183 | Buildings | Vol 1 | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
184 | Buildings | Vol 1 | Whole page  undefinable in existing housing. | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
185 | Buildings | Vol 1 | Vents  ✓ Membrane rows  Define what membrane? | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation | No action
186 | Buildings | Vol 1 | Foundation area, content à ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation | No action
187 | Buildings | Vol 1 | à See previous foundation notes | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision
188 | Buildings | Vol 1 | All pages à ✕ | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision
189 | Buildings | Vol 1 | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof | No action
190 | Buildings | Vol 1 | Load wind/fix  Not known in existing stock | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof | No action
191 | Buildings | Vol 1 | Frame_Tr  not always identifiable Frame_ Sp  why? | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
192 | Buildings | Vol 1 | Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
193 | Buildings | Vol 1 | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
194 | Buildings | Vol 1 | Last 3 rows  Is this needed and how is it defined? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
195 | Buildings | Vol 1 | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
196 | Buildings | Vol 1 | First row, QA Validation  N/A needs to be applied here | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof | No action
197 | Buildings | Vol 1 | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
198 | Buildings | Vol 1 | Last 5 rows  as per previous notes | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
199 | Buildings | Vol 1 | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
200 | Buildings | Vol 1 | Whole page  ✓ apart from: Cost row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
201 | Buildings | Vol 1 | First 3 rows  ? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
202 | Buildings | Vol 1 | Last row, QA validation à Critical | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof | More information required for a decision
203 | Buildings | Vol 1 | Risk  ✓ Resil, Des_Perf  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
204 | Buildings | Vol 1 | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
205 | Buildings | Vol 1 | Whole page à ✓ Apart from Cost row à ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
206 | Buildings | Vol 1 | First 3 rows à? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
207 | Buildings | Vol 1 | critically, QA Validation à Critical | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
208 | Buildings | Vol 1 | All 3 rows  ? Row 3  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
209 | Buildings | Vol 1 | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
210 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
211 | Buildings | Vol 1 | All 4 rows  ✕, ?, ?, ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
212 | Buildings | Vol 1 | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
213 | Buildings | Vol 1 | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | No action
214 | Buildings | Vol 1 | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
215 | Buildings | Vol 1 | Whole page à✕. Risk – could relate to a water risks | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
216 | Buildings | Vol 1 | Whole page à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
217 | Buildings | Vol 1 | Classifications, Masterpec, Enclosure à not sure what this is representing? | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof | No action
218 | Buildings | Vol 1 | Ins-Type, R_Value à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
219 | Buildings | Vol 1 | Whole page  ✓ Insulation installer and warranty  maybe | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
220 | Buildings | Vol 1 | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
221 | Buildings | Vol 1 | Whole pink pages/part  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
222 | Buildings | Vol 1 | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls | No action
223 | Buildings | Vol 1 | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
224 | Buildings | Vol 1 | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
225 | Buildings | Vol 1 | Grout and Wall Structure Joint  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
226 | Buildings | Vol 1 | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
227 | Buildings | Vol 1 | Condition  ✓ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
228 | Buildings | Vol 1 | Structure, Bracing à As per floor and roof bracing | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
229 | Buildings | Vol 1 | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
230 | Buildings | Vol 1 | Wall, Design Life à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
231 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
232 | Buildings | Vol 1 | Fire barrier à Multiunit. May not be known on existing stock | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
233 | Buildings | Vol 1 | Orange à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
234 | Buildings | Vol 1 | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
235 | Buildings | Vol 1 |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor | No action
236 | Buildings | Vol 1 | Whole page à why would we use this information? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
237 | Buildings | Vol 1 | Acoustic and Thermal rating à Not used. Where applicable? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
238 | Buildings | Vol 1 | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor | No action
239 | Buildings | Vol 1 | à Why / how would we use this? Too much information required. | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs | No action
240 | Buildings | Vol 1 | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs | No action
241 | Buildings | Vol 1 | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
242 | Buildings | Vol 1 | Pages  ✕ | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
243 | Buildings | Vol 1 | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision
244 | Buildings | Vol 1 | Framed and Frame material à not defined in window anatomy page 149 | Sector Discussion | Update diagram on p149 | 2.5.3 Windows | Modify Diagram
245 | Buildings | Vol 1 | Height of windows in mm à what value? | Noted: no action required | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | No action
246 | Buildings | Vol 1 | Condition  ✓ Width  why needed? | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision
247 | Buildings | Vol 1 | Manufacturer, warranty, installation date, installer àUnknown on existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
248 | Buildings | Vol 1 | Design life à How to define? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
249 | Buildings | Vol 1 | Repairs à ? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
250 | Buildings | Vol 1 | Page à✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
251 | Buildings | Vol 1 | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
252 | Buildings | Vol 1 | Hardware à Locks, Yes. Lever/knobs maybe. | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
253 | Buildings | Vol 1 | Whole Column Name – Full is circled à Not always known on existing. Why needed? | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows | No action
254 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
255 | Buildings | Vol 1 | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | No action
256 | Buildings | Vol 1 | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
257 | Buildings | Vol 1 | Services, pink section àmore commercial application. | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
258 | Buildings | Vol 1 | à No! How is this captured realistically and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components | No action
259 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
260 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
261 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
262 | Buildings | Vol 1 | à Would we use this at a per item attribute? | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
263 | Buildings | Vol 1 | Type à ✓ Last row, content à NA | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
264 | Buildings | Vol 1 | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
265 | Buildings | Vol 1 | àToo difficult and unnecessary info | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
266 | Buildings | Vol 1 | à Stove have heater fans | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment | No action
267 | Buildings | Vol 1 | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment | No action
268 | Buildings | Vol 1 | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment | No action
269 | Buildings | Vol 1 | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) | No action
270 | Buildings | Vol 1 | Pink section  Not sure how much of this is required/useful | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) | No action
271 | Buildings | Vol 1 | Blue section - ✓ | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings | No action
272 | Buildings | Vol 1 | Asset type à ✓ Kitchen Vanities in contents | Included | Add to codelist | 2.7.4 Fixtures & Fittings | New Code List entry for Fittings Type proposed | Kitchen Vanities
273 | Buildings | Vol 1 | Length, Height, Width à Why? | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings | More information required for a decision
274 | Buildings | Vol 1 | Whole page à Doubt this would be known | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings | No action
275 | Buildings | Vol 1 | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) | No action
276 | Buildings | Vol 1 | à Covered in Building WOF. *Specialist area = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components | No action
277 | Buildings | Vol 1 | àSpecialists information and only applicable to multi-unit/storey complexes. | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts | No action
278 | Buildings | Vol 1 | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. | Noted: no action required | Reviewed and Noted only | 2.7.9 Security | No action
279 | Buildings | Vol 1 | à Not so useful in residential and difficult to maintain/update. | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage | No action
280 | Buildings | Vol 1 | à Not really applicable to existing housing. Maybe some use in multi-unit development. | Noted: no action required | Reviewed and Noted only | 2.8.1 Space | No action
281 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
282 | Buildings | Vol 1 | à ✕ | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | No action
283 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
284 | Buildings | Vol 1 | Material à ✓ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
285 | Buildings | Vol 1 | Pipe type à ✕ | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data | No action
286 | Buildings | Vol 1 | Water type à ? | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data | No action
287 | Buildings | Vol 2 | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference | No action
288 | Buildings | Vol 2 | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Included | Edited to make clearer | No Specific Reference | Change made document updated
289 | Buildings | Vol 2 | This document excludes industrial buildings and Ancillary building’s  provide examples | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
290 | Buildings | Vol 2 | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
291 | Buildings | Vol 2 | Added Laundry to Outbuildings, included in the Residential standard | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
292 | Buildings | Vol 2 | The bullet points à are they attributes or measures? | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | Haydn
293 | Buildings | Vol 2 | What is Boolean data type? | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type | No action
294 | Buildings | Vol 2 | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | Change made document updated
295 | Buildings | Vol 2 | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | no action
296 | Buildings | Vol 2 | The third and fourth suite of analytics à seems very granular? | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
297 | Buildings | Vol 2 | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | References are being considerd | No Specific Reference | No action
298 | Buildings | Vol 2 | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | Haydn
299 | Buildings | Vol 2 | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference | No action
300 | Buildings | Vol 2 | Table 4. à unclear what this actually shows? | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas | No action
301 | Buildings | Vol 2 | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | No action
302 | Buildings | Vol 2 | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Included | Updated in draft Standards | Code List 16: Condition Rating | No action
303 | Buildings | Vol 2 | Operations definition à What does this mean? Is this routine/preventative maintenance? | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
304 | Buildings | Vol 2 | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
305 | Buildings | Vol 2 | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
306 | Buildings | Vol 2 | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Sector Discussion | Mandatory / Optimal and Optional will be discussed | No Specific Reference | No action
307 | Buildings | Vol 2 | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) | No action
308 | Buildings | Vol 2 | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
309 | Buildings | Vol 2 | 1st bullet point à E.g. roof? Fire alarms? | Noted: no action required | Can be as granular as needed. | No Specific Reference | No action
310 | Buildings | Vol 2 | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Included | Updated in Draft Standards | No Specific Reference | Haydn
311 | Buildings | Vol 2 | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference | No action
312 | Buildings | Vol 2 | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
313 | Buildings | Vol 2 | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | No action
314 | Buildings | Vol 2 | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
315 | Buildings | Vol 2 |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
316 | Buildings | Vol 2 | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes | No action
317 | Buildings | Vol 2 | Code G, Malicious damage à Does this include tenant damage? | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
318 | Buildings | Vol 2 | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating | No action
319 | Buildings | Vol 2 |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating | No action
320 | Buildings | Vol 2 |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference | No action
321 | Buildings | Vol 2 |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
322 | Buildings | Vol 2 |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema | No action
323 | Buildings | Vol 2 | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference | No action
324 | Buildings | Vol 2 | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Noted: no action required | No action required. Understood. | No Specific Reference | No action
325 | Buildings | Vol 2 | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | Haydn
326 | Buildings | Vol 2 | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element | To discuss with technical Working Groups
327 | Buildings | Vol 2 | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Noted: no action required | The attribute is optional. | No Specific Reference | No action
328 | Buildings | Vol 2 | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference | No action
329 | Buildings | Vol 2 | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference | No action
330 | Buildings | Vol 2 | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Noted: no action required | These are at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists | No action
331 | Potable water | Vol 1 | Add USB memory sticks/hard drives to this list. | Included | Changed in all documents | 1.5 Deliverables | Change made document updated
332 | Potable water | Vol 1 | Question: Are there requirements for developers to retain information after transmission? | Noted: no action required | We see this as something for the developer to make the call if they retain a copy or not. | 1.5 Deliverables | No action
333 | Potable water | Vol 1 | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. | Excluded | Keeping current practice. | 2.1.5 Attribute Data Fields | No action |  | date fields need to be date fields | Discussed during the May 1-3 workshops Noted no further discussion or action required
334 | Potable water | Vol 1 | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. | 2.1.10 Common Attributes | No action
335 | Potable water | Vol 1 | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters | 2.2.1 Area of Work Extent | More information required for a decision |  | fine to use locally, not to be included in standards so that they remain system agnostic | Alphanumeric, also known as alphameric, simply refers to the type of Latin and Arabic characters representing the numbers 0 - 9, the letters A - Z (both uppercase and lowercase), and some common symbols such as '@' '#' '&' and '_' Typically "-" and "/" are not accepted charactes in the Alpha Numeric range for file naming. However it weill be the responsibility of each organisation to determine the most appropriate naming convention suitable for their systems
336 | Potable water | Vol 1 | For circular assets, should length and width both be populated and be the same (diameter)? | Included | For circular assets, length is not required and will be made conditional | 2.3.1 Containment Structure | Change made document updated
337 | Potable water | Vol 1 | Rename to Length Metres for consistency | Included | Changed all instances to length metres and length millimetres as appropriate | 2.3.1 Containment Structure | Change made document updated
338 | Potable water | Vol 1 | Overflow = OS? What does OS stand for? Should this be OF? | Noted: no action required | This term was agreed to by the TWG, retained | 2.3.1 Containment Structure | No action
339 | Potable water | Vol 1 | Earlier wells were requested to be polygon type. Is the point supplementary? | Included | Typo corrected, is to be polygon. | 2.3.4 Well | Change made document updated
340 | Potable water | Vol 1 | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station | More information required for a decision |  | close | Discussed during the May 1-3 workshops Determined that this is a post processing exercise by each organisation as required
341 | Potable water | Vol 1 | I believe this table and its attribute names have become mis-aligned. | Sector Discussion | Looks OK, need more information | 2.5.1 Equipment | More information required for a decision |  | close | Checked and OK
342 | Wastewater | Vol 1 | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe | No action
343 | Wastewater | Vol 1 | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. | Noted: no action required | The standards are recording as-constructed | 1.8 Theme Structure | No action
344 | Wastewater | Vol 1 | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? | Noted: no action required | Each organisation will decide how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure | No action
345 | Wastewater | Vol 1 | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
346 | Wastewater | Vol 1 | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets | No action
347 | Wastewater | Vol 1 | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent | More information required for a decision |  | Close | Covered at a Project level
348 | Wastewater | Vol 1 | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent | No action
349 | Wastewater | Vol 1 | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | Change made document updated
350 | Wastewater | Vol 1 | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
351 | Wastewater | Vol 1 | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
352 | Wastewater | Vol 1 | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber | No action
353 | Wastewater | Vol 1 | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the structure as per the example of an irregular shaped pit. | 2.3.3 Fitting | No action
354 | Wastewater | Vol 1 | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting | No action
355 | Wastewater | Vol 1 | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting | More information required for a decision |  | close | There are a number of assets featured in this comment. Each asset class will be recorded according to the standard therefore resulting in multuiple entries
356 | Wastewater | Vol 1 | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. | Sector Discussion | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe | More information required for a decision |  | Yes, Close | It is expected that the level of detail will be the same.
357 | Wastewater | Vol 1 | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe | More information required for a decision |  | haydn to follow up | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - George to update with reference to data provided by ChCh | GISSA GH add new table for Siphons and Vacuum syatems as supplementary table to pipes Adjusted pipe table to reflect conditional that Pipe Purpose field is conditional to populate new table when siphon or vacuum | GISSA GH added new table for Siphons and Vacuum syatems as supplementary table to pipes Adjusted pipe table to reflect conditional Added to SW, PW, WW - GH 26/6/17 | New table created for pipes to accomodate Siphons and Vacuum systems Added to all 3 waters documents Node definition modified
358 | Wastewater | Vol 1 | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. | Included | Precision is defined in the standards | 2.3.4 Pipe | No action
359 | Wastewater | Vol 1 | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision |  | haydn to follow up | In this schema, all activities undertaken on an asset are categorised into four broad ‘Event Types’ as defined below, these are in the right place | N/A
360 | Wastewater | Vol 1 | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe | No action |  |  | The standard provides an eaxmple to be followed | N/A
361 | Wastewater | Vol 1 | These changes should be coded into the pipe geometry, not as separate notes about the pipe. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision |  | haydn to follow up | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Close: -
362 | Wastewater | Vol 1 | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | Change made document updated
363 | Wastewater | Vol 1 | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe | More information required for a decision |  | Mark to follow up | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - duplicate
364 | Wastewater | Vol 1 | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe | No action
365 | Wastewater | Vol 1 | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. | Noted: no action required | Reviewed and Noted only | General | No action
366 | Wastewater | Vol 1 | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | No action
367 | Wastewater | Vol 1 | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe | More information required for a decision |  | remove soil type as an attribute against pipe | Removed attribute 'Soil Type' from Pipes Table Removed from all 3 Waters documents
368 | Wastewater | Vol 1 | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? | Included | The intent of the schema is to record what has been constructed at practical completion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | No action
369 | Wastewater | Vol 1 | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe | More information required for a decision |  | Close | The schema incorporates conditional fields to use for this scenario
370 | Wastewater | Vol 1 | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General | More information required for a decision |  | Close | Discussed during the May 1-3 workshops Noted no further discussion or action required
371 | Stormwater | Vol 1 & Vol 2 | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed - Refer to volume 2 notes To be address post initial release of the standards, via data mappings with roading standards
372 | 3-Waters & Buildings | Vol 1 & Vol 2 | What are the timeframes for this being adopted as mandatory? | Noted: no action required | Business Case. | General | No action
373 | 3-Waters & Buildings | Vol 1 & Vol 2 | Will there be a further round of submissions / comments? | Noted: no action required | Yes. Seminars in November. | N/A | No action
374 | 3-Waters & Buildings | Vol 1 & Vol 2 | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Included | Mandatory, Optimal, Optional will be discussed with the sectors and addressed during the pilot implementation phase | General | More information required for a decision
375 | 3-Waters & Buildings | Vol 1 & Vol 2 | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General | No action
376 | 3-Waters & Buildings | Vol 1 & Vol 2 | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference | Sector discussion
377 | 3-Waters & Buildings | Vol 1 & Vol 2 | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Noted: no action required | Treatment is not included | No Specific Reference | No action
378 | 3-Waters & Buildings | Vol 1 & Vol 2 | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | Included | Resolved and harmonised across the standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
379 | 3-Waters & Buildings | Vol 1 & Vol 2 | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | Noted: no action required | Included in Instruments | Instruments | No action
380 | 3-Waters & Buildings | Vol 1 & Vol 2 | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | Noted: no action required | Separate sections of data cohorts | General | No action
381 | 3-Waters & Buildings | Vol 1 & Vol 2 | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | Sector Discussion | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - Refer volume 2 (Diagrams from Noel)
382 | 3-Waters & Buildings | Vol 1 & Vol 2 | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | Included | Statement noted. To be actioned. | General | Change made document updated
383 | 3-Waters & Buildings | Vol 1 & Vol 2 | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well | No action |  |  | Wells and bores can be created as separarte asset types by each organisation as required
384 | 3-Waters & Buildings | Vol 1 & Vol 2 | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | Included | Suggestion adopted Standards will be updated | 1.5 Deliverables | Change made document updated
385 | 3-Waters & Buildings | Vol 1 & Vol 2 | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Sector Discussion | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | More information required for a decision |  |  | Discussed during the May 1-3 workshops Determined that this would be addressed during the Pilot / Implementation phase
386 | Wastewater | Vol 1 | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. | Noted: no action required | Reviewed and Noted only | General | No action
387 | Wastewater | Vol 1 | a standardised approach to the collation of data relating to As Built (As Constructed) asset information | Noted: no action required | Reviewed and Noted only | Abstract | No action
388 | Wastewater | Vol 1 | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. | Included | Will consdider for final edit - happy to add in. | Executive Summary | Haydn
389 | Potable water | Vol 1 | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. | Sector Discussion | Need recommended maximum attachment size | 1.5 Deliverables | More information required for a decision |  | close | ADDRESSED
390 | Potable water | Vol 1 | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. | 2.1.1 Accuracy Requirements for Locating Assets | No action
391 | Potable water | Vol 1 | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. | Included | Picked up previously | 2.1.2 Projections and Datums | Change made document updated
392 | Potable water | Vol 1 | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. | Noted: no action required | Agreed, but per pipe section, there is a from-node and a to-node, one of each. | 2.4.4 Node | No action
393 | Potable water | Vol 1 | We split pipes when there is a valve or hydrant on them. While other councils may not | Noted: no action required | Instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. | 2.4.5 Pipe | No action
394 | Potable water | Vol 1 | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. | Sector Discussion | need examples | 2.4.5 Pipe | More information required for a decision |  | adjust wording to indicate direction of primary flow | Adjusted wording In the Pipes section as follows • Capture each pipe section in the direction of its PRIMARY flow. To be modified in all 3 Waters documents
395 | Potable water | Vol 1 | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | No action
396 | Potable water | Vol 1 | A lot of the attributes seem to be duplicated | Noted: no action required | attributes are all different | 2.5.2 Pump | No action
397 | Potable water | Vol 1 | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. | Included | Agreed, diagram will be corrected | 2.7.1 Instruments | No action
398 | 3-Waters | Vol 1 & Vol 2 | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | Included | Updated | General | Change made document updated
399 | 3-Waters | Vol 1 & Vol 2 | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | Included | Updated | General | Change made document updated
400 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General | No action
401 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Noted: no action required | This is a metadata standard not asset management standards. | General | No action
402 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Included | Updated | General | Change made document updated
403 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | Noted: no action required | These are different in some cases / in others they are not, not the same definitions across sectors | General | No action
404 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | Noted: no action required | Updated and acknowledge that this will be upto the individual organisation to address | 1.5 Deliverables | No action
405 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | No action
406 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | Noted: no action required | References to be removed. | No Specific Reference | No action
407 | 3-Waters | Vol 1 & Vol 2 | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Noted: no action required | Treatment facilities are not included as part of these standards | No Specific Reference | No action
408 | 3-Waters | Vol 1 & Vol 2 | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Noted: no action required | Out of scope. However resourse consents maybe recorded against the specifc works for each project. | No Specific Reference | No action
409 | 3-Waters | Vol 1 & Vol 2 | Content: • Land – no parameters are set for the recoding of land information. | Excluded | Out of scope. | No Specific Reference | No action
410 | 3-Waters | Vol 1 & Vol 2 | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | No action
411 | 3-Waters | Vol 1 & Vol 2 | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | No action
412 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Noted: no action required | Detailed in business case only | No Specific Reference | No action
413 | 3-Waters | Vol 1 & Vol 2 | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Noted: no action required | Applies to all assets. Mandatory and optional fields to be determined during implementation. The benefits to costs covered in business case. | General | No action
414 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Noted: no action required | Covered in business case. | General | No action
415 | 3-Waters | Vol 1 & Vol 2 | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Noted: no action required | Covered in business case. | General | No action
416 | 3-Waters | Vol 1 & Vol 2 | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General | No action
417 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | Noted: no action required | Noted Will be further addressed during the pilot implementation phase | General | No action
418 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | Noted: no action required | This is not within the scope of these standards | General | No action
419 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | Noted: no action required | This is not within the scope of these standards | General | No action
420 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | No action
421 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required
422 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Noted: no action required | Included in the draft Standards | General | No action
424 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums | No action
425 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Included | Included in the draft Standards | 2.1.2 Projections and Datums | Change made document updated
426 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Included | Included in the draft Standards Asset categories included as guidance for each organisation | General | No action
427 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure | No action
428 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | Included | Included in the draft Standards | General | No action
429 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Included | Included in the draft standards | General | No action
430 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General | No action
431 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference | No action
432 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Included | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General | No action
433 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes | No action |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30
434 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) | General for Pipes | More information required for a decision |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required |  |  |  |  | Attribute removed from Pipe tables in all documents
435 | 3-Waters | Vol 1 & Vol 2 | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings | No action
436 | 3-Waters | Vol 1 & Vol 2 | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General | No action
437 | 3-Waters | Vol 1 & Vol 2 | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes | No action
438 | 3-Waters | Vol 1 & Vol 2 | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | Sector Discussion | More information is required to inform a way forward | General for Nodes | More information required for a decision |  |  | More detail provided in the updated version |  |  |  |  | Node definition has been revised and included a list of which assets would constitute the placement of a node
439 | 3-Waters | Vol 1 & Vol 2 | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure | No action
440 | 3-Waters | Vol 1 & Vol 2 | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General | No action
441 | 3-Waters | Vol 1 & Vol 2 | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General | No action
442 | 3-Waters | Vol 1 & Vol 2 | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure | No action
443 | 3-Waters | Vol 1 & Vol 2 | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles | No action | [7 empty] | Points lines and polygons as core geospatial features agreed to
444 | 3-Waters | Vol 1 & Vol 2 | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW | No action
445 | 3-Waters | Vol 1 & Vol 2 | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | Noted: no action required | Data collection is out of scope from these standards | General | No action
446 | 3-Waters | Vol 1 & Vol 2 | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference
447 | 3-Waters | Vol 1 & Vol 2 | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node | No action
448 | 3-Waters | Vol 1 & Vol 2 | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Excluded | Junctions / end points are not assets. | General | No action
449 | 3-Waters | Vol 1 & Vol 2 | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Noted: no action required | Junctions / end points are not assets. | No Specific Reference | No action
450 | 3-Waters | Vol 1 & Vol 2 | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - there is the need to be able to capture the 3 diameters. One of the diameters is needed to be populated, but it doesn't matter which one it is. | GISSA Make a note to indicate that it is upto the asset owner to define what is needed | Done GH added to 3Waters docs 26/6/17 | It is upto the asset owner to define what is needed
451 | 3-Waters | Vol 1 & Vol 2 | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | Noted: no action required | The ID proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes | No action
452 | 3-Waters | Vol 1 & Vol 2 | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | Included | Included in the draft standards Code lists have been supplied | General | Change made document updated
453 | 3-Waters | Vol 1 & Vol 2 | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Noted: no action required | Action on volume 1 and business case. The definition of a node has been reviewed and clarified | General | No action
454 | 3-Waters | Vol 1 & Vol 2 | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Noted: no action required | Statement noted. | General | No action
455 | 3-Waters | Vol 1 & Vol 2 | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Noted: no action required | Statement noted. Data transfer is not in scope however this asopect will be left to each organisation to determine the most appropriate way forward. | No Specific Reference | No action
456 | 3-Waters | Vol 1 & Vol 2 | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference | No action
457 | 3-Waters | Vol 1 & Vol 2 | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | Noted: no action required | 1. Completed 2. Further information required from respondent. Codelists are now included 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General | No action
458 | 3-Waters & Buildings | Vol 1 & Vol 2 | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | Noted: no action required | Statement noted. Consideration for Volume 1. | General | No action
459 | 3-Waters & Buildings | Vol 1 & Vol 2 | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | Noted: no action required | Statement noted. No action required. | General | No action
460 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | Noted: no action required | Statement noted. No action required. | General | No action
461 | 3-Waters & Buildings | Vol 1 & Vol 2 | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | Noted: no action required | Statement noted. No action required. | General | No action
462 | 3-Waters & Buildings | Vol 1 & Vol 2 | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | Noted: no action required | Business case. | General | No action
463 | 3-Waters | Vol 1 & Vol 2 | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | Noted: no action required | Statement noted. | General | No action
464 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
465 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Included | These inconsistencies have been actioned in the draft standards | General | No action
466 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | These inconsistencies have been actioned in the draft standards | General | No action
467 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | Sector Discussion | To discuss | No Specific Reference | More information required for a decision |  |  | OUT OF SCOPE
468 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | Noted: no action required | Action for volume 1. Codelists have been included defining the types of assets covered in each asset class. These codelists are dynamic in nature and over time will be added to as new materials, products etc enter the market | 1.7 Heirarchy | No action
469 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Sector Discussion | Tables to be discussed in Final Version Vol 1 | No Specific Reference | More information required for a decision Tunnels have been included |  |  | Tunnels and Containement Structures included. Other features can be added as required. Awaiting further examples
470 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy | No action
471 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
472 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
473 | 3-Waters | Vol 1 & Vol 2 | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Included | Tables will be referenced in Final Versions | General | No action
474 | 3-Waters | Vol 1 & Vol 2 | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | No action
475 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Noted: no action required | Statement Noted. Business case. | No Specific Reference | No action
476 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Noted: no action required | Statement noted. | No Specific Reference | No action
477 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Noted: no action required | Business case. | No Specific Reference | No action
478 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference | No action
479 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Noted: no action required | Implenmentation is not within scope | No Specific Reference | No action
480 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Noted: no action required | Business Case | No Specific Reference | No action
481 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Noted: no action required | Business Case. | No Specific Reference | No action
482 | 3-Waters | Vol 1 & Vol 2 | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
483 | 3-Waters | Vol 1 & Vol 2 | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
484 | 3-Waters | Vol 1 & Vol 2 | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | Included | Included in the draft Standards | General | No action
485 | 3-Waters | Vol 1 & Vol 2 | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | No action
486 | 3-Waters | Vol 1 & Vol 2 | The current drafts need additional work at the hierarchy level and better definition / guidance. | Sector Discussion | Asset Classifications have been defined in the Standards | General | More information required for a decision |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required
487 | 3-Waters | Vol 1 & Vol 2 | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Included | This is about context for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | Further discussion with Sector
488 | 3-Waters | Vol 1 & Vol 2 | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | Included | Included in the draft Standards | General | change made document updated
489 | Potable water | Vol 1 | savvy - edit out slang words like this | Included | Removed in current version | Executive Summary | Change made document updated
490 | Potable water | Vol 1 | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? | Included | Consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. | In Summary | Change made document updated
491 | Potable water | Vol 1 | Consultants - Replace by organisations? | Included | Term consultants now included in glossary. | 1.1 Register | Change made document updated
492 | Potable water | Vol 1 | Again, misuse of term 'consultants. edit through the document to correct this. | Included | Term consultants now included in glossary. | 1.4 Disclaimer | Change made document updated
493 | Potable water | Vol 1 | Is this still used? | Noted: no action required | Optional supply | 1.5 Deliverables | No action
494 | Potable water | Vol 1 | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? | Noted: no action required | Both schemata and schemas are both acceptible words for the plural of schema. | 1.6 Global Schemas | No action
495 | Potable water | Vol 1 | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? | Noted: no action required | This is not within the remit of the standards | No Specific Reference | No action
496 | Potable water | Vol 1 | how can the analytics standardise the data that has already been standardised? | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | No action
497 | Potable water | Vol 1 | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference | No action
498 | Potable water | Vol 1 | i.e. not fixed and topics can be added? | Included | Agree, asset classes can be added as agreed to | 1.8 Theme Structure | No action
499 | Potable water | Vol 1 | what does this mean? No? but no Y for yes? | Included | N changed to N/A | 1.9 Data Principles | Change made document updated
500 | Potable water | Vol 1 | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | Absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.1.1 Accuracy Requirements for Locating Assets | No action
501 | Potable water | Vol 1 | precisely? 'well' is a subjective term | Included | Changed | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
502 | Potable water | Vol 1 | no 's' | Sector Discussion | Cannot identify | 2.1.1 Accuracy Requirements for Locating Assets | More information required for a decision |  | close | Modified
503 | Potable water | Vol 1 | change 'issues' to 'risks' throughout document | Noted: no action required | Not a risk but an issue | 2.1.10 Common Attributes | No action
504 | Potable water | Vol 1 | Well - change to 'bore' | Noted: no action required | Term agreed to by TWG | 2.3.4 Well | No action
505 | Potable water | Vol 1 | does this create a 'node'/ if not then it is a problem for modelling. | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | More information required for a decision
506 | Potable water | Vol 1 | how is a locator or IP cable taped to the pipe represented? | Sector Discussion | Need more information and example | 2.4.5 Pipe | More information required for a decision |  | needs a yes/no field | Created new attribute field L_or_IP To be included in all the 3 Waters documents
507 | Potable water | Vol 1 | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | No action |  |  | DUPLICATE
508 | Potable water | Vol 1 | Is a backflow preventer a mechanical equipment asset or a valve/ | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment | More information required for a decision |  | valve | To be added to valve type
509 | Potable water | Vol 1 | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. | Noted: no action required | Absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure | No action
510 | Potable water | Vol 1 | this could be much larger with additional definitions e.g.. 'trunk main' | Noted: no action required | Codelists are dynamic and wil expand over time | Glossary | No action
511 | 3-Waters | Vol 1 & Vol 2 | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
512 | 3-Waters | Vol 1 & Vol 2 | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
513 | 3-Waters | Vol 1 & Vol 2 | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
514 | 3-Waters | Vol 1 & Vol 2 | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | Noted: no action required | Volume 2 is now complete | No Specific Reference | No action
515 | 3-Waters | Vol 1 & Vol 2 | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General | No action
516 | 3-Waters | Vol 1 & Vol 2 | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Sector Discussion | Included in the draft Standards Asset Classes included that are relevant to each network. These can be added to over time. The pilot implementation phase will be used as a guide | 1.7 Heirarchy | More information required for a decision |  | duplicate | Completed
517 | 3-Waters | Vol 1 & Vol 2 | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | No action
518 | 3-Waters | Vol 1 & Vol 2 | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Included | Tables will be referenced in Final Versions However it is upto each organisation to determine the most approapriate way to create these links based on their systems | General | No action
519 | 3-Waters | Vol 1 & Vol 2 | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
520 | 3-Waters | Vol 1 & Vol 2 | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
521 | 3-Waters | Vol 1 | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General | No action
522 | 3-Waters | Vol 1 | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. | Noted: no action required | Service level performance is included in Volume 2 | General | No action
523 | 3-Waters | Vol 1 | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes | More information required for a decision |  | close | CODE LISTS INCLUDED
524 | 3-Waters | Vol 1 | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
525 | 3-Waters | Vol 1 | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. | Noted: no action required | Please refer to Project and common data | General | No action
526 | 3-Waters | Vol 1 | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset owners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
527 | 3-Waters | Vol 1 | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes | No action
528 | 3-Waters | Vol 1 | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  | close | These are other data sets (layers) applied to any analytic and out of scope - per earlier discussions | N/A
529 | 3-Waters | Vol 1 | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. | Sector Discussion | More information is required to inform a way forward | General for Pump Station | More information required for a decision |  | close | Links checked to ensure cross referencing exists.
530 | Stormwater | Vol 1 | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. | Noted: no action required | This will be catered for through recording the "Source" | General | No action
531 | Stormwater | Vol 1 | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. | Included | This is a derivation for Volume 3, including precision of survey data | General | No action
532 | Stormwater | Vol 1 | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. | Included | Now normalised and standardsed with Metaconnect | General | No action
533 | Stormwater | Vol 1 | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General | No action |  | close | Discussed during the May 1-3 workshops Determined that these are not assets, LINZ holds the authoritative data sets
534 | Stormwater | Vol 1 | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General | More information required for a decision |  | close | DUPLICATE
535 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure | No action
536 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). | Included | Already incorporated into the table | 2.3.1 Containment Structure | No action
537 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure | No action
538 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure | No action
539 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure | No action
540 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure | More information required for a decision |  | GISSA to review and circulate for comment | There are a number of fields already included to accommodate the request soil type (Bank material), grass type, vegeatation type (lining material) ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  |  |  |  | No further information received
541 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall | More information required for a decision |  | include new component | Created new attribute field 'Apron' is a Yes or No field
542 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | No action
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment | More information required for a decision |  | include new attribute | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - Graeme to provide a drawing to George | GISSA - email sent for confirmation and advice Have reviewed E33 from CCC doc Awaiting response | Added new attribute fields Over_RL Easting Northing Added to SW GH 26/6/17
544 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber | No action
545 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | Change made document updated
546 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber | More information required for a decision |  | close | DUPLICATE
547 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | No action
548 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision |  | reference operating procedures | Discussed during the May 1-3 workshops Determined that operating procedures can be referred to
549 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber | More information required for a decision |  | change to RL | Removed Depth field and added new attribute field RL To be modified in all the 3 Waters documents
550 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision |  | include as optional | We now use Lat/Long, this enables access points to be included. Location of chamber is one location, acess is another - we need to think about inlcudnig 'both'? - like very large tanks ?? | N/A
551 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. | Sector Discussion | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | More information required for a decision |  | GISSA to review and circulate for comment | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - subject to George checking |  | Completed
552 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). | Noted: no action required | Please refer to comment above | 2.4.2 Channels | No action
553 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. | Sector Discussion | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | More information required for a decision |  | GISSA to get more details from the submitter | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - subject to George checking |  | Refer to Channel Shape
554 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | No action
555 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe | No action
556 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | Haydn | [5 empty] | Volume 2
557 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | Change made document updated | [5 empty] | Completed | Completed
558 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe | More information required for a decision |  | Close | Modified description to the following 'Protective material enveloping the asset to protect it from damage or intrusion' To be modified in all the 3 Waters documents
559 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | No action
560 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | No action
561 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? | Included | yes in Volume 2 | 2.4.4 Pipe | No action
562 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | Change made document updated
563 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe | More information required for a decision |  | Close | OUT OF SCOPE
564 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). | Noted: no action required | Parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station | No action
565 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station | No action
566 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. | Included | Attribute fields are included in the Pump asset class for motors. Please review and provide details of additional | 2.5.2 Pump | No action
567 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | No action
568 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. | Sector Discussion | Will include for ratification by the reviewers. | 2.5.2 Pump | New attribute proposed | Trigger level | close | Discussed during the May 1-3 workshops Deemed as part of Volume 2
569 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve | More information required for a decision |  | close | Discussed during the May 1-3 workshops Deemed as part of Volume 2
570 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | No action
571 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve | No action
572 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment | No action
573 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | Change made document updated
574 | Potable water | Vol 1 | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date | Noted: no action required | Reviewed and Noted only | General | No action
575 | Potable water | Vol 1 | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General | New Code List proposed | Health & Safety Type | new code list to be sent by Hugh | Modified H&S field from attribute field to Code List
576 | Potable water | Vol 1 | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General | More information required for a decision |  | close | Typically systems accept 254 characters. This field has been limited to 250
577 | Potable water | Vol 1 | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) | Noted: no action required | 10 character fields have been adopted to allow for expansion | General | No action
578 | Potable water | Vol 1 | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
579 | Potable water | Vol 1 | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. | Sector Discussion | Need more information and example | General | More information required for a decision |  | close | Discussed during the May 1-3 workshops Determined that this would be addressed during the Pilot / Implementation phase
580 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). | Sector Discussion | Need more information and example | 2.3.1 Containment Structure | More information required for a decision |  | close | Discussed during the May 1-3 workshops Determined that this is a post processing exercise by each organisation as required
581 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | close | Added to Specific validation Rule the following. 'If Yes then populate the Health and Safety field' To be modified in all the 3 Waters documents
582 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | No action
583 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | New Code List proposed | Burial Status Above ground Below ground Partially buried | new code list | Created new attribute field and associated code list 'Burial State' To be included in all the 3 Waters documents
584 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure | No action
585 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure | No action
586 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | add to code list | Created new attribute and associated code list 'Inlet Protection Type' To be included in all the 3 Waters documents
587 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | include as an attribute field | Created new attribute 'Inlet Feed Type' To be included in all the 3 Waters documents
588 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | include as an attribute field | Modified attribute from Shut Off Valve field to Outlet Shut Off Valve To be modified in all the 3 Waters documents
589 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | include a y/n field | Created new attribute 'Partition' To be included in all the 3 Waters documents
590 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision |  | convert to code list | Removed 'Con_spc' field and added created new attribute field 'Acc_Rest' and associated codelist To be modified in all the 3 Waters documents
591 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | No action
592 | Potable water | Vol 1 | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment | No action |  | GISSA to discuss with Wellington Water | Create attribute field "Observation" to enable recording of results To include in all the 3 Waters documents
593 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL a. Include Ground Water Level | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well | No action
594 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL b. Resource Consent number | Included | Included in Project Attributes | 2.3.4 Well | No action
595 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading | Sector Discussion | Code lists for NZDWS could be included - for discussion | 2.3.4 Well | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | More information required for a decision |  | include the ability to record multiple links | Created new attributes 'Link Feature 2' 'Link Identifier 2' 'Link Feature 3' 'Link Identifier 3' To be included in all the 3 Waters documents
597 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed | Manufacturer | include new attribute | Created new attribute fields 'Manufacturer' Manufacturers Warranty' To be included in all the 3 Waters documents
598 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | No action
599 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. | Included | Agreed | 2.4.3 Fitting | Change made document updated
600 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting 2.4.4 Node | More information required for a decision |  | close | A description has been provided to clarify what a Node is.
601 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe | New Asset Class proposed Detail of data requirements needed | Support Structures | include new asset class, Hugh to send on the information (including pic's) | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - Graeme to provide how this is recorded in ChCh. | GISSA Have contacted Tauranga and reviewed CCC documents will include a new asset class as 'Support Structure' under Civil Structures | Created 'Support Structure' asset class added to WW - GH 25/6/17 PW - GH 25/6/17 SW - GH 25/6/17 | Created 'Support Structure' asset class in all 3 waters documents.
602 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. | 2.4.5 Pipe | No action
603 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | No action
604 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. | Included | Already catered for | 2.4.5 Pipe | No action
605 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe | No action
606 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe | No action | [7 empty] | Ground water attribute now removed as per earlier request
607 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | No action
608 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. | Included | change in all documents | 2.4.5 Pipe | Change made document updated
609 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter | Included | removed nom_Bore | 2.4.5 Pipe | Removal of attribute proposed Have marked for removal in documents |  |  | Removed attribute Nominal Bore from pipes table To be modified in all 3 Waters documents
610 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe 2.8.1 Supplementary Data | More information required for a decision |  | include 3 points | Modified wording to reflect an irregular curve 'If pipe is curved and the curve is an irregular shape, provide three points to locate the asset. At 1/4, 1/2 and 3/4 along the length of the pipe that is curved' 'If the pipe is curved and the curve is a regular shape provide two points to locate the asset. One at the first tangent point and the second at the apex of the arc' To be modified in all the 3 Waters documents
611 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
612 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision |  | Wellington Water to provide examples to GISSA for inclusion | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action - George to modify the standards to make sure that 'cover' becomes 'lid' - Graeme to send picture to George | GISSA Modify current entries to LID - check with CCC and Auckland | changed SW - GH 25/6/17 PW - GH 25/6/17 WW - GH 25/6/17 CHECK CODE LISTS STILL RELEVANT | Modifed 'Cover' entries to 'Lid'
613 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision |  | close | Discussed during the May 1-3 workshops Details can now be included as part of the Health and Safety filed Noted no further discussion or action required
614 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision |  | include | Created new attribute field 'Sealed' To be included in all the 3 Waters documents
615 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber | More information required for a decision |  | close | The asset is to be captured as a point symbol
616 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | More information required for a decision |  | close | DUPLICATE
617 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | New attribute proposed | Portable generator (Y/N) | include | received details from Noel 12/5 Created new attribute field and associated code list 'Power Backup' To be included in all the 3 Waters documents
618 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | New attribute proposed | Calculation |  | received details from Noel 12/5 Included attribute fields for Seismic Performance Status Seismic Standard Seismic calculation To be included in all the 3 Waters documents
619 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve | More information required for a decision |  | Wellington Water to provide examples to GISSA for inclusion | received details from Noel 12/5 ON HOLD VALVE ATTRIBUTES NEED TO BE REVIEWED AS A WHOLE
620 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve | New Code List proposed | Valve Control & Automatic Control | Noel to provide advice on if this is needed | received details from Noel 12/5 ON HOLD VALVE ATTRIBUTES NEED TO BE REVIEWED AS A WHOLE
621 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. | Sector Discussion | see 00620 | 2.5.3 Valve | New Code List proposed | Valve Power | Noel to provide advice on if this is needed | received details from Noel 12/5 ON HOLD VALVE ATTRIBUTES NEED TO BE REVIEWED AS A WHOLE
622 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
623 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve | More information required for a decision |  | Noel to provide advice on if this is needed | received details from Noel 12/5 ON HOLD VALVE ATTRIBUTES NEED TO BE REVIEWED AS A WHOLE |  |  |  | Refer to Valve Purpose attribute
624 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | No action
625 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection
626 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
627 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Incoming Pressure
628 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Outgoing Pressure
629 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Headloss
630 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE l. Valve mechanism code list should be similar to: BFL Butterfly DIA Diaphragm SLC Sluice GAT Gate BAL Ball KNF Knifegate DAV Double air FLP Flap gate NED Needle SAV Single air SND Solenoid WSC Check PRV Pressure reducing RLV Pressure relief | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Type (Mechanism) Butterfly Diaphragm Sluice Gate Ball Knifegate Double air Flap gate Needle Single air Solenoid Check Pressure reducing Pressure relief | include | Incorporated into the existing code list 'Valve Type'
631 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow | include | Created new attribute field and associated code list 'Valve Purpose' To be included in all the 3 Waters documents
632 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Include attribute fields describing how the pump is powered - electrical, diesel, petrol. | Sector Discussion | Does this relate to the motor or the pump? To be compared to the attributes of the motor | 2.5.2 Pump | More information required for a decision |  | Wellington Water to provide examples to GISSA for inclusion | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action - Tauranga to send descriptions to George | GISSA GH to contact Tauranga - Is this the same as motor fuel type? | This issue has now been covered by the updated draft standard – Refer CODELIST 44 – Fuel Type Response from Tauranga 23/06/2017
633 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump | New attribute proposed | Pump oreintation | Wellington Water to provide examples to GISSA for inclusion | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action - George to include as a voluntary field | GISSA Create new attribute 'P_Orient' full name "Pump Orientation" | Included as P_Orient (MW - 23/06/2017)
634 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP c. “Actual pump rate” will at times be meaningless because of Variable Speed Drive (VSD) pumps, that can run at different speeds. This field is therefore either irrelevant for VSD, although it may be an eventual ‘input’ of actual data from control systems. | Noted: no action required | Reviewed and Noted only | 2.5.2 Pump | No action
635 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty end date, Purchase date to be reviewed. | 2.5.1 Equipment | More information required for a decision |  | include, use warranty end date, purchase date to be optional | Warranty end date already included Created 'Purchase Date' as an optional field To be included in all the 3 Waters documents
636 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. Include Capitalized cost as well as purchase cost | Included | ODRC / ORC / RC are included | 2.5.1 Equipment | No action
637 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT c. The abbreviated and full attribute names contained in this table are not related to each other (this is possible a typographical error). | Noted: no action required | Resolved in updated version | 2.5.1 Equipment | No action
638 | Potable water | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. An attribute field with an ability to include a SCADA reference should be included. | Noted: no action required | Refer to Telemetry | 2.5.1 Equipment | No action
639 | Potable water | Vol 1 | Asset Class: Electrical Asset - CABLING a. Ductwork poses a tricky question because it is separate from cabling. Ductwork can be a part of the structure, and can carry many cables. If it is going to be recorded, Ductwork needs to be an asset class in its own right. | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision |  | Wellington Water to discuss if this needs to be an asset type, or just a different type of pipe | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - George to include as a separate class of asset called a conduit | GISSA create new asset class 'Conduit' Refer to Buildings for what is there?? | Created and added PW, SW, WW - GH 27/6/17 | Created new asset class 'Conduit' in all 3 watres standards
640 | Potable water | Vol 1 | Asset Class: Instrumentation - INSTRUMENTS a. SCADA and RTU (controllers) are not instruments, because they do not measure variables. Include them under electrical equipment. | Included | Reviewed and Noted for Inclusion | 2.7.1 Instruments | Change made document updated
641 | Wastewater | Vol 1 | All Asset Classes a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Will ensure that they are applied. | General | Change made document updated
642 | Wastewater | Vol 1 | All Asset Classes b. Missing asset classes: There are a number of missing asset classes in the Wastewater Standard – including “Containment Structures” and “Tunnels”. Wellington Water has 23 containment structures for Wastewater, which is material in terms of asset renewal. | Sector Discussion | Additional Assets and attributes will be added to final version | General | More information required for a decision |  | Close | Add Tunnels and Containement structures Asset Classes to Wastewater
643 | Wastewater | Vol 1 | All Asset Classes c. It was uncertain how the ‘crossover’ between the Wastewater and Stormwater network is managed within the Standard (including weirs). | Noted: no action required | Otherwise please be specific about the uncertainty. | General | No action
644 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. A definition may be required in relation to “relative level”. Relationship of ladders to access chamber; H&S attributes may be required, as ladders need to be certified. Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. This should be considered for inclusion in Volume 2. | Included | Include H&S Attributes | 2.3.1 Access Chamber | Haydn
645 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. Vegetation should not form part of this asset class data attribute for the Wastewater network! | Sector Discussion | to be discussed with the TWG | 2.3.2 Channel | More information required for a decision |  | Close | Discussed during the May 1-3 workshops Noted no further discussion or action required
646 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b. Is this really an ‘asset class’ for Wastewater (open sewers?) | Noted: no action required | If they do not exist then this asset class will not be used | 2.3.2 Channel | No action
647 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. Generally felt to be a ‘solid’ set of data attributes related to pipes. | Noted: no action required | Reviewed and Noted only | 2.3.4 Pipe | No action
648 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. Is there scope for a new field called “expected remaining life” based on observations? | Included | Remaining life is 'expected', observed or otherwise (e.g. calculated) - related to intervention type | 2.3.4 Pipe | Haydn
649 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. How are ‘pipe supports’ treated within the Standard? | Sector Discussion | Please provide examples of the types of supports that are used | 2.3.4 Pipe | More information required for a decision |  | Close | DUPLICATE
650 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. The “Material Description “ field contents need to be set at the correct level – a significant impact on design life results between different materials such as uPVC, mPVC and oPVC, MDPE, HDPE and HPPE | Included | Material is a mandatory attribute | 2.3.4 Pipe | No action
651 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Soil Type should also be captured as part of this Standard (impacts design life) and used to inform a wider geospatial dataset. We need to remember that a pipe may cross several soil types. | Sector Discussion | Was previously discussed and rejected by the TWG | 2.3.4 Pipe | Change made document updated |  | Close | DUPLICATE
652 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Surface Material should be recorded as part of this Standard – impacts structural composition. We need to remember that this field must be an updatable attribute based on non-3W observations. Pipes will also cross several different surface material | Included | Add Surface Material | 2.3.4 Pipe | New attribute & associated Code List proposed | Surface Material Surface Material Type
653 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Included | This is a geospatial layer and can attribute accordingly | 2.3.4 Pipe | No action
654 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. In general, the focus group thought this was a well thought out set of attributes associated with Pump Stations. | Noted: no action required | Reviewed and Noted only | 2.3.5 Pump Station | No action
655 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Attributes related to power supply are important; elements of the “electrical” asset class are related to the pump station (see comments in section 2.9 related to the parent-child relationship inherent in pump stations). Attributes include (at least) an ICP number. | Included | Already included. | 2.3.5 Pump Station | No action
656 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION c. The Standard is silent on elements related to “Access” and/or “Easements” for this asset class. | Noted: no action required | Correct. Volume 1 focusses on recording asset data at practical completion | 2.3.5 Pump Station | No action
657 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station | More information required for a decision |  | include as a y/n field | Created new attribute field 'Overflow' To be included in all the 3 Waters documents
658 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION e. The cost attribute is associated with a particular construction date – ie, the pump station is assumed to be ‘static’. This is not likely. (again – may relate to parent-child relationship of pump station to assets it contains). | Included | ODRC / ORC / RC are included | 2.3.5 Pump Station | No action
659 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION f. Safe working limits are a legal requirement  does this form part of the building standard? | Included | Depth is recorded | 2.3.5 Pump Station | No action
660 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION g. “Building Owner” could be split between multiple owners | Included | Owner vs manager fields available in the draft standard Catenate multiple owners in field Buildings are separate assets, see buildings | 2.3.5 Pump Station | More information required for a decision
661 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Elements of a pump may be regarded as a distinct asset – such as motors, impellors, control system, cabling. The attributes of a pump relate to the pump type – this field may need further expansion and/or definition. | Excluded | Detailed drawing and component information is provided in manuals on handover - a reference attribute is included | 2.4.2 Pump | No action |  | GISSA to follow up with Wellington Water (Marty) | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  |  |  |  | No further information provided
662 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. The line between a pump asset and maintenance is not discussed within the Standard – even though this could change the asset function. | Sector Discussion | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | 2.4.2 Pump | Change made document updated |  | Close | OUT OF SCOPE
663 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. The data attributes within this section seem to relate entirely to Electrical Equipment; this does not make sense for this asset class. For example, the “Serial #” field has a description related to “protective material”. | Included | To be resolved in all 3W tables. | 2.4.1 Equipment | More information required for a decision
664 | Wastewater | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. “Risk” should be a key field – with a strong relationship to a relevant Volume 2 table. Safety in Design elements (and residual risk) should form part of this also. | Noted: no action required | Links are not within the remit of these standards - this is an analytical element | 2.4.1 Equipment | No action
665 | 3-Waters | Vol 2 | Data Relationships: Linkages shown in charts between Schema are inconsistent. For example, the “Repairs & Maintenance” schema is shown as interfacing to “As-constructed” and “Condition” schemas. But other Schemas have “Repairs & Maintenance” as an interface. For example, “Financial Performance” and “Demand” both have “Repairs & Maintenance” as an interface. If interlinkages are not shown to be consistent then the validity of the Standard can be questioned. This aligns with the overall statement made in section 1.9 of this document. | Sector Discussion | Relationships are explained in depth in Vol 2 | No Specific Reference | No action
666 | 3-Waters | Vol 2 | 2. Project Area: The project area artefact could apply to any business project over the 3 waters and not simply a new subdivision reticulation e.g. new facility or augmentation of WW or WS plant, refurbishment of upgrading of network etc. Understanding how projects/investments are delivered and perform is an important AM capability. The metadata schema should not constrain how assets are managed to meet desired outcomes. | Noted: no action required | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | No Specific Reference | No action
667 | 3-Waters | Vol 2 | 3. Delivery Risk: In order to generate valid information and outcomes the recording of data in a schema for national reporting will require consistency both within an organisation and between organisations over time. This should be recognised as a risk to the successful delivery of benefits by the Data Standard. | Noted: no action required | Delivery risk is a risk for Volume 3 - Methodology | 1.4.2 Intervention Methodologies (Volume 3) | No action
668 | 3-Waters | Vol 2 | 4. Units of measure in asset management would include flow, pressure, time - these are not in the Code list 1, but these and other units are referenced throughout the schemas. Note that different flow and pressure measurement units will apply to different assets or uses. | Included | Amended Code list | Table 2: Water Supply Service Attributes | No action
669 | 3-Waters | Vol 2 | 5. Date Range & Traceability: Similar to the comments made in section 2.1 related to Volume 1, key fields in Volume 2 should be auditable, giving the ability to track when changes are made, why and by whom. While a function of an information system, the requirement for such should be included in a metadata standard. | Sector Discussion | More information is required tofully iundertstand this feedback, but systems business rules (e.g. date ranges) are the place for defining extents, not these standards Assessors are included Data Table 1: Condition Attributes Assessor_N Assessor Name text | No Specific Reference | More information required for a decision
670 | 3-Waters | Vol 2 | 6. Code lists provided for Volume 2 generally require more work to develop consistent, full and meaningful references for use. We note that code lists have not been provided for Volume 1. | Included | Code lists have been updated for comment. | List of Code Lists | No action
671 | 3-Waters | Vol 2 | 7. Depreciation Data: Depreciation is an indicator of loss of service potential. Replacement value must reflect the true value of replacement in the current environment – which may be different to the environment at original installation. Changes to value and the rate of deterioration may be due to specific changes to asset attributes and environment over time. There must be fields to link changes to time and place. | Noted: no action required | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Code List 47: Financial Performance Metrics | No action
672 | 3-Waters | Vol 2 | 8. Lack of observation schema: As noted in section 4.4(a), the lack of an “Observations” schema hampers the ability for observation to inform multiple data schemas – such as condition or updates of asset attributes in the as-built schema. | Noted: no action required | Statement noted. Observations will feed into the attributes. | Data Table 1: Condition Attributes | No action
673 | 3-Waters | Vol 2 | 9. H&S Data: Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. | Included | Now included in Risk attributes Con_Rat_HS Consequence Rating Health and Safety | Table 7: Risk Attributes | More information required for a decision
674 | 3-Waters | Vol 2 | Condition a. Condition data is relevant for a range of decisions and processes in the asset lifecycle, most particularly around renewals, risk and valuations. The following comments consider these aspects but also apply to many of the other processes in some degree. | Included | Statement noted. | 2.2 Condition Schema
675 | 3-Waters | Vol 2 | Condition b. The inclusion of a calculated remaining useful life within the condition schema is fundamentally flawed because it does not account for other relevant asset life determining factors. Examples of such include criticality, demand, performance, optimisation and the asset’s operating environment. By linking condition grade directly to remaining useful life, the schema pre-supposes an end of life or replacement date decision. These conclusions should only be made while considering the wider factors as above. Noting this, Code List 6 linking condition grade to remaining useful life should be removed. | Sector Discussion | Let's discuss - these standards are not about decision-making - they are elements for decisionmaking - these standards define each of these elements. We are not suggesting you should make a decision on condition alone. But if your note is about definition of remaining useful life then let’s chat. | 2.2 Condition Schema | More information required for a decision
676 | 3-Waters | Vol 2 | Condition c. It is recommended that the schema be modified to take into account the level of confidence in condition grades. There is little or no recognition of the probabilistic nature of condition assessments and hence the confidence limits which apply to the grades. Any condition grade is made within a band of confidence at a point in time. The confidence level is relative to whether it is being applied to a subject asset or extrapolated to an asset group, and whether it is applied at the time of assessment or projected forward. | Noted: no action required | This is a calculable field, for example, stochasticity | No Specific Reference | No action
677 | 3-Waters | Vol 2 | Condition d. The basis of the interfaces with other schema (Table 5) is unclear and the linkages shown do not acknowledge the relationships between condition data and all other schema. Eg: i. Criticality determines priorities for condition data collection ii. Repairs and maintenance activities are a key potential source of condition data iii. Condition is indicative of likelihood of failure and hence helps determine risk iv. Service and financial performance are impacted by condition v. Demand and utilisation inform the criticality of an asset and hence priority for condition data collection. | Noted: no action required | These are analytical outputs of specific problems being solved. We can discuss | No Specific Reference | No action
678 | 3-Waters | Vol 2 | Condition e. Items included in the condition data attributes (Table 2) appear to be a mix of data at different levels of detail; some being at the assessment level and others at the observation level. Any hierarchy or relationship between these is not implied or explained however. The potential one-to-many linkages from asset to assessments and further to observations are not apparent. Any data required must be clarified in terms of how it relates to other data to enable practical processes for capture and storage. | Sector Discussion | Action: To be discussed with Wellington Water. | Data Table 1: Condition Attributes | More information required for a decision
679 | 3-Waters | Vol 2 | Condition f. The description of condition grades against physical deterioration (Code List 2) is a good approach however the terminology is inconsistent. Most descriptors but not all relate to asset failure. All should be described on the same basis to allow for consistent interpretation. “Asset failure” in this sense also requires definition and is unclear in the schema. | Included | Uniform terminology now applies | Code List 16: Condition Rating | No action
680 | 3-Waters | Vol 2 | Condition g. The condition grade types (Code List 3) are unclear and do not give any sense of the distinctions or relationships between structural, service, mean, peak and overall grades. | Included | Condition code lists (e.g. structural, exterior, interior) are now included in Vol 2 | Code List 16: Condition Rating | No action
681 | 3-Waters | Vol 2 | Condition h. The condition grade assessment methodologies (Code List 4) and assessment types (Code List 5) are extremely limited and do not capture many methodologies that are currently available and in use. Terminology is not consistent with the purpose of the list, ie; “Cut out” is a sampling methodology rather than an assessment type as listed. A cut out may be assessed visually, by destructive and/or non-destructive testing, or other means. Code lists 7 – 10 are similarly limited and the purpose and usage of which are unclear. | Sector Discussion | See code list | Code List 17: Condition Rating – Methodology | More information required for a decision
682 | 3-Waters | Vol 2 | Repairs and Maintenance a. The Proactive and Reactive Activity Type descriptions need additional clarification to minimise ambiguity. How should “impairment” be interpreted - breakdown, significant performance issue or just incipient failure only detectible with monitoring equipment (e.g. bearing vibration, thermographic image, etc)? Also “Scheduled” needs to exclude non-routine or one-off activities that are set to occur in the future. | Noted: no action required | See code list | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
683 | 3-Waters | Vol 2 | Repairs and Maintenance b. The schema does not support optimisation of maintenance tasks through RCM analyses or other FMECA based approaches. An example would be the need for a clear and unambiguous definition of asset function. This is not well covered in Part 1 attributes. Comment should be requested from an RCM practitioner. | Noted: no action required | Statement noted. This is not a maintenance management system. | No Specific Reference | No action
684 | 3-Waters | Vol 2 | Repairs and Maintenance c. Recording the “Image_ID” against activities does not cater for referencing other types of digital files. Suggest this optional attribute is made generic and capable of accepting hyperlinks to reference files in other systems. | Noted: no action required | This is an analytical requirement | No Specific Reference | No action
685 | 3-Waters | Vol 2 | Repairs and Maintenance d. Fail_Mode and Cause_Iss is important but must be specific to each asset type rather than generic across all assets. It’s not clear if this is the intention. | Noted: no action required | This is an analytical requirement and is matched to other elements (e.g. AssetID) to determine response | No Specific Reference | No action
686 | 3-Waters | Vol 2 | Repairs and Maintenance e. A key decision for every asset is to either run to failure or apply a scheduled maintenance/inspection plan. | Noted: no action required | This is an analytical requirement (i.e. both) | No Specific Reference | No action
687 | 3-Waters | Vol 2 | Repairs and Maintenance f. In Part 1 Condition Assessment Type is an asset attribute, but Condition is part of a different schema. Shouldn’t these go together to reflect the fact that the condition assessment approach may change over time? | Included | Yes, but in the analytical phase. | No Specific Reference | No action
688 | 3-Waters | Vol 2 | Repairs and Maintenance g. It isn’t clear how maintenance strategies are to be handled (i.e. managing maintenance work that has weekly/monthly/annual/ etc activities). AMIS functional requirements should be considered before fields like Recur and Recur_Cyc are established. | Noted: no action required | Standard is not intended to populate a maintenance plan. Code Lists are included to handle this requirement e.g. Recurrence Cycle | Code List 5: Recurrence Cycle Unit | No action
689 | 3-Waters | Vol 2 | Repairs and Maintenance h. Need quantity as well as cost information to be able to analyse trends and predict future costs. Need to record all resources – not restricted. | Noted: no action required | Code lists for quanitifying repairs included | Code List 6: Bases of Cost | New Code List from Working Group
690 | 3-Waters | Vol 2 | Repairs and Maintenance i. The combination of Activity Type, start date/time, end date/time does not appear to meet the requirements for DIA non-financial reporting for urgent/non-urgent callouts (i.e. need to separately record time to reach site and time to resolve issue). | Noted: no action required | Type of maintenance activity is included | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
691 | 3-Waters | Vol 2 | Repairs and Maintenance j. There needs to be a new Event Type similar to “Upgrade/Improvement”. Irrespective of the funding source (capital vs operational) assets need to have a full history of events recorded against them. If we exclude upgrades and rely solely on project registers to capture this information we make lifecycle management significantly more difficult. | Noted: no action required | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Code List 49: Description of Financial Performance Element | No action
692 | 3-Waters | Vol 2 | Repairs and Maintenance k. Why record overflows etc. in repairs and maintenance schema and not in the level of service? Overflows are recorded per financial year, different organisations have different financial years, is history recorded i.e. over time. Should other compliance activities i.e. RON and CDEM should also be coded. | Included | One is a record of the type event One is a record a service level e.g. overflows per year and an analytic | Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | No action
693 | 3-Waters | Vol 2 | Repairs and Maintenance l. Asset versus component issue can give rise to different design criteria and system performance i.e. a pump has a l/s design while a filer has (say) minimum pressure drop, but it is performing of the pumping station that is the issue. | Noted: no action required | Statement noted | No Specific Reference | No action
694 | 3-Waters | Vol 2 | Repairs and Maintenance m. Does not appear to allow for other investigation methods e.g. vibration analysis, DCVG results, thermal imaging, usage data analytics for identifying if an intervention is required. | Included | Code lists to be discussed against current code lists e.g. Condition (This is really a Volume 3 question) | Code List 17: Condition Rating – Methodology | No action
695 | 3-Waters | Vol 2 | Repairs and Maintenance n. As found and as left condition or status is useful for items like valves, could also apply to depth of cover, locks etc. | Included | Statement Noted: No action required. | No Specific Reference | No action
696 | 3-Waters | Vol 2 | Repairs and Maintenance o. Asset performance does not clearly link to key result areas or key performance indications set by organisations in the management of assets or demanded by consumers. | Sector Discussion | This is an anlytical question - discuss with sector | No Specific Reference | More information required for a decision
697 | 3-Waters | Vol 2 | Repairs and Maintenance p. Asset or service performance - it is not clear what is referred to or if this is consistent. | Sector Discussion | Section updated in Volume 2 | 5.4 Service Performance Schema | More information required for a decision
698 | 3-Waters | Vol 2 | Repairs and Maintenance q. How are components and soft parts etc linked to assets, is the lifecycle of O&M supported by this? | Noted: no action required | Component type is an attribute in the repair schema and captured under each asset. | 2.3.4 Components of Repairs, Maintenance and Operations | No action
699 | 3-Waters | Vol 2 | Repairs and Maintenance r. Benchmarking - same as identified in service levels schema, consistency is required for valid and useful outputs to be obtained. | Noted: no action required | Statement noted and agreed. | No Specific Reference | No action
700 | 3-Waters | Vol 2 | Repairs and Maintenance s. Outage duration - mandatory for all actions but what if no outage? Also what if the customers are reinstated over time ie 95% connected in 1 hour while the rest are out for days? Outage is linked to ' number of people' - this can be impossible to measure depending on each connection (as in an apartment block), would customer or property be a better measure. | Noted: no action required | Agreed. Then outage duration = 0. | No Specific Reference | No action
701 | 3-Waters | Vol 2 | Repairs and Maintenance t. Third party damage excluded from outage definition but included in repair schema as cause. | Included | Third Party attribute included | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
702 | 3-Waters | Vol 2 | Repairs and Maintenance u. Maintenance planning - focused on time based maintenance (elapsed), but could encompass operating hours or CBRM. A MMS would do a better job, would it be better not to specify these matters in the schema and just have an objective for an outcome based system in place. This could be applied throughout the data standard noting the issues with consistently in benchmarking. | Sector Discussion | Analytical elements included in standards to schieve this analytic | No Specific Reference | More information required for a decision
703 | 3-Waters | Vol 2 | Repairs and Maintenance v. It would be desirable to have costs for maintenance collected on an area/project basis for performance analysis. | Included | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | No Specific Reference | No action
704 | 3-Waters | Vol 2 | Repairs and Maintenance w. Should complaints be linked to an issue or root cause rather than an address or asset - this would enable better linking and development of appropriate solutions and priority setting than a collection of disparate reports. Also need to know the outcome of the assessment of a compliant ie internal plumbing, no issue found etc before an organisation make decisions on number of complaints. Option of an outcome based CRM system rather than data standard? | Included | Linking CRM information to asset information is not in scope These root cause examples in the code list are asset related interrogations for asset management purposes. | No Specific Reference | No action
705 | 3-Waters | Vol 2 | Utilisation a. Asset utilisation needs to consider the level of redundancy in the network or asset system required to achieve the desired overall level of risk. The proposed calculation of utilisation could work for an individual pump, but would be of little/no value for a trunk main network. It could easily be misinterpreted. | Included | Redundancy is include in the codelists in Vol 2 as an analytical attribute (see vulnerability). | Code List 43: Global Resilience Rating Elements | No action
706 | 3-Waters | Vol 2 | Utilisation b. Until the intervention methodologies are proposed for each of the 3 waters we find it difficult to understand what fields may or may not be wanted for this schema. | Noted: no action required | Statement noted. | 3.2.5 Code Lists
707 | 3-Waters | Vol 2 | Demand a. Demand applies to collections of assets. Why would you want to record demand against an individual asset such as a pipe or valve? | Included | This is an analytics requirement, but may no be required agaist all asset components. | No Specific Reference
708 | 3-Waters | Vol 2 | Demand b. The fields offered are very limiting in this schema and the use of demand needs to be thought through in more depth. | Noted: no action required | Demand Section has been updated in Volume 2 | 3.3 Demand Schema
709 | 3-Waters | Vol 2 | Demand c. Peak demand at a system level is not the sum of zone demands due to the diversity/averaging effect as the study area increases in size. Average demand at a system level is the sum of the zone demands. The schema does not seem to recognise this. | Noted: no action required | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler | Data Table 4: Demand Attributes | No action
710 | 3-Waters | Vol 2 | Demand d. What analytics would this schema (as is) be used to support? | Noted: no action required | Future connections on flow (population demand) | Code List 33: Demand – Measure | No action
711 | 3-Waters | Vol 2 | Demand e. Should this schema exist in an AMIS? | Noted: no action required | Yes | 3.3 Demand Schema | No action
712 | 3-Waters | Vol 2 | Criticality a. Criticality is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | No change | 4.3 Criticality Schema | No action
713 | 3-Waters | Vol 2 | Criticality b. The current approach to criticality from Wellington Water uses criticality as an equivalent to consequence in the evaluation of risk. To this effect the criteria for criticality that we have developed uses cumulative weighted impacts in combination with importance (exposure) factors to derive risk. My view is that the criticality descriptors offered in the standards are only one component of the consequence variable in the risk equation ie the exposure factor. To this extent it is puzzling to identify how criticality as described could be used in the evaluation of risk – given the subsequent content of the risk schema. | Noted: no action required | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | 4.3 Criticality Schema | No action
714 | 3-Waters | Vol 2 | Criticality c. For example if the renewal of a pipe was being considered wrt risk of failure – condition is an indicator of probability, the potential impacts could be social, environmental or financial loss and the exposure is measured by the number of people or the importance of the facility affected by the loss of service. | Noted: no action required | These are analytical inferences which are attributed in code in algorithms by attributes these standards define | No Specific Reference | No action
715 | 3-Waters | Vol 2 | Criticality d. Until worked examples are provided as to how the consultants perceive criticality being used for different decisions we struggle to see how the schema as offered would be useful or at best would have limited value. | Noted: no action required | Explanation found in criticality schema | 4.3 Criticality Schema | No action
716 | 3-Waters | Vol 2 | Criticality e. The code list 27,28,29 tables have some potential flaws in our view. i. Special facilities is too vague as a term for Code 5. Few utilities would have munition storage or critical data centres and in most cases data centres would have back up. How is this derived for example if it was potential damage from blowing up a munitions store, how would compare to an LPG centre or holding tanks containing solvents ii. For a water utility is a hospital really less critical than a data centre? iii. What happens when an asset services 3 or 4 hospitals iv. Where is economic loss factored into these tables – they seem to be very “government” centric v. We struggle to think that decision making using criticality for small towns of less than 5000 people would only ever have code 3 assets as their most important asset. Risk is about context and the context must consider the community and the economic scale of their investment. We do not believe one size fits all. | Noted: no action required | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. | No Specific Reference | No action
717 | 3-Waters | Vol 2 | Risk a. Risk is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | Statement noted. | No Specific Reference | No action
718 | 3-Waters | Vol 2 | Risk b. We assume that the risk schema is intended to facilitate risk management within water utilities. | Noted: no action required | Yes, and for buildings per the Biulding Standard | 4.4 Risk Schema | No action
719 | 3-Waters | Vol 2 | Risk c. We have reviewed this schema with respect to the principles of risk management as outlined in Section 3 of the guideline document for AS/NZS 31000:2009 | Noted: no action required | Noted | 4.4 Risk Schema | No action
720 | 3-Waters | Vol 2 | Risk d. In particular the schema as drafted inhibits the following principles: | Noted: no action required | Noted | 4.4 Risk Schema | No action
721 | 3-Waters | Vol 2 | Risk e. 3(g) Risk management is aligned with the organisations external and internal context and risk profile | Sector Discussion | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
722 | 3-Waters | Vol 2 | Risk f. 3(h) Risk management recognises the capabilities, perceptions, and intentions of external and internal people that can facilitate or hinder the achievement of the organisations objectives | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
723 | 3-Waters | Vol 2 | Risk g. 3(j) Risk management continually senses and responds to change. As external and internal events occur, context and knowledge change, monitoring and review of risks takes place, new risks emerge, some change, others disappear | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
724 | 3-Waters | Vol 2 | Risk h. To propose a specific risk matrix into a national standard seems to conflict with these basic principles | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct And any organisation can taylor the analysis to the local context | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
725 | 3-Waters | Vol 2 | Risk i. Although interdependencies between other schemas are stated it is difficult to extract how they would be used together. Risk, criticality and condition must be interconnected but there is no indication as to how the application of these schemas would allow this | Noted: no action required | This would depend on the problem being solved and the analytical approach in doing so | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
726 | 3-Waters | Vol 2 | Risk j. The suggestion that probability scales for different events and water types are the same is unhelpful in the absence of worked examples. Are there examples to demonstrate a sensible cross relationship for the use of probability scales in water supply and stormwater? | Noted: no action required | Unclear of what this means, but the scales are adaptive to event type, but specifiuc to asset type | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
727 | 3-Waters | Vol 2 | Risk k. Other than flood risk, how do you assess time based probabilities? The use of the word “time to time” or “in your career” will lead to subjective assessments that will simply promote inconsistent investment decisions rather than secure them. | Noted: no action required | Code list updated | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
728 | 3-Waters | Vol 2 | Risk l. We believe the contents of the fields that describe 1- 5 consequences should be omitted. A decision to occupy these fields for a national risk schema to derive nationally consistent approaches to risk will do exactly the opposite – it promotes subjective assessment and also directly contravenes the principles of risk management as described in AS/NZS 31000. | Noted: no action required | To discuss, see code lists | Code List 41: Consequence Rating | More information required for a decision
729 | 3-Waters | Vol 2 | Resilience NO schema offered However, we urge you to consider a fundamental question when addressing resilience for water utilities. Is the assessment of an assets’ resilience important or is it more important to assess the resilience of the service provided to customers on a national scale? We would suggest the latter, and therefore question the merits of offering a schema for asset resilience. If it is the latter, we also suggest that resilience is better attributed to customers rather than assets. | Included | Schema updated | 4.5 Resilience Schema | No action
730 | 3-Waters | Vol 2 | Design Performance This schema is not required. We don’t need evaluative criteria here. Attributes should be in the as built schema and actual performance should be in service performance. Table 12 in all volume 2 documents (sections 9.3) refer to the linkages with the resilience schema not the design performance | Noted: no action required | Let's discuss this is important. Design performance is different than Service Performance | 5.2 Design Performance Schema | More information required for a decision
731 | 3-Waters | Vol 2 | Financial Performance a. General comment – It would be interesting to know what is determined to be core data requirements with regards to the attributes. There is a large set of attributes to collect a large number would only be relevant to a small number of organisations. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | 5.3 Financial Performance Schema | No action
732 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
733 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
734 | 3-Waters | Vol 2 | Financial Performance c. Valuation date doesn’t seem to appear anywhere. | Noted: no action required | Included in standards | Data Table 10c: Valuation Attributes Details (Collected Level Indicated) | No action
735 | 3-Waters | Vol 2 | Financial Performance d. Linking the financial information e.g. revised asset lives with condition data. | Noted: no action required | Attributes included in standards, this is an analytical exercise | No Specific Reference | No action
736 | 3-Waters | Vol 2 | Financial Performance e. Terminology is not consistent with the Repairs and Maintenance schema e.g. reactive/planned/etc. | Noted: no action required | Now consistently applied | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
737 | 3-Waters | Vol 2 | Service Performance Level of service is recorded against individual assets, this may cause issues where service level is required from a network, facility, project, contract or organisational levels. These levels of service may not directly relate to asset parameters or the level of service at an asset may relate to another asset upstream (e.g. minimum pressure at a downstream point relates to the upstream network and pumps/regulators etc). Also levels of service are not static and these may change (this change may be the result of internal or external drivers). | Noted: no action required | These are analytical constructs from an individual assetID dataset. How consolidated into geographic units os for the specific analysis, e.g. network, zone, catchement etc. | No Specific Reference | No action
738 | 3-Waters | Vol 2 | Service Performance a. Benchmarking relies on the consistency of inputs. In order to generate valid information and outcomes the recording of data in a scheme for national reporting will require consistency in an organisation, between organisations and over time. Other national standards have shown there are issues with this approach, will the benefits of a metadata standard be realised (what are the risks and assumptions to the achievement of this benefit)? | Noted: no action required | This is a reference to standardised analytical approaches | No Specific Reference | No action
739 | 3-Waters | Vol 2 | Service Performance b. Residential demand figure, valid for industrial or commercial areas, how updated and how is history against assets recorded? | Noted: no action required | This is a reference to an analytical approach. E.g. ParcelID District Plan Zone type and connection demand (or Level of Service). | No Specific Reference | No action
740 | 3-Waters | Vol 2 | Service Performance c. Is it feasible that the same assessor (individual) is used for all items in each asset i.e. cultural significance and technical design and financial measures? | Noted: no action required | The same or multiple | No Specific Reference | No action
741 | 3-Waters | Vol 2 | Service Performance d. Consents compliance is linked to an asset when consents are typically given on an activity/facility - correct linkages and business processes will need to be established and implemented to ensure that compliance is achieved in light of asset changes. | Noted: no action required | Consent attributes are captured at property level which is not inconsistent with reporting at network/zone level - i.e. it is a spatial query between the two data sets. The attributes are specified for capturing asset detail in the standards | No Specific Reference | No action
742 | 3-Waters | Vol 2 | Service Performance e. Third party damage is excluded from service measures (interruptions) for water supply. This is a valid facet of AM, and the scheme has this included in repair and maintenance for WW assets. | Noted: no action required | Included in the Standards | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
743 | 3-Waters | Vol 2 | Service Performance f. MoH grading should be linked to a time the grade was awarded, and possibly should be greater than just a single field i.e. who assessed etc. We question the merit of this as a valid asset performance measure as it is always system based. | Noted: no action required | Included in the Standards | Data Table 11: Service Performance Attributes – Functional | No action
744 | 3-Waters | Vol 2 | Service Performance g. The fact a health and safety assessment has been carried out is interesting, but it is the results that are important (have the risks been addressed or are there outstanding issues etc) and there is no mention of this. | Noted: no action required | Included in the Standards | Table 2: Water Supply Service Attributes & Code List 41: Consequence Rating | No action
745 | 3-Waters | Vol 2 | Maintenance Planning i. Will the scheme provide an effective (and efficient) link to maintenance management systems that are in use currently? | Included | Yes that is the intention for the future. | No Specific Reference | No action
746 | 3-Waters | Vol 2 | Maintenance Planning ii. Are all costs collected at an asset level, won't different treatments give rise to different outcomes, ie, where are staff or contractor costs added to a facility, item or asset. Is maintenance carried out on assets as they exist or on notional assets? | Included | Application of costs will be at the discretion of the rganisation, but likely to be applied to a cohort of assets when being maintained | No Specific Reference | No action
747 | 3-Waters | Vol 2 | Operational Performance i. Actual performance should also be recorded as well as consent compliance - is water quality improving over time or always just inside the limit? | Included | Action: add in to schema (design performance? Service performance) | Data Table 9: Design Performance Attributes | No action
748 | 3-Waters | Vol 2 | Operational Performance ii. There is reference to LAWA framework – is this commonly used throughout the country? Would it be better to refer to the National Policy Statement or specific Regional rules as applicable for the authority? | Noted: no action required | All regional councils use LAWA | No Specific Reference | No action
749 | 3-Waters | Vol 2 | Valuation and depreciation Asset life versus economic/accounting life, does asset structure match the chart of accounts used by all organisations and applied in all business models i.e. contracted services? | Noted: no action required | Yes - there are appropriate fields for ODRC, ORC, RC and Forecast, Actual and Budget financial information in Finance Performance sections | Code List 47: Financial Performance Metrics | No action
750 | 3-Waters | Vol 2 | Planning for growth or decline i. Assets will need lifecycle stages not just in service ie proposed (linked to project), out of service, in store, abandoned, leased for F/O etc (assets can provide other services, not just those implicit in the standard) | Included | Discuss with Sector - to consider schema | No Specific Reference | Create a code list of service types as suggested here?
751 | 3-Waters | Vol 2 | Planning for growth or decline ii. Levels of service can change over time on different assets, this will need to be understood/recorded | Noted: no action required | Atributes to do this are included in the standards | No Specific Reference | No action
752 | Wastewater | Vol 1 | In talking about As Managed, I assume this is for how the councils handle data rather than how the data supplied by survey from the field, as these are two different worlds? | Sector Discussion | This is a discussion in the development of Volume 3 | No Specific Reference | No action |  | close | OUT OF SCOPE - VOLUME 5
753 | Wastewater | Vol 1 | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this | Included | Reviewed and Noted for Inclusion Included as part of the Project Attributes table Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | More information required for a decision
754 | Wastewater | Vol 1 | There is increased risk to data accuracy in companies that are not working all the time with software projection transformations. As the client, I would always want to receive the data in it original projection and transfer it myself | Included | The requirement is for each company to deliver the data in the final projection and datum | 1.5 Deliverables | No action
755 | Wastewater | Vol 1 | Why is this BIM Enabled? Should this not be BIM Enabled/Geospatial Representation as these still hold and display 3d information. | Noted: no action required | Update, asset management and facility management systems do…. | 1.9 Data Principles | No action
756 | Wastewater | Vol 1 | This surely should be "current parcel" boundaries. Not sure as to what a title/property boundary is, as what is the definition of property (residence, address, rating unit, parcel(s))? Also, is this relevant?You want the assets to be shown in true survey location even if this shows them being constructed illegally through private property. | Sector Discussion | For analytical purposes Have added 'geographical units' code list | 2.1 Technical Reference Information | More information required for a decision |  | close | OUT OF SCOPE
757 | Wastewater | Vol 1 | I believe this is how data should be stored, but supply of data should be as captured. By forcing this to the supplier you are increasing the risk of error, with groups that will only project data occasionally more likely to make mistakes | Noted: no action required | The intent of this is to educate the indutsry in what capability it will need | 2.1.2 Projections and Datums | No action
758 | Wastewater | Vol 1 | Why would you develop a new specification and then allow for it to be supplied in a historic format such as shapefile. This also means that the defined "text" geometry type cannot be supplied and instead would need to be changed to a point | Noted: no action required | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF | 2.1.7 Metadata Definitions | No action
759 | Wastewater | Vol 1 | Is this cost of the asset or cost of the asset plus installation? Is this standard cost of the recommended price of the asset, rather than any discounts were achieved? | Noted: no action required | All replacement costs include installation | 2.1.10 Common Attributes | No action
760 | Wastewater | Vol 1 | Is the central location the centre of access (i.e. manhole lid)or the centre of the structure? | Included | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. | 2.3.1 Access Chamber | Change made document updated
761 | Wastewater | Vol 1 | Pipe length shown here is neither the length of the digital pipe feature or the length of the real world feature, as you are not taking into account the "faux" pipe connectors angle. The middle pipe length here is very confusing! | Sector Discussion | Need more information for a way forward | 2.3.1 Access Chamber | More information required for a decision |  | noted, close | Discussed during the May 1-3 workshops Noted no further discussion or action required
762 | Wastewater | Vol 1 | Does this mean covered by dirt and not readily accessible or below ground level? | Noted: no action required | Below ground level | 2.3.3 Fitting | No action
763 | Wastewater | Vol 1 | What happens when two separate pipes are installed between access points (e.g. different material etc). Also there are examples were pipes may not have access chambers (as defined by this document). While that may be not best practice, it does occur. | Noted: no action required | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists | 2.3.4 Pipe | No action
764 | Wastewater | Vol 1 | Is this the digital length or the real world length? | Included | This is the real world length as described in the QA validation field. | 2.3.4 Pipe | No action
765 | Wastewater | Vol 1 | What does this mean? What level of accuracy is defined as a discrepancy? | Included | Changes made to wording to reflect tolerances used in practice ('field') | 2.7.2 Matching to Existing Infrastructure | Change made document updated
766 | Potable water | Vol 1 | Asset Group: To be consistent with Section 1.8 Should this heading be changed to "Asset Category" ? (Or in section 1.8 change "Asset Category" to "Asset Group" | Included | Changed to Asset Group for consistency. | 1.7 Heirarchy | Change made document updated
767 | Potable water | Vol 1 | Asset Type: To be consistent with Section 1.8, should this be changed to "Asset Class" | Included | Changed to Asset Class. | 1.7 Heirarchy | Change made document updated
768 | Potable water | Vol 1 | The paragraph refers to "Asset Types", yet table 1.8 does not reference "Asset Types", only "Asset Class". If these are not interchange in relation to meaning, then I suggest a explanation of "Asset Type" and "Asset Class" be documented within the document somewhere. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
769 | Potable water | Vol 1 | My personal preference is to utilize "Asset Class" as standard terminology, and replace any instances of "Asset Type" within the document if they are inferring the same meaning. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
770 | Potable water | Vol 1 | My personal preference is to utilize "Asset Category" as standard terminology, and replace any instances of "Asset Group" within document. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
771 | Potable water | Vol 1 | Conflicts with section 2.3.4 states that a well is to be represented as a polygon | Included | Changed to Polygon | 1.8 Theme Structure | Change made document updated
772 | Potable water | Vol 1 | Listed here as a guide, but each definition of the asset class states the required spatial representation. ie 2.3.1 states polygon feature. Therefore for clarity, should this table also list the requirement of the standard for each asset class? | Sector Discussion | More information is needed for a way forward | 1.9 Data Principles | More information required for a decision |  | haydn to follow up | The standard allows for representing any component / asset / asset class / group of assets etc in any way organisations like. I'm not sure we need to do this for all, as it will be different in different circumstances | N/A
773 | Potable water | Vol 1 | I am assuming this only for Geo-spatial attributes? (As there may be different sources utilized across multiple attributes.) If this is correct, can this be added for clarity in the contents column. | Included | Defined by organisation | 2.1.10 Common Attributes | No action
774 | Potable water | Vol 1 | If the data source changes, is there a need to keep a date history of the changes. | Noted: no action required | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. | 2.1.10 Common Attributes | No action
775 | Potable water | Vol 1 | Common Attributes for your consideration: (We currently have the following 3 attributes fields across all our assets) - Manufacturer (of asset) - Supplier (of asset) - Installed By (Contractor who installed asset) Fields to be utilized to identify failing assets due to manufacturer/supplier and potential faulty installation by a contractor. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | include and align with buildings | Incorporated where relevant
776 | Potable water | Vol 1 | This field should be allowed to be empty. What if there is no photographic references available. Flows through to Asset Class definitions | Sector Discussion | consider N/A as an appropriate response. | 2.1.10 Common Attributes | More information required for a decision |  | make non-mandatory | Modified attribute General Validation Rule to also include that the field is 'Optional' Modify in all 3Waters and BH documents
777 | Potable water | Vol 1 | Define "Asset Classes" and "Asset Types" | Included | Asset Classifications have been defined in the Standards | 2.2 Asset Categories | No action
778 | Potable water | Vol 1 | RL: Add a definition of RL in the "Glossary of Terms and Definitions" in the document (Reduced Level) "RL" acronym used in multiple places in the document. | Included | Included in Glossary | 2.3.2 Embankment, Glossary | Change made document updated
779 | Potable water | Vol 1 | No Type field for Wells. ie Type_Well Is this an oversight or genuinely not needed? | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision |  | GISSA to follow up | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Action: - Noel to provide to George | GISSA Reviewed Type of well covered by Purpose attribute | Type of well covered by Purpose attribute
780 | Potable water | Vol 1 | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision |  | include as a code list (Noel to provide) | Created attribute field 'Construction Method' and associated code list |  | Action: - Noel to provide to George | GISSA Refer to Noels email | Completed GH 16/5/17
781 | Potable water | Vol 1 | Seem to be missing Chamber Diameter, for circular access chambers. (As it states that AC_Length and AC_width only to be used if chamber is non circular) | Sector Discussion | Needs some rework and clarifiation. | 2.4.1 Access Chamber | More information required for a decision |  | close | RESOLVED |  | Close: -
782 | Potable water | Vol 1 | Potential Attribute: Manufacturer of Fitting | Included | Already identified and will be refered to TWG. | 2.4.3 Fitting | New attribute proposed | Manufacturer
783 | Potable water | Vol 1 | Water flow direction is not absolute. I am assuming this is for a network operating under "normal" conditions. | Included | Correct. For a network operating under 'normal' conditions. | 2.4.5 Pipe | No action
784 | Potable water | Vol 1 | For clarity, perhaps include a diagram showing an irregular access chamber. Refer to page 20 in Vol 1 of the waster water meta-data standard (V1.2 DRAFT A - 14 July 2016) | Sector Discussion | Completed | 2.4.6 Pump Station | Change made document updated |  | close | RESOLVED |  | Close: -
785 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrectly matched. EG Serial_No => Protective Material This is carried through to the Waste Water and Storm Water manuals. | Included | Resolved in current version. | 2.5.1 Equipment | Change made document updated
786 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrect matched. | Included | Resolved in current version | 2.5.1 Equipment | Change made document updated
787 | Potable water | Vol 1 | In our AMIS we are planning to utilize two fields to describe valves. Valve Type: Eg Isolation, Scour, Toby, Pressure Reducing, etc .. Valve Mechanism: Eg Gate, Knife, Ball, Air Release, etc.. Rather than combine function and mechanism into one attribute field. | Sector Discussion | to be discussed with the TWG refer to 630, 631 | 2.5.3 Valve | More information required for a decision |  | refer 630/631 | refer 630/631 |  | Action - George to talk to Noel | GISSA Review Valve details as per CCC and Tauranga ref detail | Completed MW 22/6/17
788 | Potable water | Vol 1 | Where are readings recorded? Should there not be an attribute for the latest meter reading and date it was recorded. | Noted: no action required | As Constructed' data not operational data. | 2.7.1 Instruments | No action
789 | Potable water | Vol 1 | Incorrect reference: Should be 1.8 | Included | Resolved in current version. | 2.8.2 Matching to Existing Infrastructure | Change made document updated
790 | Potable water | Vol 2 | Terminology Constancy: In Vol 1, Section 1.8, a lot of the elements below are referred to as "Asset Classes" They are also referred to "Asset Classes" in the attribute and validation file format. Suggest change "Categories" to "Classes" | Noted: no action required | Standards updated to a consistent approach | Table 3: Asset Hierarchy Framework | No action
791 | Potable water | Vol 2 | I am unsure what this means. Can there be more explanation of the content in the Rules column. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
792 | Potable water | Vol 2 | What is Rule 2? Ensure on what this means. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
793 | Potable water | Vol 2 | How are these levels recorded in the date table 7? (ie Network, facility) Table 7 only links back to an individual asset level (Unique_ID) There does seem to be merit to applying Risk to a network level, sub-network level or at a facility level? Could also apply this thinking to Criticality definition? | Sector Discussion | Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance or criticality | No Specific Reference | More information required for a decision
794 | Potable water | Vol 1 | All three standards use this sentence correct for all 3 waters | Sector Discussion | Please provide further information. | Executive Summary | More information required for a decision |  | haydn to follow up | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: -
795 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.7 Heirarchy | Change made document updated
796 | Potable water | Vol 1 | Believe there should be a level between asset group and asset type (see my hierarchy tree). Also Asset Class & Asset Category is not specified in the hierarchy. | Sector Discussion | Please provide further information relating to your hierachy. | 1.7 Heirarchy | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
797 | Potable water | Vol 1 | Defined as Asset Type on previous page | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
798 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
799 | Potable water | Vol 1 | What information is required to determine if a tank/reservoir is a civil structure or not. i.e. How to determine if a tank/reservoir is a containment structure or a retaining structure. | Noted: no action required | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | 1.8 Theme Structure | No action
800 | Potable water | Vol 1 | Will there be reference documents for treatment plant assets? | Noted: no action required | Not at this point in time | 1.8.1 Other Asset Classes in the precinct of a Water Network | No action
801 | Potable water | Vol 1 | How would an asset that could be represented as more than one of these be represented. e.g. would a scour be a single asset (pipe) or two (pipe and fitting) or would that be up to the Client to determine | Sector Discussion | More information is required to inform a way forward | 1.9 Data Principles | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
802 | Potable water | Vol 1 | water | Included | changed to Water. | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
803 | Potable water | Vol 1 | water code lists | Included | Section under review. | 2.1.5 Attribute Data Fields | Change made document updated
804 | Potable water | Vol 1 | Definition etc missing | Included | Section under review. | 2.1.6 Attribute Data Type Definitions | Change made document updated
805 | Potable water | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils/contractors to use an ESRI based product, or something else? if not suggest removing ESRI from this sentence. | Noted: no action required | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for | 2.1.7 Metadata Definitions | No action
806 | Potable water | Vol 1 | Section 2.1.4 | Included | Section under review. | 2.1.7 Metadata Definitions | Change made document updated
807 | Potable water | Vol 1 | Does this code list include options for multiple networks? or is each network to be recorded as an individual project? | Included | ProjectID already included Yes it does - added multiples in Project Table | 2.1.9 Project Attributes | Change made document updated
808 | Potable water | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
809 | Potable water | Vol 1 | See note regarding Design Company above. | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
810 | Potable water | Vol 1 | Should this not be a code list? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
811 | Potable water | Vol 1 | What is the definition of cost for contractors? What is the value of capturing this when there are no controls around application of defining cost? | Included | Reviewed and Noted for Inclusion Financial code lists for ODRC, ORC and OC are included | 2.1.10 Common Attributes | haydn
812 | Potable water | Vol 1 | What exactly are the photographic references? This appears to be a 250 Char field so completely useless for using this data. Is this intended to be used in a similar way to 'Unique ID' as a reference number for the photo? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | close | DUPLICATE
813 | Potable water | Vol 1 | Again using a 250 character field means the data could be all over the place. Example uses this field to record specific instructions to access the asset. To me that should be a separately labelled field. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
814 | Potable water | Vol 1 | See note regarding this field on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
815 | Potable water | Vol 1 | See not for Design Company on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
816 | Potable water | Vol 1 | Would a T not be a fitting instead of a node? | Noted: no action required | T is a fitting but also an intersection so therefore a node. | 2.4.4 Node | No action
817 | Potable water | Vol 1 | Is there a particular reason that Valves etc do not 'break' pipes? When works are undertaken (renewals in particular) actual physical assets provide useful 'real world' demarcation points. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | 2.4.5 Pipe | No action
818 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram |  | modify diagram | Discussed during the May 1-3 workshops Noted no further discussion or action required
819 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram |  | modify diagram | Discussed during the May 1-3 workshops Noted no further discussion or action required
820 | Potable water | Vol 1 | What are the reasons for Internal Diameter, Nominal Diameter and Nominal Bore all being required? Are these all not essentially the same thing? | Sector Discussion | The range of diameter types are an analytical requirement for interogating assets through a range of lenses | 2.4.5 Pipe | More information required for a decision |  | fields are conditional, Wellington Water to provide guidelines | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30
821 | Potable water | Vol 1 | Would this class also cover assets that provide access but are not part of a dam or weir wall? Suggest that this be added to the wastewater specification as well. | Included | Agreed 9/3/2017 | 2.3.6 Tunnel | Comment clarifed in potable water document and tunnel asset class added to wastewater document
822 | Potable water | Vol 1 | Should purchase date be included? Do some warranties apply from date of purchase? | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision |  | close | DUPLICATE
823 | Potable water | Vol 2 | a' instead of 'the' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
824 | Potable water | Vol 2 | Why is infrastructure for collection and treatment not covered? These assets are integral to potable water supply and asset managers need quality information that they can use to make asset management decisions. Sentence also contradicts itself. "does not cover infrastructure...treatment of water, except in the case of..infrastructure to treat water". | Noted: no action required | There is a desire to create anoter standard which includes these assets, as there is in th ebuilding environment for Large Commercial Buildings and Industrial Buildings | No Specific Reference | No action
825 | Potable water | Vol 2 | Pressure is more of a Quality provision. Suggest moving this into Quality. | Noted: no action required | Pressure is a Design Attribute How it performs against that design is a Design Performance attribute | No Specific Reference | No action
826 | Potable water | Vol 2 | Delete extra "that" | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
827 | Potable water | Vol 2 | outlines' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
828 | Potable water | Vol 2 | investment' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
829 | Potable water | Vol 2 | replace' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
830 | Potable water | Vol 2 | Influences | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
831 | Potable water | Vol 2 | Replication | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
832 | Potable water | Vol 2 | General comment - risk and criticality are closely linked. Are they really different things? Just use one term and get rid of the other. | Noted: no action required | No action required. Decision to separate two schemas taken at project management level | No Specific Reference | No action
833 | Potable water | Vol 2 | Table is missing a 'comments' field | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
834 | Potable water | Vol 2 | Inconsistent with the wastewater and stormwater measure headings (Rating). Suggest same terminology is used across all three waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
835 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
836 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would" more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
837 | Potable water | Vol 2 | Is this a different manual than the 3rd Edition New Zealand Pipe Inspection Manual? If not use full document name as used in the wastewater and stormwater documents. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
838 | Potable water | Vol 2 | Should this not be in line with the wastewater and stormwater measures? (IIMM 2015) | Noted: no action required | No action required. This is the same document | No Specific Reference | No action
839 | Potable water | Vol 2 | If this information is to be completed by field (maintenance and operations) staff they are unlikely to know if works have been deferred or will be deferred. | Noted: no action required | Not an attribute of these standards | No Specific Reference | No action
840 | Potable water | Vol 2 | Replace "data" with "cost" | Included | Documents have undergone a full publishing edit | Haydn | No action
841 | Potable water | Vol 2 | Stormwater document includes complete code lists for these items. Water and wastewater do not. | Noted: no action required | Code lists updated | List of Code Lists | No action
842 | Potable water | Vol 2 | Not convinced that this is a useful or practical schema, at least for potable water assets. Perhaps don't bother with this and just use demand schema instead? They are similar. | Noted: no action required | Utilisation and Demand are different decision elements as explained in the standards. | 3.2 Utilisation Schema 3.3 Demand Schema | No action
843 | Potable water | Vol 2 | Missing sentence from WW and SW Volume two further explaining the utilisation schema. " Utilisation is measured using time or other base unit measured against a known availability." | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
844 | Potable water | Vol 2 | "Current Utilisation" at an asset by asset level would require an impractical amount of monitoring. i.e. are we really going to know average and peak flows through each and every length of water pipe? | Included | This is an analytical construct, and easily monitored in an analytical sense at whatever frequency required for intervention circumstances | 3.2 Utilisation Schema | An explanation of Data Science will be provided for at the Technical Working Groups
845 | Potable water | Vol 2 | Partly a function of the pressure in the pipe. Are we really going to know potential utilisation for each and every length of water pipe? | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
846 | Potable water | Vol 2 | Don't think it's possible to determine this for each and every asset. At least for potable water assets. | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
847 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets without extensive modelling. Alternatively would require data from modelling software. | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
848 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
849 | Potable water | Vol 2 | This does not seem to be an relevant measure for water demand in a metropolitan situation. | Included | Completed - see Demand section | 3.3 Demand Schema | No action
850 | Potable water | Vol 2 | Criticality varies across all three waters. While a data centre may have a higher water criticality than a hospital, the opposite would be true of wastewater. | Included | Correct, which is why each asst class is treated differently when an analysis of things like criticality are conducted across a network | No Specific Reference | No action
851 | Potable water | Vol 2 | Of risk & criticality, which are both similar schema, criticality is much quicker and easier to measure and much less subjective. I would be tempted to exclude risk or use it with caution in decision-making compared the use of other schema. | Noted: no action required | It will be required n some circumstances, and here it is defined when you do | No Specific Reference | No action
852 | Potable water | Vol 2 | Ln only needs to be 1 due to 1,5 rule | Included | Completed | No Specific Reference | No action
853 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
854 | Potable water | Vol 2 | Even at a score of 3 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
855 | Potable water | Vol 2 | Even at a score of 3 is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
856 | Potable water | Vol 2 | Even at a score of 4 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
857 | Potable water | Vol 2 | Not convinced there is much use in this table, at least for water assets. Most revenue is derived from consumption so would be associated with a meter and the usage of water. | Noted: no action required | No action required. Organisation can choose how revenue is recorded against an asset | No Specific Reference | No action
858 | Potable water | Vol 2 | So this is theoretical revenue? Not actual revenue? | Included | Actual, Forecast and Budget included in financial code lists | Code List 6: Bases of Cost | No action
859 | Potable water | Vol 2 | Delete this text. Captured in the field below. | Included | Completd | No Specific Reference | No action
860 | Potable water | Vol 2 | This whole section is confusing. It's trying to do two things at once. Individual asset attributes and whole of network attributes should be separated out. | Included | Network analytics are completed on individual asset analytical interogations | No Specific Reference | No action
861 | Potable water | Vol 2 | So its not intended to be used for decisions at an individual asset level? If not, strip out all the individual asset measures and move somewhere else. | Included | It is in some circumstances to be used on an individual assetID | No Specific Reference | No action
862 | Potable water | Vol 2 | This table seems to be a jumble of attributes for individual assets and DIA measures which are taken for the network / organisation as a whole. I'm not really sure the whole of network / organisation attributes are metadata. Delete DIA whole of network / organisation attributes or move to a separate table. dlane: Some data items are network wide while others are asset specific. If data capture is required these should be split into separate network and asset tables. | Included | Volume 2 is completed in these draft standards. Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance | No Specific Reference | No action
863 | Potable water | Vol 2 | How does this field work? Is it the duration of the most recent unplanned interruption, the the total duration of all unplanned interruptions (from field below) or the average unplanned interruption duration? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
864 | Potable water | Vol 2 | How does this field work? Is it the connections affected in the most recent unplanned interruption, the total connections affected in all unplanned interruptions (from field below) or the average number of connections affected in unplanned an unplanned interruption? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
865 | Potable water | Vol 2 | Delete this field. It makes no sense and is confusing. Field Ref 11.04 does the job. | Included | Table updated | No Specific Reference | Change made document updated
866 | Potable water | Vol 2 | Need to include the units of measure. kPa,psi etc | Included | Tables updated in code lists of Vol 2 | Code List 44: Description of Design Performance – Engineering Unit of Measure | psi to be added
867 | Potable water | Vol 2 | Surely this field would only be used for a reservoir asset. Not, say, a pipe supplied from the reservoir. Please clarify the use of this field. | Included | It can be both | No Specific Reference | No action
868 | Potable water | Vol 2 | Not sure it would come from Repairs and Maintenance Schema. | Noted: no action required | This MoH included in the Service Performance Attributes | Data Table 11: Service Performance Attributes – Functional | No action
869 | Potable water | Vol 2 | Confusing to have it on this table. So this field is used at a facility level not an individual asset level? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
870 | Potable water | Vol 2 | Confusing to have it in this table. So this field is used at an organisation level? The question of whether there is an adequate backflow prevention programme doesn't relate to individual assets? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
871 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
872 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
873 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
874 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
875 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
876 | Potable water | Vol 2 | This is not a demand attribute, its abstraction/take and is source based. as you've said that this is potable water assets only I don't think it's appropriate here. | Noted: no action required | A source is an asset (e.g. a reservoir), abstraction is the process, demand is the level of abstratcion on the asset - each are different and can apply to a pipe connection no less (e.g. a school) | No Specific Reference | No action
877 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
878 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
879 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated?. | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
880 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. Move to financial schema? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
881 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
882 | Potable water | Vol 2 | Differs from tables in the stormwater and wastewater specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Tables are very similar, with the asset specific elements being applied when required. Tables have been normalised where possible | No Specific Reference | No action
883 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
884 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
885 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
886 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
887 | Stormwater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Included | Reviewed and Noted for Inclusion | 2.1.7 Metadata Definitions | Change made document updated
888 | Stormwater | Vol 1 | 2.1.4 | Included | Reviewed and Noted for Inclusion | 2.1.6 Attribute Data Types Definitions 2.1.7 Metadata Definitions | Change made document updated
889 | Stormwater | Vol 1 | Does this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Noted: no action required | Either | 2.1.9 Project Attributes | No action
890 | Stormwater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
891 | Stormwater | Vol 1 | See note regarding Design Company above. | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
892 | Stormwater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
893 | Stormwater | Vol 2 | Heading (see water and wastewater) | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
894 | Stormwater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or at code should be a single character as per the water measures. Should be consistent across all 3 waters | Included | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
895 | Stormwater | Vol 2 | Differs from table in wastewater and water specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
896 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
897 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
898 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.8 Theme Structure | Change made document updated
899 | Wastewater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Noted: no action required | Not the intention. The intention is to outline why the field is structured in this way | 2.1.7 Metadata Definitions | No action
900 | Wastewater | Vol 1 | 2.1.4 | Included | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | 2.1.7 Metadata Definitions | Change made document updated
901 | Wastewater | Vol 1 | Doe this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Sector Discussion | This is an operational question related to an organisations ability to import data into their asset management systems. For immature organisations likely to be project by project, for mature ones project agnostics | 2.1.9 Project Attributes | More information required for a decision |  | Close | Discussed during the May 1-3 workshops Noted no further discussion or action required
902 | Wastewater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
903 | Wastewater | Vol 1 | See note regarding Design Company above. | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
904 | Wastewater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision | [7 empty] | No further information provided
905 | Wastewater | Vol 2 | Not a valid measure for wastewater utilisation. | Included | Updated | No Specific Reference | No action
906 | Wastewater | Vol 2 | Criticality varies across all three waters. for example, for wastewater a hospital would have a higher value than a data centre. while water could score differently | Noted: no action required | No action required, based on the importance of the building as defined in the Buildings standard | Code List 13: Facility Importance Rating
907 | Wastewater | Vol 2 | Heading is different from that used in water and stormwater documents. Suggest standardising for simplicity. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
908 | Wastewater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or code should be a single character as per the water measures. should be consistent across all 3 waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
909 | Wastewater | Vol 2 | Differs from tables in the stormwater and wastewater spec. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
910 | 3-Waters & Buildings | Vol 1 & Vol 2 | An obvious mistake in the Potable Water Metadata Std is that someone has put the Residential Executive Summary in it????. | Included | Included in the draft Standards | Executive Summary | Change made document updated
911 | 3-Waters & Buildings | Vol 1 & Vol 2 | You are asking for public to comment on missing attributes within meta data tables. Considering you have spent 12500 hours on this, could you please comment if all the attributes defined by Australian standard ADAC have been included? http://engicom.com.au/adac/government-organisations I appreciate your list of assets may be more comprehensive. If any of the asset attributes defined in ADAC are missing there are like to be areas where assets will miss vital information for future analysis. If you have used IPWEA in your decision making process it would be useful to include this information on your website so it doesn’t look like you are reinventing the wheel. Well done on sorting out the asset management data through the lifecycle of each asset. Local councils desperately need national standard for asset capture, storage and access to information. | Included | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. | General | No action
912 | 3-Waters & Buildings | Vol 1 & Vol 2 | I’d like to provide feedback on the proposed standard. However I caveat this as coming from a hands on GIS Practitioner View, which may be different to my colleagues here at LINZ. I think it will be incredibly important to incorporate good practice guidance at some stage on how these standards are practically implemented. Ideally providing an empty or working dataset that a person can take, open with their system and populate. Generally when you go to create the schema in a system you’ll follow it and interpret changing the types, field lengths, column names etc. My request is based on recent experience. Often this step is left out, and implementation of the standard fails. This was my experience with the ANZLIC geospatial metadata standard, 10 years after its release 95% of GIS practitioners in New Zealand could still not easily implement the standard within the most common desktop GIS software. The Australian based tool provided did not support NZ requirements. We ended up shoving the required text into a single desc field in an inappropriate manner, ending up with a total mess. This may require getting software providers onboard with adding these into their pre-defined templates for users of the most common software providers. If you could imagine in the same way we create a LINZ letterhead letter in MS Word. My 2 cents from a GIS data capture perspective and I am happy to discuss this further if appropriate, otherwise happy to leave it as this. | Noted: no action required | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | N/A | No action
913 | 3-Waters & Buildings | Vol 1 & Vol 2 | In each of these documents out for proposal, there is reference to standard codes for things like asset type and material (“the CODELIST”), but none of these are available yet – will this be available before consultation closes? | Included | Code lists are included Attributes to be discussed | General | Gauge input from next review
914 | 3-Waters & Buildings | Vol 1 & Vol 2 | This is a great initiative and will aid everybody involved in the area of Asset Management. I would ask is has there been any coordination with the Institute of Public Works Engineering Australasia as they have a system already in place called ADAC (http://www.engicom.com.au/adac). Could your framework be an extension to that so we can leverage what software companies have developed already to support that schema. It appears that a lot of the info you are capturing has already been covered, why reinvent the wheel? | Noted: no action required | IPEWA Australisia has representation around the table, and has had for 2 years | N/A | No action
915 | 3-Waters & Buildings | Vol 1 & Vol 2 | Structure of the standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes. Further to the split of water sectors there is an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group has specified that a single document that focusses on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. In terms of usability our end users are expecting a data framework that is easy to understand and use. In the proposed layout we are expecting the standards will be met with cost burdens. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
916 | 3-Waters & Buildings | Vol 1 & Vol 2 | 2. Applicability of volumes 1 and 2 The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was about creating an as-built data set for industry that can be used to collect field data, most of the workshops evolved around this input. Volume 2 for derived data has had limited industry input and we do not believe it is ready to be published. Further work on this volume is therefore required. | Noted: no action required | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. | General | No action
917 | 3-Waters & Buildings | Vol 1 & Vol 2 | 3. Data hierarchy The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. As presented at the workshops, an example of how this could be applied to the tables is outlined below: Level 0 (system/layout specific data – master data. Typically assigned by organisational systems and numbering or coding rules - contains the common data set) -Inventory identification number / -Functional location i.e. Network type (water, wastewater, stormwater) / -etc. Level 1: Data categories, in example: “Technical/physical” i.e. Containment structures (available technical core classes) (or) Operational data (or) Financial data etc. Level 2: (attributes) Minimum required attributes, in example: -Function / -Depth / -Material / -etc. Level 3: (attributes) Conditional attributes, in example: -Diameter if circular / -length and width if not circular / -Joint type (if the structure has joints) / -etc. Level 4: (attributes) Optional attributes, in example: -Manufacturer / -Model/part number / -etc. | Included | Asset Classifications have been defined in the Standards Tables are to be discussed at length | No Specific Reference | Sector discussion
918 | 3-Waters & Buildings | Vol 1 & Vol 2 | 4. Terminologies and definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need to be agreed. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
919 | 3-Waters & Buildings | Vol 1 & Vol 2 | 5. Graphical representation and its accuracy This subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. Graphical representation should be removed from the document; the purpose of this standard is collecting metadata of asset physical properties. Geospatial requirements are a standard in its own right and even providing these as guidelines does not seem appropriate. | Included | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH | General | No action
920 | 3-Waters & Buildings | Vol 1 & Vol 2 | 6. General content 1.“Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. 2. The units of measure have not been covered during the workshops. Further input may be required before the draft is ready for public release. 3. Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and the implementation may not be practical. 4. Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. In many instances data will be collected in-house. 5. Australian examples and photos should be replaced by New Zealand examples. Word choice such as “savvy” (used often) is not the best choice. Some of the language used needs to be reviewed in order to retain the standard’s professionalism. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included | General | No action
921 | 3-Waters & Buildings | Vol 1 & Vol 2 | 7. Implementation The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate has not been considered where organisations may choose not to collect certain information for low risk assets. An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard | Noted: no action required | This is not within the scope of these standards | N/A | No action
922 | 3-Waters & Buildings | Vol 1 & Vol 2 | We believe there is a reasonable amount of work that has not been completed, such as standard definitions, which may lead to inconsistencies between the water organisations. Without this work being completed the documentation that has been produced could only be used as a guideline or a code of practice. | Noted: no action required | All definitions have been standardised and normalised | No Specific Reference | No action
923 | 3-Waters | Vol 1 & Vol 2 | However, page 141 of Potable Water Volume 1 As-constructed/As-built references code lists for 3 waters assets that can be reviewed in a supplementary document called 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016 Is this document available for download or can it be emailed to me? I would like to cross-check what is in this code list against the attribute tables to assist with my review. | Included | Code lists are included | General | Change made document updated
924 | 3-Waters | Vol 1 & Vol 2 | As-constructed schema should not be a separate document, and should recognize that many assets are created though term contracts not just greenfield build. We should not separate “as-constructed” from other elements of the standard because this perpetuates last century’s practice of asset management being about the asset whereas it is about the service enabled by the asset. We should modify the “as-constructed” schema to recognise that construction happens both in new builds and in renewal term contracts and the information should support both efficiently. I am not convinced of the value of separating the standards into two parts. While as constructed data is central to an asset information system there are few transactions that use it in practice. Most construction projects will use subsets of the inventory tables, performance based construction projects will also use the condition and performance tables, term PPP or BOOT contracts will use almost the entire standard. This means there is no one to one connection between projects and elements of the entire data schemas so the split of the source documents is artificial. I think there is a serious downside to separating the two documents that drives us towards a combined view. Asset management is all about delivering services that require significant assets. Separating as-constructed from performance data perpetuates past practice that asset management was about having assets in good condition, whereas it is about having assets in sufficient condition to deliver targeted services. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
925 | 3-Waters | Vol 1 & Vol 2 | Another challenge with this proposed separation and the associated “constructor” reference fields is that for roads and 3 waters, though to a lesser extent buildings, much infrastructure is created through renewal or replacement programmes. For example for State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. This means that we need to think seriously about replacing the “constructor” record in the “as-constructed” table with a reference to an “Asset Intervention” record as described elsewhere in my comments. Unless this is done there will be not be normalisation of records relating responsibility for modification of inventory, a ridiculous amount of duplicate records created from term contracts where much inventory is created, and a mismatch between the constructor records in the “as-constructed” schema and those of the maintenance schema, when in term network management contracts these are the same constructor. The same duplication will occur when the same constructor creates many inventory records as occurs in term contracts | Noted: no action required | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | No Specific Reference | No action
926 | 3-Waters | Vol 1 & Vol 2 | The categories of data type should be simple, exhaustive and mutually exclusive so should vulnerability and resilience stand alone? The proposed “global meta data schemata” classifies data into several categories. This is a necessary and good thing because it help users appreciate the scope of the data and find the elements they may be interested in. To do this well the elements must be simple, described in commonly understood language, cover the field of interest, i.e. be exhaustive, and be mutually exclusive, i.e. not have definitions that overlap or require subtle nuancing. | Included | Included in the draft Standards | General | No action
927 | 3-Waters | Vol 1 & Vol 2 | Vulnerability - risk There is an open question in the document as to whether vulnerability should be drawn out as a standalone data category, when it influences risk. I do not think it should be standalone because this then makes “risk” become “risk other than vulnerability” and I think that is a bit silly. I certainly agree that vulnerability is important. I think it so important that we should draw it out in the risk or resilience categories. The high level approach to risk is to consider likelihood and consequence. Simplistically consequence conflates: • vulnerability of service, and • impact from reduction or loss of service and vulnerability of service conflates: • vulnerability of infrastructure (considering network effects), and • availability of alternate infrastructure or alternate services. I think we should draw out these or similar elements of risk for those elements of infrastructure type that potentially have a consequence greater than tolerable. This might mean (in the transport context) arterials and above in a transport world because of their importance to the economy and society. Effectively this creates a level of service gap around vulnerability, the very gap that rental companies advertise as being closed when they proclaim on their hoardings that a building to let is 85% EQ code compliant. | Included | Included in the draft Standards | 4.2 Vulnerability Schema | No action
928 | 3-Waters | Vol 1 & Vol 2 | Resilience - performance Resilience is a service level, or a strategic goal. As a service level it should be within the performance elements of the data standard. I know that it has prominence because it is an important element of performance, but so too are accessibility and safety for transport, or availability of supply or health for water. As a strategic goal it is a driver of service levels. | Included | Resilience is a state and requires measurement The level of service is subject to the level of service any organisation seeks to apply, and an invetment plan to meet that level | 4.5 Resilience Schema | No action
929 | 3-Waters | Vol 1 & Vol 2 | Utilisation is multifaceted and requires enhancement The definition of utilisation given in the draft standard is the proportion of an assets available capacity that is actually being used. I think that there will need to be some clever messaging to ensure that the unit of capacity chosen is understood for infrastructure in different circumstances. Using a transport example provides an illustration of this. Over 60% of New Zealand’s roads are classified as access or low volume access roads. This means that they have less than 1000 vehicles using them per day. A single lane has a capacity of about 1400 vehicles per hour, depending on its configuration, i.e. on the proposed definition of capacity most roads have a daily utilisation of about 1.5% yet these roads represent the last and/or first mile of most trips and so are critical to our economy and society. The level of utilisation will always be low simply because there are rural and urban areas with low population that are connected to market or work place. Even with planned intensification of central urban areas daily utilisation might only rise to 5%. This is analogous to the smallest element of supply or removal for potable or waste water. Also, where there is suppressed demand because demand exceeds supply, e.g. on congested transport networks (whether roads or busses), we may report 100% utilisation, but that is bad because the potential benefit of suppressed trips is being lost or costing more. In a water example we may constrain the development of business when supply is inadequate for development yet fully used by current development. Together these factors mean that we have to be careful about the utilisation measure and how we use it alongside other measures at a local and network level, a simplistic approach won’t do. I think this section of the draft standard needs work to draw out these issues. In addition we need to consider how utilisation and performance metrics are used to optimise asset investment decisions. | Noted: no action required | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | No Specific Reference | No action
930 | 3-Waters | Vol 1 & Vol 2 | Inventory Interventions At the moment there are two types of works records, those recorded as maintenance and those associated with the as-constructed fields. I think we should consider what we want from the recording of “works” or inventory interventions because I expect that will lead to an improved data structure with one form of works interventions record. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
931 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Planned, current, completed or abandoned works so we can fuel the nationwide forward and current works viewer enabling better coordination of works and reduced disruption of customers whether the works are construction, renewal or maintenance. Interventions on inventory are a process that creates or modifies inventory. Much information is required about the process as much as of the fact that it creates inventory. E.g. the forward works viewer being developed to display proposed and current works have time, duration, and place elements of information as well as descriptive information about the constructor and infrastructure being modified or created as reflected in the proposed “as-constructed” schema. | Included | Statement noted. Already done in Repairs and Maintenance schema. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
932 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Responsibility for management of infrastructure, noting that ownership may pass to a client when inventory enters service, but responsibility for maintenance may extend beyond the transfer date | Noted: no action required | Noted | No Specific Reference | No action
933 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • A hierarchy of works and tasks that distinguish a term contract (or work) from a work task within it so that the work identifies responsibility, type of work, stage of work etc, and the task the date and type of work done linked to the infrastructure impacted. I think this allows better alignment with supplier’s management systems, responsibility for work done, and supports many forms of contract from term based contracts to single task contracts. This also enables security to be built into system for data exchange. This is important because for most infrastructure networks (buildings aside) most new infrastructure arises due to renewal works and not due to greenfield construction. | Included | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
934 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
935 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
936 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Types of inventory intervention with appropriate records, including, but not limited to: o Physical works, probably the most common type o Waste or abandonment, associated with infrastructure being removed from the inventory and reflected in a valuation as a write-off o Inventory received from third parties, e.g. as a result of transfer from development of a new residential area to a council, or the transfer of responsibility of a road from a local authority to the Transport Agency as a State highway o Inventory transferred to third parties, e.g. the transfer of responsibility of a previous State highway to a local authority on completion of a State highway bypass. I acknowledge that “inventory interventions” is not the best term and that a better one should be found. | Included | Included in the draft Standards | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
937 | 3-Waters | Vol 1 & Vol 2 | Assessments There is an opportunity to introduce a concept of an intervention type of “Assessment”. This arises because there are many instances where responsibility for some parameter in many of the tables is explicitly referenced, yet is essentially the same information in each case. This information is who changed the parameter, when, why, as a result of what process…? This proposed approach will enable normalisation of data describing the assessment of condition or performance (whether current or forecast), valuation, risk or any other metric in a standard way. It will then identify the provenance and responsibility for each. This proposal is much the same as that for “inventory interventions” in that it suggests that the core information is about the process leading to the metric in the data and this should be recognised. | Noted: no action required | Assesments are (or interventions) are subject to the element being interrogated (e.g. condition). The standards have attributes which capture these. These will however be predominantly the focus of the work when develop-ing Volume 3 | Data Table 1: Condition Attributes & Code List 17: Condition Rating – Methodology | No action
938 | 3-Waters | Vol 1 & Vol 2 | Supply of as constructed data I think that we shouldn’t mandate the form for the supply of as constructed (or other data) but rather the relevant metadata describing its provenance, quality etc. If the form is mandated then it would require an absurd level of record keeping and compliance from term contractors who create many new assets. E.g. for State highways we use term contractors who create the vast majority of new surface infrastructure each year. For State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. Suitably qualified and quality assured staff from contractors enter the as-constructed data directly into our inventory system, and this isn’t shown as an acceptable method of delivery yet it patently is. One of the purported benefits of meta-data standards is that it enables business to business transfer of data. Defining the transfer of data on a disc seems to fly in the face of these benefits and the advance of B2B technology. Similarly I would think that NIU doesn’t want to be involved in contractual requirements for each form of contract, rather whether information is being managed well and is fit for purpose. I think the supply of data section starting on page 1 of volume 1 needs review. | Noted: no action required | Data format (form here) is not within the scope of these standards | General | No action
939 | 3-Waters | Vol 1 & Vol 2 | Asset management I think the sections of the standard on asset management need a revision to better reflect: 1. That customer service at least long term cost is the goal, and not maintenance of asset condition, noting that the two are related. 2. Investment decisions made in a customer service centric world. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
940 | 3-Waters | Vol 1 & Vol 2 | Customer service focus The various diagrams, for example figure 3 on page 24 of volume 2 is written in very economic language around the return for investment of public funds. This is of course critical, but loses the narrative that relates providing customer service that is economic. | Noted: no action required | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. | No Specific Reference | No action
941 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: I think the steps in the above referenced diagram, and the description on the preceding pages are missing an element and that is what is being targeted in terms of service levels and how this target is established. Or alternatively (as a poor second best) are missing the inputs describing the economic and social benefits of different service levels experienced by customers. If these were present then the analytics could do the required work. This step is required to establish the performance targets referenced in the performance elements of the standard. Eg what is the optimal economic service level for service outages considering investment to reduce the frequency, duration and impact of service outages against the social and economic impacts of these. This step is difficult and complex but needed none the less. It requires decisions about the relative weight to be given to quasi commercial models or economic models. It requires significant analytics to be undertaken to determine the relationships between costs and benefits of different levels of service for different types of customers in different circumstances. Much of these analytics are represented in the economic evaluation manual used to determine the economic value of transport proposals in New Zealand. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | No action
942 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: The service led approach enables a more informed discussion with customers about expectations of service level and the cost of these than a black box economic model. It essentially proposes a three stage approach: (See figure in word document) This recognizes that information is never perfect to enable ideal one off analytics because customers’ needs, systems and contexts change so what might be optimum now likely won’t be at another time. The aspect of service level target should be reflected in the analytics framework. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. | No Specific Reference | No action
943 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world I think that section 1.8 needs some rework though many aspects are worth keeping. There is significant reliance on the metaphor that as assets deteriorate and consequently the maintenance expense to sustain targeted service levels increases there is a sweet spot between condition and maintenance cost. I think we need to recast that metaphor in a customer centric world and recognize that the sweet spot is tautological because the definition used for condition grade 5 is that it has failed or soon will so it is no coincidence that replacement is needed there. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
944 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world The proposed standard presents a theoretical approach to stochastic analysis. This style of analysis is becoming common place. The standard might reference the UK’s Highways Efficiency Maintenance Programme website, especially this url: http://www.highwaysefficiency.org.uk/efficiency-resources/asset-management/life-cycling-planning-toolkit.html That site includes standard tools for “stochastic analysis” of renewal programmes using the “5-step condition rating”. While the text is all about roads the processes are generic. With translation, or a babel fish (as Douglass Adams might say) they are as applicable to buildings as to roads. The tools on that site are of course single factor analyses as condition based analytics generally are. There is no single or multifactor customer service optimisation (e.g. skid resistance and ride comfort for roads) that assists planning in a constrained environment or in an environment where value for money matters, but it is a straight forward approach to estimating the works required to sustain performance. That reference, or a more applicable one, or a derivative of it, would go some way to making the theoretical text in the proposed standard tangible. | Noted: no action required | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
945 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If the text were recast to be more customer service centric it might use the following approach. The two most important decisions to intervene with some form of monitoring or works when managing a network to provide customer service are: 1. When delivered service levels have or will drop below the targeted level or there is too great a risk that they will 2. When, despite the targeted service level being met, it is cheaper in the long run to intervene, or there is an unacceptable risk that costs will rise unless an intervention is made Intervention decisions can initially lead to a monitor, maintenance, renewal or improvement interventions, whichever is part of the least long term cost intervention strategy. A more colloquial way of putting this is only intervene if its broken, or cheaper in the long run. | Noted: no action required | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
946 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world Transport examples of the two decision types are: Ensuring the service is delivered to target. • Replacing the tires on your car when the tread depth has reduced and become unsafe, or ahead of winter when risk is greatest when tread depth has almost become unsafe • Continuing to monitor the change in direction of a river beside a roadway that may ultimately risk scouring of the road formation in order that preventive works can be taken when necessary and most cost effectively to preserve the transport route • Water cutting the excess bitumen off a road to restore the prominence of the chips so tyres grip these rather than “float” on the water film when the road is wet in order to restore the skid resistance of the road surface. • Resurfacing a road when the skid resistance of a road is falling and is either unsafe or will become unsafe before the next opportunity to intervene because the stones have polished Ensuring that delivery of the service is at the least possible long term cost. • Replacing the oil in your car engine even though it is performing well in order to forestall engine damage • Monitoring the condition and maintenance expenditure on deteriorating roads so that and expected renewal works can be designed and timed to be cost effective long term • Sealing cracks in an asphaltic concrete road surface to reduce water ingress to the pavement which would cause the pavement to deteriorate rapidly and require more expensive repairs • Rebuilding or replacing the structural layers in a pavement when this is the cheapest long term cost because deterioration in pavement strength is leading to the need for significant and increasingly frequent and costly repairs and resurfacing treatments to maintain service levels | Noted: no action required | And, is the intention of the analytical foundations set down for Volume 4. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
947 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If discussion of the type inferred in the above table were included then the standard would be more tangible to users and better focussed on customer service, the goal of asset management. I think it worth the discussion including reference to or guidance on the economic decision to continue to maintain infrastructure or to renew or replace it on a site specific basis. The IIMM might be suitably referenced. When funds can be used on other investments outside asset management of the infrastructure in question then we look for the sweet spot where the net present value of the renewal plus reduced subsequent maintenance stream is better than the present value of the continued and increasingly expensive maintenance stream. This should be included because it can be implemented site by site for significant investment, and needn’t rely on sophisticated network level analytics and data, though it requires some to describe the relationship between condition, time and maintenance cost. This analysis that maintenance costs typically increase as condition worsens is shown in the following indicative diagram as indicated in the draft standard metaphorical diagrams. This shows there isn’t a sweet spot from this relationship alone. Another factor is required for optimisation and that is the present value of the replacement cost option on a site specific basis, or long term budget on a network basis. (see figures in word document) | Noted: no action required | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
948 | 3-Waters | Vol 1 & Vol 2 | Global Schemata The global asset metadata schemata diagram on page 16 of volume 2 appears out of place with the prosaic listing of detailed data requirements. If it were fully developed as an idea in the text you would expect it to tell a story about why certain data elements are required. No such story is conveyed, so the inference is that whatever data is in the standard will enable such analysis, if that were true then the benefit of the advanced analytics would be small. That seems odd. Does this description add value? | Noted: no action required | The diagram provides context for the detail that follows There are some who are already applying this level of complexity to decision-making. | 1.4 Context of Asset Data and Analytics | No action
949 | 3-Waters | Vol 1 & Vol 2 | Network level performance targets The standard for service performance p101 vol 2 as proposed enables the measurement of performance against a target. This is good. However there is no reference to what good looks like so the measurements are just that. It may be useful to add records that: • Enables the categorisation of target service levels • Set service targets for each performance aspect for each category This would provide the data required to enable reporting of whether the service provided was good enough or not, in a situation where targets differ by category. The One Network Road Classification framework developed by REG for transport classifies roads into 8 categories and sets targets for each. | Noted: no action required | Levels of service are policy decisions, and are not within the scope of these standards However, where organisatoins provide these levels, these standards will attribute them and analyse them for decision-making purposes | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
950 | 3-Waters | Vol 1 & Vol 2 | Financial Performance The standard has sections on p88 vol2 and succeeding pages. It would be beneficial to review common good practice to understand what data elements should be here. The Australian Infrastructure Financial Management Guide is one such reference. Here as elsewhere the tables can be normalised by reference to an assessment record as proposed above, the type here being valuation. In addition I would have thought there would be considerable opportunity to normalise valuation approaches by assigning each asset a valuation type, and that type record containing the depreciation rates etc. applicable to it. I am not sure that the valuation section has been fully developed yet because some thought must be given to valuation components being different to asset register components. There is no need for them to be the same as they have different drivers. This sections contains data about construction cost that will be transferred to the “as constructed” tables. It asks that the cost of an asset be supplied and that supply is mandatory. However there is a challenge with this because almost all construction contacts cost elements at a higher level of aggregation than each asset. E.g.the construction of a sewage treatment plant does not lead to an estimated cost per inventory item created. Contracts with lump sum maintenance items likewise have no costs per maintenance work task. Therefore a review is required of how costs are acquired and stored and at what level. I suspect that it will be best to capture financial information at the financial/contractual transaction level and activity at the inventory affected level. The concept proposed above for having transactional records for works and tasks enables costs to be collected at that level. | Noted: no action required | There is an opportuity to reflect on the tables and code lists provided in the standards. There are some analytical assumptions being addressed here, which are for the analytics in which will be unpacked in more detail in Volume 4. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
951 | 3-Waters | Vol 1 & Vol 2 | Information required to manage well varies by criticality of network and context I expect that, as with roads, the information needs of managing a water network in a simple undemanding context differ from those of a demanding context. While the performance metrics around health and availability may be common the needs for sophisticated infrastructure and condition metrics would differ. Similarly the information needs for the critical elements in a complex network would be greater than for other elements. This would lead to a hierarchy of mandatory fields based on context. I think this should be considered. | Sector Discussion | To discuss | 5.4 Service Performance Schema | No action |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required
952 | 3-Waters | Vol 1 | pg 3: Validating the data submission: is this to go against each asset or an organisational process requirement? | Included | Against each asset and against each attribute | General | No action
953 | 3-Waters | Vol 1 | 1.8 They are requesting that “each asset type must be delivered on a separate level/layer and the files must be clearly labelled…” If this is in a CAD format this makes perfect sense, but then the attribute information that is being requesting won’t be able to put against the individual asset (when last I tried this, it can only be done with blocks, and blocks can be tricky to convert to a shape file). But if in a shape file format, it is a bit of an overkill, it is structuring back to the way we used to have it. And we will need to combine the information in order to import into Assetfinda. it is also implying that information from contractors will be to a High enough standard that we can suck it into our GIS and all points and lines will meet perfectly. In a perfect world that would be great, but from having a draughing background. I can guarantee you are going to get hydrants, valves etc. not matching perfectly with your pipes (this comes from the skill of the person doing the as built) and greater maintenance issues later. We would be relying on the project managers to insist on high quality as built. This then brings up the issue of disposals of existing infrastructure. Or the assigning of asset id numbers that have intelligence. | Noted: no action required | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | 1.8 Theme Structure | No action
954 | 3-Waters | Vol 1 | 1.11 Projects will need to be on board with this. | Noted: no action required | Noted, but out of scope. | 1.11 Acceptance Testing | No action
955 | 3-Waters | Vol 1 | 2.1.1 Precision needs to be clarified on what is acceptable. | Included | Precision is defined in the standards | 2.1.1 Accuracy Requirements for Locating Assets | No action
956 | 3-Waters | Vol 1 | 2.1.5 In the proposed structure, the data Code list fields will be limited to 10 characters, this is not going to allow us to use unabbreviated materials e.g.: uPVC instead of PVC Unplasticised. We need to decide on this now as it affects the look up tables and associated finance. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the Full Name once the asset data is provided. | 2.1.5 Attribute Data Fields | No action
957 | 3-Waters | Vol 1 | 2.1.8 The attribute fields they are suggesting may impact on Assetfinda fields e.g.: they are the same but have different criteria. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | haydn to follow up | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30
958 | 3-Waters | Vol 1 | 2.4.1 For Access chamber of valves they are requesting one location point, which is what we have and one polygon of the same area representing a plan view of the valve pit. We have over 2000 valves, that is a lot of additional files, and I feel a duplication of work, as the plan view can already been seen as a schematic when viewing the reticulation. - The same as above goes for Storm water | Sector Discussion | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | General for Access Chambers and Valves | More information required for a decision |  | close | Large assets like the ones being described here ought to use drawings and operations manuals (referenced). Much like pump stations we collect a certain amount of information, after that, it is agreed we go to the original data source. | N/A
959 | 3-Waters | Vol 1 | 2.4.7 Says that pump stations should be a polygon feature and all attributes are to be attached to this polygon. Then in 2.5.2 which refers to Pumps it requires pumps to be a point feature with all attribute information attached to this point. So which is it. The Pump station, the pump, or both? - The same as above goes for Storm water | Noted: no action required | The pump station refers to site specific information. The pump is the asset specific information. | General for Pump and Pump Station | No action
960 | 3-Waters | Vol 1 | 2.6.2 Cathodic Protection- I don’t know what that is. | Noted: no action required | This refers to systems installed to protect water mains from corrosion. | 2.6.2 Cathodic Protection | No action
961 | 3-Waters | Vol 1 | 2.8.2 This puts all the responsibility on the contractor to provide all the specified information in the way the document wants it, with us only needing to import it. - The same as above goes for Storm water | Noted: no action required | It also puts the responsibility on the asset owner to specify it properly | General | No action
962 | 3-Waters | Vol 1 | All the attributes that are being requested of us seems to me to be a lot more information than will ever be needed or used, but if supplied by a contractor as suggested, is achievable. | Noted: no action required | Noted, for analytical purposes | General | No action
963 | 3-Waters | Vol 1 | Waste Water seems to be a repeat of the above. | Noted: no action required | Repeat | General | No action
964 | Potable water | Vol 1 | In Summary The main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed potable water assets as defined by asset managers in New Zealand. While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant. It’s not clear who is meant by consultants here. | Included | Note added in glossary 9/3/2017 | In Summary | Change made document updated
965 | Potable water | Vol 1 | The objective of the specification in Volume 1 is to provide geospatially savvy potable water asset “As Manufactured” and “As-constructed / As-built” digital data. The objective of the specification in Volume 2 is to provide geospatially savvy potable water asset “As Managed” digital data. I don’t like the use of the word savvy | Included | Reviewed and removed | General | Change made document updated
966 | Potable water | Vol 1 | Table 1.8 doesn’t appear to include an allowed category or descriptor for “back-flow preventer” | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | 1.8 Theme Structure | New Code List Entry proposed | Back-Flow Preventer | include as valve type | Include 'Backflow preventer' as valve type Is there a difference btn backflow preventer and a non retrn valve - AWAITING FURTHER INFORMATION TO CLOSE OFF
967 | Potable water | Vol 1 | I presume in Table 1.9 that “N” stands for No. I’m sure there will be some exceptions to the rule per asset | Noted: no action required | Reviewed and Noted only | 1.9 Data Principles | No action
968 | Potable water | Vol 1 | 2.1.1 The explanations on pages 6 and 7 between absolute accuracy, relative accuracy and spatial precision are useful; however I think the sector needs to derive one preferred conceptual practice i.e. is absolute accuracy more important than relative accuracy? Whose data set has primacy? E.g. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | 2.1.1 Accuracy Requirements for Locating Assets | No action
969 | Potable water | Vol 1 | I agree with the QA Validation field being a mandatory attribute in Table 2.1.5 | Noted: no action required | Reviewed and Noted only | 2.1.5 Attribute Data Fields | No action
970 | Potable water | Vol 1 | Not all fields in the project attribute table in 2.1.7 are practical. What about a project that is geographically separated (relining different pipes) or across different asset classes? (e.g. water mains and sewers) | Noted: no action required | Reviewed and Noted only | 2.1.9 Project Attributes | No action
971 | Potable water | Vol 1 | 2.1.1 Pg 17 . Ditto for “Area of Work” extent. | Noted: no action required | Reviewed and Noted only | 2.2.1 Area of Work Extent | No action
972 | Potable water | Vol 1 | 2.3.1 How will an open civil structure be represented? E.g. a settlement pond | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | 2.3.1 Containment Structure | More information required for a decision |  | close | To be completed for June release
973 | Potable water | Vol 1 | The repetitive use of the generic term “Health & Safety Issues” in the respective attribute tables should be revised to documented Health & Safety Risks. Or similar | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure trigger there are 'special circumstances'. A code list is proposed | General | More information required for a decision | Health & Safety Type | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
974 | Potable water | Vol 1 | I’m unsure what the use of a “Resilience field (as an open text field?) is in these tables. Too much variability and not enough guidance around what data and format to enter. This is an AM (Vol 2) derivation anyway and not an “As-Built” attribute in my view. Whereas “Design Life” is. | Noted: no action required | Resilience Rating is a measured a6ttribute | 4.5 Resilience Schema | No action
975 | Potable water | Vol 1 | 2.3.4 The term Well should be changed to “Bore” | Sector Discussion | Commented on this previoulsy | 2.3.4 Well | More information required for a decision |  | close | DUPLICATE
976 | Potable water | Vol 1 | 2.4.3 The point feature is to be “snapped” to the pipe asset it is associated with. Does the spatial representation snapped to the polyline create a node? If not then this creates problems when modelling. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed | 2.5.3 Valve | No action
977 | Potable water | Vol 1 | 2.4.5 How is a locator cable or Intrinsic Protection (IP) cable for anti-corrosion ruining with a pipe (e.g. taped to the pipe) to be represented? Why in the table do we have to submit pipe diameter, nominal diameter, external diameter and nominal bore? This is overkill and one wrong piece of information will lead to confusion i.e. which one is the correct one? | Sector Discussion | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | 2.4.5 Pipe & 2.6.2 Cathodic Protection | More information required for a decision |  | close | DUPLICATE
978 | Potable water | Vol 1 | 2.4.7 Should the spatial representation include and ancillary works e.g. dry wells, wet wells, filters, air scrubbers or bio-filters (more applicable to wastewater PS I realise) | Noted: no action required | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. | 2.4.6 Pump Station | No action
979 | Potable water | Vol 1 | 2.5.2 Pumps, can take many types and forms. I trust the fields in the table are flexible enough to accommodate the variety to be expected. | Noted: no action required | We hope so. This will be tested during the pilot phase | 2.5.2 Pump | No action
980 | Potable water | Vol 1 | Is a backflow preventer to be considered a mechanical equipment asset or a valve? | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | 2.5.1 Equipment & 2.5.3 Valve | More information required for a decision | Back-Flow Preventer | valve | DUPLICATE
981 | Potable water | Vol 1 | 2.6.1 Electrical asset – table doesn’t look accommodating enough for the variety of electrical fittings and assets to be expected | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | 2.6.1 Cabling | More information required for a decision |  | Mark to help provide clarity | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30
982 | Potable water | Vol 1 | 2.6.2 Good to see Cathodic Protection systems included. | Noted: no action required | Reviewed and Noted only | 2.6.2 Cathodic Protection | No action
983 | Potable water | Vol 1 | 2.8.2 reporting Mismatches could be problematic depending upon the spatial base used – see 2.1.1 above. | Noted: no action required | Reviewed and Noted only | 2.8.2 Matching to Existing Infrastructure | No action
984 | Potable water | Vol 1 | There are a heap more Definitions that could be added to the Glossary e.g. “trunk main” for starters. | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Glossary | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
985 | Potable water | Vol 1 | Request for code lists: On page 158 of volume 1 of the potable water standard there is mention of supplementary document 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016. Even though this document is in draft, I’d really like to take a look at it. Can it be made available for download, or am I to a copy emailed to me? | Sector Discussion | Code lists now incorporated into document | General | Change made document updated |  | close | CODE LISTS NOW INCLUDED IN ALL DOCUMENTS |  | Closed: -
986 | 3-Waters & Buildings | Vol 1 & Vol 2 | We appreciate the work put in by your team and the various working groups in developing these documents. The process of evaluating the standards has also been useful for Education as an agency, in promoting a review of our data collection processes and considering how these align with a potential implementation of the standards. Our comments on the standards focus at the strategic level. For our organization, with over 30,000 buildings, the cost of changing data collection are high. We therefore need to consider very carefully what information we capture, what decisions we will need to take with information, how we control the quality of information and how it is updated. For that reason it is important to us that we understand the proposed benefits and implementation uses of the standards before taking firm decisions on data collection for their use. We look forward to further discussion on implementation. Your presentation at the last governance group was a helpful insight into your team’s thinking: we want to ensure that agencies understand each other before committing to implementation or advancing a business case with Ministers. For that reason our comments are interim, subject to these further discussions. | Noted: no action required | Statement noted. | General | No action
987 | 3-Waters & Buildings | Vol 1 & Vol 2 | Overview of the Metadata Standards Education recognises the importance of asset information in protecting New Zealand’s ability to provide services in a fast-changing national economy. We also endorse a commitment to standardising and sharing information between public agencies. However, we have concerns about the detail and structure of the data proposed in the metadata standards. A challenge in commenting on the proposed metadata standards is understanding the objectives of the data collection process. It remains unclear how this information will be used, what elements of the process will be compulsory and how the comparison between agencies will work. Education is concerned that the costs of collecting the information outlined in the metadata standards will exceed the benefits. Understanding the benefits derived from these comparisons is critical to determining what data should be collected and how it should be categorised. For instance, the data that is needed to promote All-of-Government procurement is very different from the data needed to identify major network risks within New Zealand | Noted: no action required | Statement noted. Business case. | General | No action
988 | 3-Waters & Buildings | Vol 1 & Vol 2 | Education is also concerned that the focus on the physical condition of the assets may be poorly targeted. Rapid changes in demographics profiles, technology and consumer preferences will also have a major impact on the ability of the current asset networks to meet the future needs of communities. We think that the metadata project should place as much emphasis on the ‘fitness for purpose’, as it does to the physical condition. | Noted: no action required | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | General | No action
989 | 3-Waters & Buildings | Vol 1 & Vol 2 | In addition, the metadata standards assume that decisions on asset maintenance are made centrally. Where maintenance decisions are made is a policy choice that is influenced by broader factors than asset management. In the case of Education, asset maintenance decisions are largely managed at a school level. This is a fundamental premise of how the management of schools is devolved to local communities. This is more responsive to the needs of local communities, as well as meaning minor maintenance decisions can be made in the context of education delivery. However, this also means that, while we fund schools for maintenance, we do not specifically control how that funding is spent. This limits the extent to which Education is able to track maintenance expenditure. | Noted: no action required | This standard does not assume where or how decisions are made, it is a set of metadata standards that define decision elements for analytics to support those decisions - in a standard way | No Specific Reference | No action
990 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: Education’s documentation for new construction includes much of the data outlined in the Metadata standards. However, while we collect and hold this information for each project, we do not capture this data into a central database. The nature of this information is useful when looking at the details of potential redevelopment of an asset but not for evaluation at a portfolio level. As with our response to the overall project, Education believes that clearly articulating the benefits of the process will better inform how and what information needs to be collected. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
991 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: We are aware that much of the information for as-built projects will be provided by the contractor. However, we have concerns that the rigorous specification of data may limit the pool of contractors to larger firms with the resources to provide information in a metadata standard. There is a risk that this reduces competition in the industry, and creates price increases especially in provincial centres where Education operates. Education’s exposure to price increases with small building firms is more pronounced than other government agencies who may build a smaller number of more complex facilities (e.g. Courts, Corrections, Defence). | Included | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | N/A | No action
992 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
993 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | Repeat | N/A | No action
994 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education’s ability to maintain the quality of data is also limited by the devolution of maintenance and minor capital works to schools. Most of the subsequent alterations to buildings are controlled by the schools. Reconfiguring teaching spaces is a regular occurrence across the portfolio but it is unlikely that these changes will be updated in as-built records. | Noted: no action required | Implementation considerations are out of scope | General | No action
995 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The detail of components specified in the metadata standards appear to be very granular for many of Education’s buildings – for instance there are about 200 fields to describe a building ceiling. The majority of Education’s building will be a simple domestic-scale or light industrial structures, where there is little benefit in collecting this level of detailed information. | Noted: no action required | Implementation considerations are out of scope | General | No action
996 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education would recommend that different levels of information are collected for different types of assets. For instance, complex multi-storey buildings with lifts, fire protection and science laboratories, would require more extensive data to be collected than single-storey wooden-structure school buildings. | Noted: no action required | Implementation considerations are out of scope | General | No action
997 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The information Education collects on underground services varies greatly depending on the scale and nature of the development. Many of Education’s developments are additions or small schools in provincial locations, with work undertaken by local building firms. The ability of small contracting firms to record in detail where underground services are located is poor, and records are unlikely to be available in an electronic format. Detailed collection of this data may be appropriate for major assets. However, we recommend that collection of geospatial information on underground services is restricted to the larger or more complex developments. | Included | Implementation considerations are out of scope | N/A | No action
998 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The risk assessment analysis in the proposed standards is difficult to interpret and evaluate especially for the type of assets being developed by Education. The scale of Ministry buildings tends to be domestic or light industrial in scale. The risk implications for different components of the assets (such as the roof) cannot be easily separated from the risk profile of other components of the building. We recommend this aspect of the risk criteria of the Metadata standards be critically reviewed. | Sector Discussion | The standards make the separation of components and the analysis of risk at a component level of granularity possible. There will be a further discussion about this level of recording with the technial working group. | No Specific Reference | More information required for a decision |  | volume 2 | Discussed during the May 1-3 workshops Deemed as part of Volume 2 |  | Closed: -
999 | 3-Waters & Buildings | Vol 2 | Broad comments The focus of the data collection is around the building envelope (walls, roof) with significantly less focus on the interior assets. However, building interiors represent a large component of the total cost of providing assets and are the components with the shortest life expectancy. The interior configuration has a major influence on the ability of school buildings to generate positive educational and social outcomes. For these reasons, Education believes the metadata standards should have a greater focus on the interior assets and configuration. | Noted: no action required | All components are collected, including interior components | No Specific Reference | No action
1000 | 3-Waters & Buildings | Vol 2 | Broad comments As well as the definition of the data held, the metadata schema will need to outline the data structure and hierarchy. If information is not collected at a consistent level in the asset hierarchy it makes comparisons between entities difficult. For instance, it is difficult to compare what proportion of the portfolio has fitted wall insulation, if one agency collects the information by building and another by facility. This aspect of the standards should be reviewed. | Noted: no action required | Data Classification, Heirarchy and Structure are all outlined in the Draft Standards | No Specific Reference | No action
1001 | 3-Waters & Buildings | Vol 2 | Broad comments The amount of information collected about the assessor for each data category is unnecessary. It is always useful to know who undertook the assessment but the collection of qualification and experience against each asset is excessive. This detail should be replaced with a measure of confidence around the measures, such as whether it was the result of an exhaustive analysis or a desk-top assessment. | Noted: no action required | Each organisation will decide at what level of granularity (detail) it collects tdata to manage its assets. | No Specific Reference | No action
1002 | 3-Waters & Buildings | Vol 2 | Detailed comments on categories of data The metadata standard outlines the format and categorisation of data on the assets. The following considers each of the categories individually. It discusses these in broad terms and then outlines how Education collates and reports of these asset categories. | Noted: no action required | Statement noted, no action required. | No Specific Reference | No action
1003 | 3-Waters & Buildings | Vol 2 | Condition: The metadata standards propose that condition measures categorise assets by: structure; external; interior; services; and fittings. Separating external cladding and structure is a useful differentiation for some of the housing and light commercial categories. The detail captured on the interior is overly simplistic. The proposed metadata standards focus on cosmetic issues such as the quality of the paint finish, rather than configuration and functionality which is of greater importance for Education. As noted above, interior components represent around one-third of the total building cost and have the highest depreciation rates/shortest lives. Ministry measures: The broad asset categories used by Education are: external; interior; services; and roof. More detailed condition data is held for individual schools but the revaluation and portfolio reporting for Education uses these four categories. Education is currently reviewing options to measure how different building design and fabric choices impact on the light, air quality, temperature and noise levels in teaching spaces. | Noted: no action required | Condition Elements are covered in detail in the standards They do not differentiate buildings by type, beyond the Building Code definition of Facility Importance (which is not building type) These are asset metadata standards, not portfolio form / function and mix standards | 2.2 Condition Schema Code List 13: Facility Importance Rating | No action
1004 | 3-Waters & Buildings | Vol 2 | Repairs and Maintenance The definitions of repairs and maintenance defined in the metadata standards are reasonable and workable. 1. However, collecting data on deferred maintenance items is too complex and unproductive. Part of the issue is that subsequent work may override the maintenance items, but be difficult to identify and measure. Under-maintaining an asset may be best reflected in the condition assessment process. 2. Ministry measures: Education currently identifies programme maintenance items to be undertaken on a building, including recurrence timeframes. Education also categorises the reason for maintenance according to priority (i.e. health and safety, protection of building etc). While Education has a good knowledge of the budgeting for repairs and maintenance, it does not track specific expenditure, accountability for which has been devolved to schools. This means that the explicit scope of work that has been undertaken is not available in Education’s information systems. | Included | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
1005 | 3-Waters & Buildings | Vol 2 | Utilisation: The utilisation measures by nature need to be specific to the industry in which the agency operates and would tend to be for internal reporting only. There is limited advantage in establishing utilisation standards for comparison between entities with very different objectives. This is more appropriately a component of the annual reporting to stakeholders rather than a metadata measure. Ministry measures: Currently Education has a formula for entitlement of classrooms and other space based on school enrolments. Education measures schools’ provision of space compared to entitlement with an optimal target range of 85% to 105%. | Noted: no action required | Agreed, but the standards apply across all Sectoirs (e.g. Housing Providers) | 3.2 Utilisation | No action
1006 | 3-Waters & Buildings | Vol 2 | Demand There are several problems attempting to identify demand for an asset. These are compounded for school assets, which provide free and compulsory services. Commonly residential and light commercial facilities have a variety of different demand parameters. For instance a school hall will support school assemblies, indoor sports activities and community events. Each of these demands has different physical requirements. Measures of demand are therefore difficult to establish. Ministry measures: Education regularly needs to address circumstances where the demand for a school exceeds its capacity. This would commonly be dealt with by strategies such as the application of enrolment zones. Education uses local and regional demographic trends amongst other inputs to identify demand for additional learning spaces and/or new schools. | Noted: no action required | Demand Section has been updated in Volume 2 And, there are many examples of useful demand analytics for schools | 3.3 Demand Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1007 | 3-Waters & Buildings | Vol 2 | Criticality Applying criticality to residential and light commercial buildings is more difficult than with infrastructure. The metadata approach to defining communities being serviced by public sector buildings is not viable. Communities which use public sector buildings tend to be complex and overlapping and criticality dependent on other assets within the network. The definitions of criticality should therefore be limited to explicit requirements in supporting post-disaster response or recovery i.e. identifying assets which have an explicit function defined by Ministry of Civil Defence and Emergency Management plans. Ministry measures: The criticality for the school as a civil defence centre is an agreement between Civil Defence and the Board of Trustees. This will partially be dependent on other community infrastructure in the location. Schools which are Civil Defence centres are not identified within Education’s central information systems. | Noted: no action required | Critciality will be closely linked to Faclity Importance per the Building Code | Code List 13: Facility Importance Rating | No action
1008 | 3-Waters & Buildings | Vol 2 | Risk The metadata schema for risk measurement works to associate risks with asset components. For most of the risks (e.g. earthquake, flooding) it is more appropriate to associate the risk with a building or site, rather than individual component (e.g. roof). Ministry measures: Education has risk registers at a portfolio level and each school has a risk register. Some of the risks associated with the assets relate to the use of materials (e.g. asbestos). These are also logged on the school risk register but not captured centrally. | Included | Risk can be applied at any level of granularity Analytics enable Portfolio level of risk to be established | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1009 | 3-Waters & Buildings | Vol 2 | Resilience The resilience measures have yet to be developed within the metadata standards. The focus of the resilience measures appears to be around major civil defence and emergency events, such as earthquakes. It will be useful to identify the ‘Importance Level’ as defined in building legislation. A sole focus of the civil defence component of resilience is too narrow. We believe the issues should also encompass the ability to change the use of assets or to reconfigure them for different demand or purposes such Ministry measures: When Education developed the business plan for transportable modular classrooms it aimed for these to constitute a proportion of the network to allow flexibility to respond to demographic changes. | Included | Resilience has been updated in the standards | 4.5 Resilience Schema | No action
1010 | 3-Waters & Buildings | Vol 2 | Design Performance The majority of the design performance schema appears to relate to items of equipment, such as pumps and piping. This represents a relatively small proportion of the assets within Education’s network. The majority of the network is relatively uncomplicated, one and two storey buildings, with limited HVAC or specialist facilities. Collecting design performance at the level of individual items is therefore of limited value. Ministry Measures There are some specialised assets within Education’s portfolio, such as lifts in multi-storey buildings. However, these are few in number and are managed under a national contract. Details on the design performance of smaller components, such as heat pumps are typically held by the school. | Included | There are also mant examples of building design perfomance (Earthquake Rating, Energy Rating etc.) | Table 14: Design Performance Examples | An explanation of Data Science will be provided for at the Technical Working Groups
1011 | 3-Waters & Buildings | Vol 2 | Financial Performance There has been significant effort to develop measures for financial performance within the standards. The proposed standards outline a detailed basis for the collection of valuation, depreciation, time of payment information. Rather than replicate data held elsewhere, it would be more useful to ensure that there are linkages with the agency’s broader financial system. This has the advantage of enabling association of asset measures with other agency performance measures, for instance measuring the asset cost per visitor or student. Ministry Measures Education has recently established a new asset management system (Tribal K2) which tracks budgeting for maintenance and other property costs. The system links to Ministry’s property data warehouse system. This allows analysis and development of a broad range of performance measures. The result is the ability to compare asset performance measures to aspects such as student numbers (e.g. the percentage of students learning in buildings that fall into each asset condition category). | Noted: no action required | Organisation specific financial analytics will be supported by attribution within this standard. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1012 | 3-Waters & Buildings | Vol 2 | Service Performance The service performance schema appears to be a raft of unrelated criteria, which individually may be critical to the functionality of the asset, but do not belong in the same category. The result is measures which relate to different levels of assets from components (e.g. disabled access) through to facilities (e.g. iwi interest). A number of the proximity measures, such as kilometres to communities are difficult to establish without further definitions of community. The result is a wide range of criteria which does not allow comparison between different agencies. Similarly, the raft of measures around district plan criteria, such as provision of car parks, is difficult to update. For many public service assets the land will be designated so underlying zonings will be poor indicators of the use of the site. Some aspects of the data, such as iwi values, heritage considerations or community interests, cannot be easily summarised into a data base. It would be better to include an identifier which would highlight whether more detailed analysis is available on file. Overall Education would advocate for service performance to be restructured into a number of separate themes. Ministry measures Education has a basis for evaluating the service levels called the Innovative Learning Environment (ILE) assessment tool. The information is currently collected at a building level and is a requirement of the five yearly capital and maintenance planning process. Education is evaluating ways of standardising the capture of the information. The ILE assessment tool also has facility to include a range of qualitative measures such as ‘how well the design reflects the needs of the local community’ which may be developed in future. | Noted: no action required | No action required with regards to comment son the business case. The standard is intended to system and organisation agnostic. | 5.4 Service Performance Schema | No action
1013 | 3-Waters & Buildings | Vol 1 & Vol 2 | Introduction The Auckland Council family fully supports of the intention behind this standard and has actively contributed in the working groups for roads, residential housing and light commercial buildings and the three waters. The Auckland Council family welcomes the opportunity to provide feedback at this time, and the opportunity to participate in the further development of the standard. The metadata standard is a great opportunity to gain national consensus of what minimum level of data capture is required. This initiative will enable us to ensure that data can be applied in a consistent and repeatable way to make good asset management decisions based on acceptable levels of service, replacement and growth strategies. | Noted: no action required | Statement noted. | General | No action
1014 | 3-Waters & Buildings | Vol 1 & Vol 2 | Summary Feedback is currently sought with specific regards to the three waters and the residential housing and light commercial buildings standards. We have found it difficult to provide meaningful feedback in the absence of a clear strategic message, an understanding of which is shared by all reviewers. That message needs to link the standards to the business case and to recently held discussions with the Minister of Finance. A further opportunity to work on and develop the standard from the ground up, in the way that the transport group has developed the roads standard, would also help the Auckland Council family to feel more confident about the result. To that end we suggest that it would be useful to incorporate such an opportunity into the process from here. We would like: • To present our feedback to the combined governance group • The working groups to review and address all feedback on the standards • The resulting outputs to be made available for consideration by the governance group prior to any public release of the standards | Noted: no action required | Discussions will continue across the Infrastructure Sectors (Core and Social) | No Specific Reference | No action
1015 | 3-Waters & Buildings | Vol 1 | Volume 1 – As-built metadata standard What we like: • Provides reasonable coverage of possible data fields • As a collection of possible attributes it will help to drive a culture of good practice to capture metadata • It brings attention to the need for good base data What we consider could be further developed: • In its current format the standard is not adoptable due to the constraints it will place on systems and business processes this needs to be addressed before it can be adopted. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | to be tested/validated as part of the implementation pilots | Discussed during the May 1-3 workshops Determined that this would be addressed during the Pilot / Implementation phase |  | Closed: -
1016 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • The layout should be modified to clarify the distinctions between master data and metadata. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | include a note as to what masterdata is | All the data specified within these standards is master data. It is the data which is normlly held within an Asset Management Information System and used for the systematic analysis to inform evidence-based investment decisions. In the purest sense metadata is data about data. These tables incorporate different tyes of data to provide an overall picture of what the assets are and where they are. | N/A | Closed: - this is to be discussed during implementation
1017 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • A number of elements have been included but are not complete, and an understanding of industry definitions, hierarchies and processes is required to complete this volume. We would welcome the opportunity to assist with this. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | action for GISSA to include wording upfront | This is a discussion for the Pilot. There are many commercial considerations here, alongside a variety of 'industry standards' as described by the 'industry'. | N/A | Closed: - this is to be discussed during implementation
1018 | 3-Waters & Buildings | Vol 2 | Volume 2 – Asset management performance standard What we like: • Recognition of the notion that data is only useful if it is used • An approach that recognises the value of rigorous analysis to inform decision making What we consider could be further developed: • In general, we consider that this volume is under developed with inconsistencies and cross-overs to Volume 1. We would welcome an opportunity to further input into its development, as we recognise that it can provide a useful tool, particularly for organisations with limited capability in this area. | Noted: no action required | Volume 2 is now a comprehensive document | No Specific Reference | No action
1019 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • This volume assumes generalist practices that are inadequate for non-linear assets and includes operational and derived data that is not suitable for inclusion in an AMIS system. | Noted: no action required | This volume is spatially aware, and will attribute point, line, ployline and 3D objects. It is also agnostic to any AMIS and GIS system | No Specific Reference | This will be discussed at the technical workshops
1020 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Needs to be carefully framed for the asset types that it relates to. | Noted: no action required | Asset types are specifically defined within the standards - See Volume 1 of each Group of Assets | No Specific Reference | No action
1021 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Replacement trigger points should be broadened from reliance on subjective visual condition to incorporate best practice for optimal replacement, that is, based on objective measurement and sound engineering judgement. | Included | Visual inspections are only one type of condition assessment to trigger an interventi. Capacity could be another (at Very High > 95%) | Code List 31: Demand – Capacity Unit of Measure | No action
1022 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Reference should also be made to failure mode effects analysis (FMEA/FMECA) as a means to support optimal replacement points. Our feedback does not further consider this volume due to the large disparity with practice and limited workshops to fully capture industry needs. | Included | The standards do not preclude failure mode analysis of any type. The standard captures some of the attributes for this analysis. | 2.3.5 Code Lists | This will be discussed at the technical workshops - mor ework is required here with the sector
1023 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 1. Create a separate volume that covers strategic fit and business needs across all asset categories. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1024 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 2. Focus on a business standard for assets including improving the hierarchy to cover both asset and data hierarchies and outline the relationship between them. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | No Specific Reference | No action
1025 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 3. Review publishing formats to maximise the impact of the standard. | Included | The drafts have now had a full publishing edit | General | No action
1026 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 4. Remove content that is not related to the business standard including those referring to implementation paths, delivery mechanisms and quality control rules. | Sector Discussion | To discuss - for example? | General | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: -
1027 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Workshops The working groups were presented with A-Spec as a straw-man and tasked to focus on the possible data that could be captured for individual asset types. The working groups started with limited traction and concern was raised early on as to the purpose of the workshops in diving into attribute detail that is quite easily obtainable from various sources. A basic data hierarchy was established that allowed the attributes to be tackled in a constructive manner. In hindsight, it would have been useful to consider other industry standards as part of the process. We feel that such consideration could still be undertaken as part of the follow on from this feedback. Despite the concerns mentioned above, the workshop groups generally worked well and came to agreement on the things that were required. It would be extremely useful for the working groups to go over the feedback and address it as appropriate. Strategic, governance and procedural feedback should also be reviewed by the governance groups. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | General | No action
1028 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Definitions of industry terminologies and attributes. | Sector Discussion | Examples required | General | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: -
1029 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Identification of business needs. | Noted: no action required | Business case will outline / describe benefits | N/A | No action
1030 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • An assessment of “fit for purpose” data capture. A matrix and understanding of the minimum data capture required based on organisational needs. | Noted: no action required | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | N/A | No action
1031 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Exploring the origin of the data and identifying whether it belongs to volume one (As constructed) of these standards or is better suited with other data sources, for example geotechnical data. | Noted: no action required | These data sets are what are required for asset management purposes | General | No action
1032 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Validation of the Codes list or optional pick lists. | Noted: no action required | Reviewed and implemented | General | No action
1033 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • The standard is required to be system agnostic. Identifying how the standard will be implemented has an effect on the data capture requirements. To enable this we need to understand what the systems and processes look like. The standard needs to be reconciled with these systems and processes at organisation level. | Noted: no action required | Updated | General | No action
1034 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Comparison to international practice and other complimentary standards. | Sector Discussion | Information to be provided for discussion | General | More information required for a decision |  |  | There has been a number of reviews against international standards. These (eg OGC) have been aligned to the standards. We will continue to review the standards throughout the pilot for application, due to the variable nature of these standards |  | Closed: - implementation issue
1035 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • There is a logical split between roads, buildings and three waters; however there is less logic to further splitting up the three waters when the majority of the components and attributes are the same. It would be sensible to consider consolidating these. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
1036 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Rather than repeating the introductory statements in both volumes of each version of the standard a covering or base document (as seen in most other standards) should be considered, as the principles of data collection are the same. This would also have the advantage of slimming the volumes down. | Noted: no action required | Format based on technical differentiation | General | No action
1037 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Common data sets are repeated at every asset class adding unnecessary volume. | Noted: no action required | Action on data scientists. | General | No action
1038 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • The standard seems to reference the manner in which data will be collected. This is the responsibility of the various organisations and should not form part of the standard. | Noted: no action required | This is not within the scope of these standards | General | No action
1039 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The document will benefit from a better structure around the rationale, strategic drivers and added benefits, of the standard. Some of this information is scattered across the introduction section but it could be strengthened and focused on the purpose of the standard, which is about agreeing on common classifications and definitions. We think there is general agreement that data standards are needed and this doesn’t need to be emphasised. | Noted: no action required | This is not a policy report, an asset management plan, nor a 30 Year Infratsructure Plan (where you would find this requirement). This is a metadata standard for assets at an assetID level of granularity. It does however capture the context of the analytics which inform these types of documents which support organisations asset management | No Specific Reference | No action
1040 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • We believe that the key purpose of this standard should be to outline data requirements that enable organisations to compare their performance and share asset lifecycle knowledge while continuing to measure their performance in a meaningful and cost effective manner in the context of their strategic objectives. | Noted: no action required | Statement noted. | General | No action
1041 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The intention of this standard development was to produce a metadata capture culture and identify the appropriate level of capture. This intention has been somewhat obscured by the very much “field-base” information that is supplied by suppliers and contractors on the physical attributes of assets. We believe that it would be useful to reconsider the audience of this standard and review it to ensure that the audience is appropriately targeted. In that way the business strategy can direct appropriate attribute fields, which will then be common sense as long as common definitions are understood. | Noted: no action required | This observation describes on audience, this is not the only audience, for example design engineers. | General | No action
1042 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Data capture, as acknowledged in the standard is but one component of good asset management and the ways in which this initiative will support organisational challenges such as achieving ISO 55001 accreditation could be made clearer within it. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1043 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The standard strategic goal is to enable organisations and the country “to collect locally and use globally”. It is unclear how this standard compares and incorporates international best practice. There are examples of other international metadata standards however only A-Spec was examined. | Noted: no action required | A number of other standards have been investigated. (Uniclass, Cbi, Omniclass, Master Spec etc. etc.) The strategic goal is to enable organisations and the country “to collect locally and use nationally” | No Specific Reference | No action
1044 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The way in which the standard is currently written presents the data capture requirements in a set manner and format thereby requiring business needs to be moulded for the data specific needs. These limitations are likely to prevent users from taking opportunities in system and process advances that may become available. Some of these initiatives already exist such as open data sources from product suppliers. We expect these advances to become more readily available in the future. It is not clear how the static two-dimensional model presented by this standard will allow business to incorporate these changes. | Noted: no action required | The standard does exactly the opposite to what this is suggesting. The question is not so much about how it is collected but how the data is manipulated into a common format when it is (see FME) | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1045 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Existing systems have been heavily invested in and are very diverse, even in the Auckland council family, to tailor for specific needs. With the possibility of the standard purely becoming a mapping exercise; it then does not support the need to prescribe data fields to intricate detail. The level of data capture required to complete the national level analytics is not identified. Anything else is considered optional and does not support the reason for capturing data at every level. | Noted: no action required | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. But Note use of tools like FME. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1046 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • In order to address the matters referred to in the point above, the standard could be reconfigured to provide the required performance outcome and guidance on how these requirements may be met, while allowing flexibility in means and methods of demonstrating compliance. | Noted: no action required | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. And, there are many analytcal options on the same data sets depending upon he problem being solved. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1047 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • As has been mentioned previously, the document uses terminology and jargon that is not consistent with those used in NZ. This is an easy fix, and appropriate language is a great factor in the ease of adopting new things. | Included | The drafts have now had a full publishing edit | General | More information required for a decision
1048 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • There are plenty of NZ examples of assets of each class and type, and we will be happy to provide some if required. Using Australian examples in a NZ standard is not appropriate where there is a suitable local example available. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: -
1049 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • It is also important that the examples used are relevant to the asset type contemplated in the standard. Building examples for the residential housing and light commercial standard will make the logic of the approach more apparent. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision
1050 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • Most of the terminology used in the attribute fields is not defined. Without these definitions data cannot be accurately mapped and the data collector will be left to assumptions that will compromise data integrity. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision
1051 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • At the beginning of the working group workshops we agreed that these are business standards – hence system agnostic; this is even mentioned in the document. At the same time the proposed standard – language, data formats and terminology – has been prepared for an easy input to a functional specification for a GIS application. It is evident that the asset classification and the attributes were “flattened” to fit this particular implementation. This has detrimentally affected the business value of the standard – we have a number of attributes that do not belong to the asset class they are listed against. An example: in stormwater, swale only attributes are elevated at channel level, at which level they are meaningless. | Sector Discussion | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | General | More information required for a decision |  | close | DUPLICATE
1052 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The current format of data requirements as a mix of business standard and specification is of particular concern. On one hand it makes the business part of the standard logic hard to follow, while on the other hand the document is not sufficiently detailed to be effective as a functional specification. As a consequence standard does not show the business what it needs to collect and the application vendors will not understand what they need to build. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | volume 3&4 | Discussed during the May 1-3 workshops Deemed as part of Volume 3 or 4
1053 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The asset data hierarchy needs to be completed. Most importantly the way assets have been grouped for data capture needs to be reconsidered in order to represent the business asset hierarchy. Business hierarchy is of great importance for FMEA, operation and maintenance of complex assets, for example. The exclusion of business hierarchies from the standard will require every organisation to create another set of rules outside of the standard in order to maintain these relationships. | Sector Discussion | The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers that in turn will provide consistency to the asset owners. As each organisation has their own hierachy it is expected that they will categorise the data being provided according to their needs | General | More information required for a decision |  | same action as 1017 | DUPLICATE
1054 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • We strongly recommend that all implementation related fields be removed from the document, as outlined below: o Attribute abbreviations – these are in many cases system related setup and for instance instrumentation may be adopted by numbering systems such as ISA55 that is international practice. The purpose of these abbreviations is not clear. o Character length – This serves no purpose and is not supportive of being system agnostic. By providing full and proper definitions to the attribute field data may be mapped correctly, regardless of character lengths. o Comments – This filed has no purpose that cannot be fulfilled by either the unit filed or description fields o QA validation – These are rules set by business and specific software systems. It also does not serve any purpose to identify minimum capture level. This could be done in a better way through a developed hierarchy that identifies, master data from metadata and compulsory fields from conditional or optional fields | Included | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | General | No action
1055 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • To date geometrical and topology rules have not been discussed. Currently there are different requirements governing the way geospatial data is captured. As with the asset management systems, investment has been made in maintaining systems to these rules. From an analytics point this does not seem to have any impact on the analytic output. Development of such a standard is considered to be a separate endeavour in its own right and has the potential for having great cost impacts to organisations. In the same way one could argue other data sets must then be prescribed – such as geotechnical information, drawings and so on. Flexibility is key, as planning for known technology, given the pace of technological change, will mean that the standard is out of date before it is published. | Included | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | General | No action
1056 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • Attribute sets are not normalised across the asset classes. An example of this is the repetitive material types in the codes lists. (Note. Watercare, Wellington Water and Christchurch City Council were the only parties to receive the codes lists later on request. This was never published. | Included | It is acknowledged that codelists will need to be dynamic in nature and will be open to continued contribution from the sector. The code lists are now incorporated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | General | No action
1057 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • As-built data versus operational data versus derived data is crossed over between the volumes. Separation is required through the data hierarchy. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | close | An addition of explanation has been added to standards The standards will catalyse asset management discussions and improve knowledge in this space | page 1
1058 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 1. Create a separate volume for strategic fit and business needs | Noted: no action required | To discuss | No Specific Reference | More information required for a decision
1059 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Improve the Asset Hierarchy section to cover both asset and data hierarchy and to outline the relationship between them. | Included | Asset Classifications have been defined in the Standards | General | No action
1060 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and simplify attributes specifications; all attributes that do not belong to the As Built standard, such as demand, repair and maintenance, health and safety issues, service and financial performance should be removed. These are time related measures and events that are covered by other parts of the standard. Connecting these events and measures to assets is the subject of asset analytics, not the as built standard. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
1061 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and clean the attribute tables – remove all values that are included as they are not relevant. | Sector Discussion | The standards have harmonised and standardised data and hierarchies across the standards | General | More information required for a decision |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required
1062 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Clean the relationship between asset classes, attributes and values. One asset class has to belong to one asset category. | Included | Asset Classifications have been defined in the Standards | General | More information required for a decision
1063 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Outline a list of core asset characteristics – the whole concept of the standard as vehicle for comparability becomes meaningless if we don’t agree on a few critically important attributes that must be collected. | Noted: no action required | Mandatory, Optimal, Optional will be discussed with the sectors | No Specific Reference | More information required for a decision
1064 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Our recommendation is to add a section on asset geometry and topology for water networks – but not one that could be mistaken for a specification for GIS applications. This section needs to address the core rules for creating geometric networks and outline the participation of all assets in these networks. | Included | Included in the draft Standards | General | No action
1065 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Since all standards are related and are part of the same suite of documents it would make sense for them to be published as related volumes (chapters?) rather than independent books. | Included | This has been reviewed, and a decision to keep as separate documents made - at this time (the documents would be 300+ pages if combined | No Specific Reference | No action
1066 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Another approach to publishing standards which would be effective is by using links to look up the list of attribute values. | Included | Other access toolss will be reviewed before release in July 2017 | No Specific Reference | No action
1067 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Think about publishing the data tables in a data view in addition to the document | Included | Included in the draft Standards | General | More information required for a decision
1068 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 4. Remove content that is not related to the business asset data standard: • We strongly recommend that all references to implementation paths, delivery mechanisms and quality control rules be removed from this document. This should be a subject to a separate project/ research due to the variety of business models that can be applied. Unless there is a directive for a centralised implementation of these standards, they remain the responsibility of each organisation and have to be adapted to the particular technology platform. | Noted: no action required | Unclear of where there are examples of this | No Specific Reference | No action
1069 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | ?? | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | double check that spreadsheet David/Nina to confirm | No action required unless hear from David (Opus) or Nina (Auckland)
1070 | 3-Waters | Vol 1 | Asset class definitions needed: Need clear definition of asset classes. Channels are particularly bad examples; they cover a range of assets with various function and purpose - and badly. Under current structure there is no way to describe sw treatment devices. | Sector Discussion | Classifications and types defined in the standards Refer to code lists | General | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
1071 | 3-Waters | Vol 1 | Attribute definitions needed: Many definitions are unclear or missing. Some appear to be database oriented - need to be business meaningful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
1072 | 3-Waters | Vol 1 | Standard is about structured data, not any information about assets: This standard should cover the data that needs to be captured in as structured way for further analytical and reporting use. Hence all data that has no such value needs to be removed. In complex assets most of the asset specific data is kept in operation manuals and other operation related documentation. | Noted: no action required | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | General | No action
1073 | 3-Waters | Vol 1 | This is volume one - as constructed assets. Remove all data that is not relevant to as constructed - there are other volumes that this data is described | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | close | Discussed during the May 1-3 workshops Noted no further discussion or action required
1074 | 3-Waters | Vol 1 | Huge number of attributes that are not relevant and not agreed. Need to go back to the workshop discussions and agree how feedback following working sessions will be captured - cannot afford to continue like that. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | close | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: -
1075 | 3-Waters | Vol 1 | Renewal material in pipes. This should be relabeled to say lining material. | Included | Attributes included, lining material included in standards see code lists | General for Pipes | No action
1076 | 3-Waters | Vol 1 | Missing attributes. Lining material installation data is critical | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  | check if qualification notes are needed as to how to use fields | Modified General Validation Rule for Material, Renewal Method and Renewal Material to also include that the fields are 'Conditional'
1077 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Noted: no action required | Information to be provided for discussion refer to ID1069 | General | More information required for a decision
NEW001 | 3-Waters | Vol 2 | Code List 9 - people with a spade won't understand the difference between these codes, as they are all the same thing to the person on the ground | Sector Discussion | Codelist 21 on page 45 | Sector Discussion |  |  |  |  | understanding the importance of data, and what is essential v optional, will be determined during initial implementation | Graeme provide the codelist | Christchurch | DUPLICATE see NEW005 | DUPLICATE see NEW005
NEW002 | 3-Waters & Buildings | Vol 1 & Vol 2 | In volume 2 there is a space to define mandatory - but there isn't the same in volume 1. what's going on? | Sector Discussion |  | General |  |  |  | understanding the importance of data, and what is essential v optional, will be determined during initial implementation |  | Action: - Haydn Remove the mandatory field from volume 1 | Haydn | Completed | Completed
NEW003 | 3-Waters & Buildings | Vol 2 | Need to include an attribute where something hasn't been assessed yet | Sector Discussion |  | General |  |  |  | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty |  | Action: - George to add 'not assessed' as an attribute where needed | GISSA | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty
NEW004 | 3-Waters & Buildings | Vol 1 & Vol 2 | There are potentially occurances where the standards include code lists, where not enough information is known to make the code lists finite - suggestion that these code lists are flagged as being examples etc | Sector Discussion |  | General |  |  |  | Completed Added to standard |  | Action: All required additions/changes to code lists to be provided to GISSA by COB 2nd June 2016 | GISSA | Completed Added to standard | Completed Added to standard
NEW005 | 3-Waters & Buildings | Vol 2 | Table 2 - looks more transactional than elemental, why connected to an 'event' rather than directly to the 'table'? | Sector Discussion |  | General |  |  |  | Multivariate analysis |  | Action: Nick and Haydn to discuss and determine if changes are needed to the standards pre relase | Haydn | No further action required | No further action required

## Workshop 1 3-Waters Vol 2
NZAMS - Sector Feedback - Final Version (Workshop 1 3-Waters Vol 2) | [7 empty] | 0
ID | Standard | Volume | Feedback | Status Included, Excluded, Sector discussion, Noted: no action required | Final Comments for Publication | Section Reference in Final Version - per Contents page | Additional Work | Proposed Codelists / Attributes | Workshop Outcome LINZ notes 1/2 MAY | Notes / Updates | Ref | Workshop Outcome LINZ notes 23/24 MAY | GISSA / Other | Actions taken by whom and when | ACTION TAKEN
1 | Potable water | Vol 2 | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Completed with Metaconnect | No Specific Reference | No action
2 | Potable water | Vol 2 | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Included | Completed with Metaconnect | No Specific Reference | No action
3 | Potable water | Vol 2 | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Included | Completed with Metaconnect | No Specific Reference | No action
4 | Buildings | Vol 2 | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Included | Completed with Metaconnect | No Specific Reference | No action
5 | Stormwater | Vol 2 | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | Completed with Metaconnect | No Specific Reference | No action
6 | Stormwater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action |  |  | Refer to Volume 1 tab
7 | Wastewater | Vol 2 | Should be "coordinate reference system" as in ISO 19111 | Included | Standards are OGC spatial attribution compliant | Use of the Specification | No action |  |  | Refer to Volume 1 tab |  |  | Completed in Volume 1
8 | Wastewater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action |  |  | Refer to Volume 1 tab |  |  | Completed in Volume 1
9 | Potable water | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | not required in this section, covered in later sections | Use of the Specification | No action
10 | Potable water | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
11 | Potable water | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
12 | Potable water | Vol 1 | or vertical datum | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
13 | Potable water | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | changed precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | Change made document updated
14 | Buildings | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
15 | Buildings | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
16 | Stormwater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
17 | Stormwater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
18 | Stormwater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
19 | Stormwater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
20 | Wastewater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Updated in draft standards | Use of the Specification | No action
21 | Wastewater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
22 | Wastewater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
23 | Wastewater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Updated in draft standards | 2.1.2 Projections and Datums | Change made document updated
24 | Wastewater | Vol 1 | Update to NZVD2016 | Included | Updated in draft standards | Glossary | Change made document updated
25 | 3-Waters | Vol 1 & Vol 2 | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General | No action
26 | 3-Waters | Vol 1 & Vol 2 | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Noted: no action required | Reviewed and Noted only | General | No action
27 | 3-Waters | Vol 1 & Vol 2 | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference | No action
28 | 3-Waters | Vol 1 & Vol 2 | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | Included | The drafts have now had a full publishing edit | General | Change made document updated
29 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Noted: no action required | The adoption of extents of fields is determined ny each organisation | General | No action
30 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General | No action
31 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General | No action
32 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | Noted: no action required | Future work is yet to be determined | General | No action
33 | 3-Waters | Vol 1 & Vol 2 | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | Included | The classification has been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
34 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | Included | The classification has been defined in the Standards Code Lists included | General | No action
35 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | Included | The classification has been defined in the Standards | General | No action
36 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | Included | Asset Classifications have been defined in the Standards Code Lists included | General | No action
37 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy | No action
38 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Noted: no action required | The adoption of extents of fields is determined by each organisation | General for Hierarchy | No action
39 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference | No action |  | closed
40 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference | No action
41 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics | No action
42 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums | No action
44 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Included | Adjustment will be made to standards | General | Change made document updated
45 | 3-Waters | Vol 1 & Vol 2 | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Noted: no action required | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. | General | No action
46 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Noted: no action required | Reviewed and Noted only | General | No action
47 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Included | Photographic Evidence is an optional attribute | General | change made document updated
48 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Noted: no action required | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General | New Code List proposed | Health & Safety Type
49 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Included | Adjustment will be made to standards | General | Change made document updated
50 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | No action
51 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | No action
52 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | Included | Code lists included in standards | 2.3.3 Retaining Structure | No action
53 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Sector Discussion | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | No action |  | closed | Refer to Volume 1 tab |  | Close: - this is done
54 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves | More information required for a decision |  | Mark and Marty to discuss and come up with a reccomended outcome | Refer to Volume 1 tab |  | The attributes that need to be collected on valves are waiting on input from Marty and co - DH to chase up. Proposal is that this is not finalised until post release (implementation) | Completed in Volume 1
55 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Noted: no action required | These standards are not about Treatment Plants | General | No action
56 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | Included | Code lists included in standards | General Equipment | Gauge input from next review
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | needs to be included | Refer to Volume 1 tab |  | Tauranga to provide George with more specifics. This will be incorporated before initial release | Completed in Volume 1
58 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments | No action
59 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | Gauge input from next review
60 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General | No action
61 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | Change made document updated
62 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | Change made document updated
63 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA) | closed | Refer to Volume 1 tab |  | Close: - this has been included | Completed in Volume 1
64 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | Noted: no action required | resolved in updated version | 2.5.1 Equipment | Change made document updated
65 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
66 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision
67 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision
68 | Stormwater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | AddCCTV & Laser Profiling testing to code list testing type | General | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
69 | Stormwater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Sector Discussion | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | New attribute proposed | Installer of Asset
70 | Stormwater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Sector Discussion | Reviewed and Noted for Inclusion | 2.3.4 Pipe | More information required for a decision
71 | Stormwater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | General | New Code List entry for Condition Assessment Type proposed | Deflection Test
72 | Stormwater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
73 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
74 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
75 | Stormwater | Vol 1 | Deflection Test result | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | New Code List entry for Condition Assessment Type proposed | Compaction Test
76 | Stormwater | Vol 1 | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not)
77 | Stormwater | Vol 1 | Seal Access Safety | Sector Discussion | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber | New Code List & entries proposed | Health & Safety Type
78 | Stormwater | Vol 1 | Manufacturer Manufacturing Standard Third Party QA Accreditation | Sector Discussion | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
79 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.4.4 Pipe | New attribute proposed | Rigid or Flexible as option
80 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling
81 | Stormwater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | Additional entries included in Code list Condition Assessment Type
82 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling
83 | Stormwater | Vol 1 | Rigid material standard and QA Separate Flexible material standard and it's QA | Sector Discussion | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA
84 | Stormwater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test
85 | Stormwater | Vol 1 | Compaction strength per NZS4566.2 | Sector Discussion | More information required for a way forward | 2.4.4 Pipe | More information required for a decision
86 | Stormwater | Vol 1 | Third Party QA for pipe material manufacturer | Sector Discussion | Third Party QA Accreditation to code lists | 2.4.4 Pipe | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list
87 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
88 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing
89 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing
90 | Wastewater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
91 | Wastewater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments | New attribute proposed | Installer of Asset
92 | Wastewater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
93 | Wastewater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | 1.7 Heirarchy | Create entries Desktop Visual cctv laser etc
94 | Wastewater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
95 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
96 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
97 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
98 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
99 | Wastewater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | More information is required to inform a way forward | 2.3.4 Pipe | More information required for a decision
100 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling
101 | Wastewater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Compaction Test per NZ4566.2 Foundation strength pre-install
102 | Wastewater | Vol 1 | Compaction strength per NZS4566.2 or NZS3725 | Sector Discussion | More information required for a way forward | 2.3.4 Pipe | More information required for a decision
103 | Wastewater | Vol 1 | Third Party QA for pipe material manufacturer | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
104 | Stormwater | Vol 1 | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure | More information required for a decision
105 | Stormwater | Vol 1 | Spillway should be its own Asset Class | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure | More information required for a decision
106 | Stormwater | Vol 1 | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles | More information required for a decision
107 | Stormwater | Vol 1 | Source for what? This should have more detail. | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | Change made document updated
108 | Stormwater | Vol 1 | Does this include forebay bunds and pond banks associated with ponds? | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks
109 | Stormwater | Vol 1 | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure | More information required for a decision
110 | Stormwater | Vol 1 | Bathymetry Attribute? | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | Haydn suggest this is excluded as I think it can be sourced from LINZ
111 | Buildings | Vol 1 | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable | Noted: no action required | Reviewed and Noted only | General | No action
112 | Buildings | Vol 1 | The Hierarchy table works well | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy | No action
113 | Buildings | Vol 1 | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. | Sector Discussion | Reviewed and Noted only for discussion | General | No action
114 | Buildings | Vol 1 | Complex requirement for such a large property portfolio | Noted: no action required | Reviewed and Noted only | General | No action
115 | Buildings | Vol 1 | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles | No action
116 | Buildings | Vol 1 | This is a huge task for as constructed / as built for a large portfolio | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
117 | Buildings | Vol 1 | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | Reviewed and Noted only | General | No action
118 | Buildings | Vol 1 | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General | No action
119 | Buildings | Vol 1 | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | No action
120 | Buildings | Vol 1 | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes | More information required for a decision
121 | Buildings | Vol 1 | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) | Noted: no action required | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General | No action
122 | Buildings | Vol 1 | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
123 | Buildings | Vol 1 | V_Proc  what is this and what is it to relate to? | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
124 | Buildings | Vol 1 | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? | Included | Tables will be referenced in Final Versions | General | No action
125 | Buildings | Vol 1 | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 | More information required for a decision
126 | Buildings | Vol 1 | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof | More information required for a decision
127 | Buildings | Vol 1 | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision
128 | Buildings | Vol 1 | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision
129 | Buildings | Vol 1 | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone | Noted: no action required | This detail is to be provided at the time it was built not at time of capture This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint | No action
130 | Buildings | Vol 1 | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
131 | Buildings | Vol 1 | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint | Change made document updated
132 | Buildings | Vol 1 | Graffiti  irrelevant | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint | No action
133 | Buildings | Vol 1 | Flood  applicable only in related areas, and this information is on local council records | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint | No action
134 | Buildings | Vol 1 | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint | No action
135 | Buildings | Vol 1 | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint | No action
136 | Buildings | Vol 1 | Design life how is this applied to existing property | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
137 | Buildings | Vol 1 | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling | No action
138 | Buildings | Vol 1 |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
139 | Buildings | Vol 1 | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling | No action
140 | Buildings | Vol 1 | Finish  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
141 | Buildings | Vol 1 | Finish condition assessment, condition and repairs  ✓ The rest is superfluous | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
142 | Buildings | Vol 1 | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satisfy both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling | No action
143 | Buildings | Vol 1 | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
144 | Buildings | Vol 1 | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
145 | Buildings | Vol 1 | Design life  If new = Ok | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
146 | Buildings | Vol 1 | Cost  Not needed? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
147 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
148 | Buildings | Vol 1 | Too much detail required for ceilings. Condition, material, surface finish = Yes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
149 | Buildings | Vol 1 | Risk, Resilience, and Financial performance  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
150 | Buildings | Vol 1 | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
151 | Buildings | Vol 1 | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling | More information required for a decision
152 | Buildings | Vol 1 | Smoke_Barr  Smoke relevant to multiunit development only. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
153 | Buildings | Vol 1 | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling | Change made document updated
154 | Buildings | Vol 1 | Des_Life - ? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
155 | Buildings | Vol 1 | Cost ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
156 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
157 | Buildings | Vol 1 | Whole page  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
158 | Buildings | Vol 1 | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor | No action
159 | Buildings | Vol 1 | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
160 | Buildings | Vol 1 | Live load rating of floor à too difficult to define | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
161 | Buildings | Vol 1 | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
162 | Buildings | Vol 1 | Repairs and Maintenance à what’s the need for this? | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema | No action
163 | Buildings | Vol 1 | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference | No action
164 | Buildings | Vol 1 | First 5 rows à Very detailed for residential use. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
165 | Buildings | Vol 1 | Bracing is as per ceiling notes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
166 | Buildings | Vol 1 | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision
167 | Buildings | Vol 1 | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision
168 | Buildings | Vol 1 | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
169 | Buildings | Vol 1 | Third row à Maybe | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
170 | Buildings | Vol 1 | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
171 | Buildings | Vol 1 | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
172 | Buildings | Vol 1 | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
173 | Buildings | Vol 1 | Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
174 | Buildings | Vol 1 | - Multi storey application only. Too much detail required. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
175 | Buildings | Vol 1 | Last 5 yellow rows à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
176 | Buildings | Vol 1 | - 2nd row à ? Building Code complaint for new works. Unknown for much existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
177 | Buildings | Vol 1 | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
178 | Buildings | Vol 1 | Thermal barrier à ? Floor insulation is all that is relevant in residential. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
179 | Buildings | Vol 1 | All pages à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
180 | Buildings | Vol 1 | Whole page à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
181 | Buildings | Vol 1 | Acoustic row, content  maybe Cost  X Rest of page  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
182 | Buildings | Vol 1 | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
183 | Buildings | Vol 1 | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
184 | Buildings | Vol 1 | Whole page  undefinable in existing housing. | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
185 | Buildings | Vol 1 | Vents  ✓ Membrane rows  Define what membrane? | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation | No action
186 | Buildings | Vol 1 | Foundation area, content à ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation | No action
187 | Buildings | Vol 1 | à See previous foundation notes | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision
188 | Buildings | Vol 1 | All pages à ✕ | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision
189 | Buildings | Vol 1 | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof | No action
190 | Buildings | Vol 1 | Load wind/fix  Not known in existing stock | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof | No action
191 | Buildings | Vol 1 | Frame_Tr  not always identifiable Frame_ Sp  why? | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
192 | Buildings | Vol 1 | Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
193 | Buildings | Vol 1 | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
194 | Buildings | Vol 1 | Last 3 rows  Is this needed and how is it defined? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
195 | Buildings | Vol 1 | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
196 | Buildings | Vol 1 | First row, QA Validation  N/A needs to be applied here | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof | No action
197 | Buildings | Vol 1 | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
198 | Buildings | Vol 1 | Last 5 rows  as per previous notes | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
199 | Buildings | Vol 1 | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
200 | Buildings | Vol 1 | Whole page  ✓ apart from: Cost row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
201 | Buildings | Vol 1 | First 3 rows  ? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
202 | Buildings | Vol 1 | Last row, QA validation à Critical | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof | More information required for a decision
203 | Buildings | Vol 1 | Risk  ✓ Resil, Des_Perf  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
204 | Buildings | Vol 1 | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
205 | Buildings | Vol 1 | Whole page à ✓ Apart from Cost row à ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
206 | Buildings | Vol 1 | First 3 rows à? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
207 | Buildings | Vol 1 | critically, QA Validation à Critical | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
208 | Buildings | Vol 1 | All 3 rows  ? Row 3  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
209 | Buildings | Vol 1 | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
210 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
211 | Buildings | Vol 1 | All 4 rows  ✕, ?, ?, ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
212 | Buildings | Vol 1 | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
213 | Buildings | Vol 1 | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | No action
214 | Buildings | Vol 1 | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
215 | Buildings | Vol 1 | Whole page à✕. Risk – could relate to a water risks | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
216 | Buildings | Vol 1 | Whole page à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
217 | Buildings | Vol 1 | Classifications, Masterpec, Enclosure à not sure what this is representing? | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof | No action
218 | Buildings | Vol 1 | Ins-Type, R_Value à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
219 | Buildings | Vol 1 | Whole page  ✓ Insulation installer and warranty  maybe | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
220 | Buildings | Vol 1 | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
221 | Buildings | Vol 1 | Whole pink pages/part  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
222 | Buildings | Vol 1 | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls | No action
223 | Buildings | Vol 1 | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
224 | Buildings | Vol 1 | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
225 | Buildings | Vol 1 | Grout and Wall Structure Joint  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
226 | Buildings | Vol 1 | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
227 | Buildings | Vol 1 | Condition  ✓ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
228 | Buildings | Vol 1 | Structure, Bracing à As per floor and roof bracing | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
229 | Buildings | Vol 1 | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
230 | Buildings | Vol 1 | Wall, Design Life à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
231 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
232 | Buildings | Vol 1 | Fire barrier à Multiunit. May not be known on existing stock | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
233 | Buildings | Vol 1 | Orange à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
234 | Buildings | Vol 1 | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
235 | Buildings | Vol 1 |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor | No action
236 | Buildings | Vol 1 | Whole page à why would we use this information? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
237 | Buildings | Vol 1 | Acoustic and Thermal rating à Not used. Where applicable? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
238 | Buildings | Vol 1 | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor | No action
239 | Buildings | Vol 1 | à Why / how would we use this? Too much information required. | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs | No action
240 | Buildings | Vol 1 | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs | No action
241 | Buildings | Vol 1 | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
242 | Buildings | Vol 1 | Pages  ✕ | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
243 | Buildings | Vol 1 | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision
244 | Buildings | Vol 1 | Framed and Frame material à not defined in window anatomy page 149 | Sector Discussion | Update diagram on p149 | 2.5.3 Windows | Modify Diagram
245 | Buildings | Vol 1 | Height of windows in mm à what value? | Noted: no action required | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | No action
246 | Buildings | Vol 1 | Condition  ✓ Width  why needed? | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision
247 | Buildings | Vol 1 | Manufacturer, warranty, installation date, installer àUnknown on existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
248 | Buildings | Vol 1 | Design life à How to define? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
249 | Buildings | Vol 1 | Repairs à ? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
250 | Buildings | Vol 1 | Page à✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
251 | Buildings | Vol 1 | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
252 | Buildings | Vol 1 | Hardware à Locks, Yes. Lever/knobs maybe. | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
253 | Buildings | Vol 1 | Whole Column Name – Full is circled à Not always known on existing. Why needed? | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows | No action
254 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
255 | Buildings | Vol 1 | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | No action
256 | Buildings | Vol 1 | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
257 | Buildings | Vol 1 | Services, pink section àmore commercial application. | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
258 | Buildings | Vol 1 | à No! How is this captured realistically and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components | No action
259 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
260 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
261 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
262 | Buildings | Vol 1 | à Would we use this at a per item attribute? | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
263 | Buildings | Vol 1 | Type à ✓ Last row, content à NA | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
264 | Buildings | Vol 1 | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
265 | Buildings | Vol 1 | àToo difficult and unnecessary info | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
266 | Buildings | Vol 1 | à Stove have heater fans | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment | No action
267 | Buildings | Vol 1 | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment | No action
268 | Buildings | Vol 1 | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment | No action
269 | Buildings | Vol 1 | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) | No action
270 | Buildings | Vol 1 | Pink section  Not sure how much of this is required/useful | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) | No action
271 | Buildings | Vol 1 | Blue section - ✓ | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings | No action
272 | Buildings | Vol 1 | Asset type à ✓ Kitchen Vanities in contents | Included | Add to codelist | 2.7.4 Fixtures & Fittings | New Code List entry for Fittings Type proposed | Kitchen Vanities
273 | Buildings | Vol 1 | Length, Height, Width à Why? | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings | More information required for a decision
274 | Buildings | Vol 1 | Whole page à Doubt this would be known | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings | No action
275 | Buildings | Vol 1 | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) | No action
276 | Buildings | Vol 1 | à Covered in Building WOF. *Specialist area = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components | No action
277 | Buildings | Vol 1 | àSpecialists information and only applicable to multi-unit/storey complexes. | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts | No action
278 | Buildings | Vol 1 | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. | Noted: no action required | Reviewed and Noted only | 2.7.9 Security | No action
279 | Buildings | Vol 1 | à Not so useful in residential and difficult to maintain/update. | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage | No action
280 | Buildings | Vol 1 | à Not really applicable to existing housing. Maybe some use in multi-unit development. | Noted: no action required | Reviewed and Noted only | 2.8.1 Space | No action
281 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
282 | Buildings | Vol 1 | à ✕ | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | No action
283 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
284 | Buildings | Vol 1 | Material à ✓ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
285 | Buildings | Vol 1 | Pipe type à ✕ | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data | No action
286 | Buildings | Vol 1 | Water type à ? | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data | No action
287 | Buildings | Vol 2 | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference | No action
288 | Buildings | Vol 2 | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Included | Edited to make clearer | No Specific Reference | Change made document updated
289 | Buildings | Vol 2 | This document excludes industrial buildings and Ancillary building’s  provide examples | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
290 | Buildings | Vol 2 | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
291 | Buildings | Vol 2 | Added Laundry to Outbuildings, included in the Residential standard | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
292 | Buildings | Vol 2 | The bullet points à are they attributes or measures? | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | Haydn
293 | Buildings | Vol 2 | What is Boolean data type? | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type | No action
294 | Buildings | Vol 2 | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | Change made document updated
295 | Buildings | Vol 2 | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | no action
296 | Buildings | Vol 2 | The third and fourth suite of analytics à seems very granular? | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
297 | Buildings | Vol 2 | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | References are being considerd | No Specific Reference | No action
298 | Buildings | Vol 2 | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | Haydn
299 | Buildings | Vol 2 | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference | No action
300 | Buildings | Vol 2 | Table 4. à unclear what this actually shows? | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas | No action
301 | Buildings | Vol 2 | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | No action
302 | Buildings | Vol 2 | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Included | Updated in draft Standards | Code List 16: Condition Rating | No action
303 | Buildings | Vol 2 | Operations definition à What does this mean? Is this routine/preventative maintenance? | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
304 | Buildings | Vol 2 | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
305 | Buildings | Vol 2 | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
306 | Buildings | Vol 2 | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Sector Discussion | Mandatory / Optimal and Optional will be discussed | No Specific Reference | No action
307 | Buildings | Vol 2 | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) | No action
308 | Buildings | Vol 2 | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
309 | Buildings | Vol 2 | 1st bullet point à E.g. roof? Fire alarms? | Noted: no action required | Can be as granular as needed. | No Specific Reference | No action
310 | Buildings | Vol 2 | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Included | Updated in Draft Standards | No Specific Reference | Haydn
311 | Buildings | Vol 2 | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference | No action
312 | Buildings | Vol 2 | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
313 | Buildings | Vol 2 | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | No action
314 | Buildings | Vol 2 | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
315 | Buildings | Vol 2 |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
316 | Buildings | Vol 2 | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes | No action
317 | Buildings | Vol 2 | Code G, Malicious damage à Does this include tenant damage? | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
318 | Buildings | Vol 2 | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating | No action
319 | Buildings | Vol 2 |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating | No action
320 | Buildings | Vol 2 |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference | No action
321 | Buildings | Vol 2 |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
322 | Buildings | Vol 2 |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema | No action
323 | Buildings | Vol 2 | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference | No action
324 | Buildings | Vol 2 | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Noted: no action required | No action required. Understood. | No Specific Reference | No action
325 | Buildings | Vol 2 | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | Haydn
326 | Buildings | Vol 2 | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element | To discuss with technical Working Groups
327 | Buildings | Vol 2 | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Noted: no action required | The attribute is optional. | No Specific Reference | No action
328 | Buildings | Vol 2 | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference | No action
329 | Buildings | Vol 2 | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference | No action
330 | Buildings | Vol 2 | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Noted: no action required | These are at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists | No action
331 | Potable water | Vol 1 | Add USB memory sticks/hard drives to this list. | Included | Changed in all documents | 1.5 Deliverables | Change made document updated
332 | Potable water | Vol 1 | Question: Are there requirements for developers to retain information after transmission? | Noted: no action required | We see this as something for the developer to make the call if they retain a copy or not. | 1.5 Deliverables | No action
333 | Potable water | Vol 1 | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. | Excluded | keep current practice. | 2.1.5 Attribute Data Fields | No action
334 | Potable water | Vol 1 | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. | 2.1.10 Common Attributes | No action
335 | Potable water | Vol 1 | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters | 2.2.1 Area of Work Extent | More information required for a decision
336 | Potable water | Vol 1 | For circular assets, should length and width both be populated and be the same (diameter)? | Included | For circular assets, length is not required and will be made conditional | 2.3.1 Containment Structure | Change made document updated
337 | Potable water | Vol 1 | Rename to Length Metres for consistency | Included | Changed all instances to length metres and length millimetres as appropriate | 2.3.1 Containment Structure | Change made document updated
338 | Potable water | Vol 1 | Overflow = OS? What does OS stand for? Should this be OF? | Noted: no action required | This term was agreed to by the TWG, retained | 2.3.1 Containment Structure | No action
339 | Potable water | Vol 1 | Earlier wells were requested to be polygon type. Is the point supplementary? | Included | Typo corrected, is to be polygon. | 2.3.4 Well | Change made document updated
340 | Potable water | Vol 1 | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station | More information required for a decision
341 | Potable water | Vol 1 | I believe this table and its attribute names have become mis-aligned. | Sector Discussion | Looks OK, need more information | 2.5.1 Equipment | More information required for a decision
342 | Wastewater | Vol 1 | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe | No action
343 | Wastewater | Vol 1 | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. | Noted: no action required | The standards are recording as-constructed | 1.8 Theme Structure | No action
344 | Wastewater | Vol 1 | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? | Noted: no action required | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure | No action
345 | Wastewater | Vol 1 | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
346 | Wastewater | Vol 1 | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets | No action
347 | Wastewater | Vol 1 | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent | More information required for a decision
348 | Wastewater | Vol 1 | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent | No action
349 | Wastewater | Vol 1 | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | Change made document updated
350 | Wastewater | Vol 1 | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
351 | Wastewater | Vol 1 | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
352 | Wastewater | Vol 1 | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber | No action
353 | Wastewater | Vol 1 | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. | 2.3.3 Fitting | No action
354 | Wastewater | Vol 1 | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting | No action
355 | Wastewater | Vol 1 | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting | More information required for a decision
356 | Wastewater | Vol 1 | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. | Sector Discussion | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe | More information required for a decision
357 | Wastewater | Vol 1 | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe | More information required for a decision
358 | Wastewater | Vol 1 | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. | Included | Precision is defined in the standards | 2.3.4 Pipe | No action
359 | Wastewater | Vol 1 | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision
360 | Wastewater | Vol 1 | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe | No action
361 | Wastewater | Vol 1 | These changes should be coded into the pipe geometry, not as separate notes about the pipe. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision
362 | Wastewater | Vol 1 | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | Change made document updated
363 | Wastewater | Vol 1 | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe | More information required for a decision
364 | Wastewater | Vol 1 | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe | No action
365 | Wastewater | Vol 1 | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. | Noted: no action required | Reviewed and Noted only | General | No action
366 | Wastewater | Vol 1 | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | No action
367 | Wastewater | Vol 1 | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe | More information required for a decision
368 | Wastewater | Vol 1 | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? | Included | The intent of the schema is to record what has been contructed at practical completion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | No action
369 | Wastewater | Vol 1 | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe | More information required for a decision
370 | Wastewater | Vol 1 | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General | More information required for a decision
371 | Stormwater | Vol 1 & Vol 2 | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General | More information required for a decision |  | include in glossary terms between NZTA roading and this work | Refer to Volume 1 tab |  | Close: - The mapping between standards will need to be completed post release (as part of implementation)
372 | 3-Waters & Buildings | Vol 1 & Vol 2 | What are the timeframes for this being adopted as mandatory? | Noted: no action required | Business Case. | General | No action
373 | 3-Waters & Buildings | Vol 1 & Vol 2 | Will there be a further round of submissions / comments? | Noted: no action required | Yes. Seminars in November. | N/A | No action
374 | 3-Waters & Buildings | Vol 1 & Vol 2 | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Included | Mandatory, Optimal, Optional will be discussed with the sectors and addressed during the pilot implementation phase | General | More information required for a decision
375 | 3-Waters & Buildings | Vol 1 & Vol 2 | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General | No action
376 | 3-Waters & Buildings | Vol 1 & Vol 2 | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference | Sector discussion
377 | 3-Waters & Buildings | Vol 1 & Vol 2 | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Noted: no action required | Treatment is not included | No Specific Reference | No action
378 | 3-Waters & Buildings | Vol 1 & Vol 2 | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | Included | Asset Classifications have been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
379 | 3-Waters & Buildings | Vol 1 & Vol 2 | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | Noted: no action required | Included in Instruments | Instruments | No action
380 | 3-Waters & Buildings | Vol 1 & Vol 2 | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | Noted: no action required | Separate sections of data cohorts | General | No action
381 | 3-Waters & Buildings | Vol 1 & Vol 2 | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | Sector Discussion | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments | More information required for a decision |  | Noel to provide information to GISSA | Refer to Volume 1 tab |  | New code of practice to be released in a few weeks - Noel to forward to George when it comes out. To be completed before release | Completed in Volume 1
382 | 3-Waters & Buildings | Vol 1 & Vol 2 | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | Included | Statement noted. To be actioned. | General | Change made document updated
383 | 3-Waters & Buildings | Vol 1 & Vol 2 | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well | No action |  | Closed | Refer to Volume 1 tab |  | Close: - for the purpose of analytics wells can be captured under bores | Volume 1
384 | 3-Waters & Buildings | Vol 1 & Vol 2 | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | Included | Suggestion adopted Standards will be updated | 1.5 Deliverables | Change made document updated
385 | 3-Waters & Buildings | Vol 1 & Vol 2 | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Sector Discussion | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | More information required for a decision |  | further conversation needed around how important each data element is (ie core data, mandatory etc) might not be possible to answer this until we get learnings from the Pilots | This is an output from the pilots, as agreed at the workshops | N/A | Close: - This will be determined as part of the implementation
386 | Wastewater | Vol 1 | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. | Noted: no action required | Reviewed and Noted only | General | No action
387 | Wastewater | Vol 1 | a standardised approach to the collation of data relating to As Built (As Constructed) asset information | Noted: no action required | Reviewed and Noted only | Abstract | No action
388 | Wastewater | Vol 1 | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. | Included | Will consdider for final edit - happy to add in. | Executive Summary | Haydn
389 | Potable water | Vol 1 | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. | Sector Discussion | Need recommended maximum attachment size | 1.5 Deliverables | More information required for a decision
390 | Potable water | Vol 1 | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. | 2.1.1 Accuracy Requirements for Locating Assets | No action
391 | Potable water | Vol 1 | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. | Included | picked up previously | 2.1.2 Projections and Datums | Change made document updated
392 | Potable water | Vol 1 | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. | Noted: no action required | agreed, but per pipe section, there is a from-node and a to-node, one of each. | 2.4.4 Node | No action
393 | Potable water | Vol 1 | We split pipes when there is a valve or hydrant on them. While other councils may not | Noted: no action required | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. | 2.4.5 Pipe | No action
394 | Potable water | Vol 1 | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. | Sector Discussion | need examples | 2.4.5 Pipe | More information required for a decision
395 | Potable water | Vol 1 | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | No action
396 | Potable water | Vol 1 | A lot of the attributes seem to be duplicated | Noted: no action required | attributes are all different | 2.5.2 Pump | No action
397 | Potable water | Vol 1 | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. | Included | agreed, diagram will be corrected | 2.7.1 Instruments | No action
398 | 3-Waters | Vol 1 & Vol 2 | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | Included | Updated | General | Change made document updated
399 | 3-Waters | Vol 1 & Vol 2 | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | Included | Updated | General | Change made document updated
400 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General | No action
401 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Noted: no action required | This is a metadata standard not asset management standards. | General | No action
402 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Included | Updated | General | Change made document updated
403 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | Noted: no action required | These are differentr in some cases / in others they are not, not the same definitions across sectors | General | No action
404 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | Noted: no action required | Updated and acknowledge that this will be upto the individual organisation to address | 1.5 Deliverables | No action
405 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | No action
406 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | Noted: no action required | References to be removed. | No Specific Reference | No action
407 | 3-Waters | Vol 1 & Vol 2 | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Noted: no action required | Treatment facilities are not included as part of these standards | No Specific Reference | No action
408 | 3-Waters | Vol 1 & Vol 2 | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Noted: no action required | Out of scope. However resourse consents maybe recorded against the specifc works for each project. | No Specific Reference | No action
409 | 3-Waters | Vol 1 & Vol 2 | Content: • Land – no parameters are set for the recoding of land information. | Excluded | Out of scope. | No Specific Reference | No action |  | closed
410 | 3-Waters | Vol 1 & Vol 2 | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | No action
411 | 3-Waters | Vol 1 & Vol 2 | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | No action
412 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Noted: no action required | Detailed in business case only | No Specific Reference | No action
413 | 3-Waters | Vol 1 & Vol 2 | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Noted: no action required | Applies to all assets. Mandatory and optional fields to be determined during implementation. The benefits to costs covered in business case. | General | No action
414 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Noted: no action required | Covered in business case. | General | No action
415 | 3-Waters | Vol 1 & Vol 2 | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Noted: no action required | Covered in business case. | General | No action
416 | 3-Waters | Vol 1 & Vol 2 | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General | No action
417 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | Noted: no action required | Noted Will be further addressed during the pilot implementation phase | General | No action
418 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | Noted: no action required | This is not within the scope of these standards | General | No action
419 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | Noted: no action required | This is not within the scope of these standards | General | No action
420 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | No action
421 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | closed | Refer to Volume 1 tab |  | George to talk to Nina, Graeme and Mark (Queenstown) - around what it's going to take to make this work | Volume 1
422 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Noted: no action required | Included in the draft Standards | General | No action
424 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums | No action
425 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Included | Included in the draft Standards | 2.1.2 Projections and Datums | Change made document updated
426 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Included | Included in the draft Standards Asset categories included as guidance for each organisation | General | No action
427 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure | No action
428 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | Included | Included in the draft Standards | General | No action
429 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Included | Included in the draft standards | General | No action
430 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General | No action
431 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference | No action
432 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Included | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General | No action
433 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes | No action
434 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) | General for Pipes | More information required for a decision |  | add a reference of where to go to get more specifics around the site | These are other data sets (layers) applied to any analytic and out of scope - per earlier discussions | N/A | Action: - George to remove this field | Completed in Volume 1
435 | 3-Waters | Vol 1 & Vol 2 | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings | No action
436 | 3-Waters | Vol 1 & Vol 2 | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General | No action
437 | 3-Waters | Vol 1 & Vol 2 | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes | No action
438 | 3-Waters | Vol 1 & Vol 2 | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | Sector Discussion | More information is required to inform a way forward | General for Nodes | More information required for a decision |  | Closed | Refer to Volume 1 tab |  | Action: - Geroge to work with Nina on description - conversation moved to volume 1 | Completed in Volume 1
439 | 3-Waters | Vol 1 & Vol 2 | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure | No action
440 | 3-Waters | Vol 1 & Vol 2 | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General | No action
441 | 3-Waters | Vol 1 & Vol 2 | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General | No action
442 | 3-Waters | Vol 1 & Vol 2 | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure | No action
443 | 3-Waters | Vol 1 & Vol 2 | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles | No action
444 | 3-Waters | Vol 1 & Vol 2 | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW | No action
445 | 3-Waters | Vol 1 & Vol 2 | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | Noted: no action required | Data collection is out of scope from these standards | General | No action
446 | 3-Waters | Vol 1 & Vol 2 | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference
447 | 3-Waters | Vol 1 & Vol 2 | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node | No action
448 | 3-Waters | Vol 1 & Vol 2 | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Excluded | Junctions / end points are not assets. | General | No action |  | closed
449 | 3-Waters | Vol 1 & Vol 2 | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Noted: no action required | Junctions / end points are not assets. | No Specific Reference | No action |  |  | This is covered in the standards ODRC, ORC, RC | Code List 47: Financial Performance Metrics | Close: -
450 | 3-Waters | Vol 1 & Vol 2 | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  | Closed | Refer to Volume 1 tab |  | Close: - discuss with volume 1
451 | 3-Waters | Vol 1 & Vol 2 | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | Noted: no action required | The ID proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes | No action
452 | 3-Waters | Vol 1 & Vol 2 | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | Included | Included in the draft standards Code lists have been supplied | General | Change made document updated
453 | 3-Waters | Vol 1 & Vol 2 | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Noted: no action required | Action on volume 1 and business case. The definition of a node has been reviewed and clarified | General | No action
454 | 3-Waters | Vol 1 & Vol 2 | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Noted: no action required | Statement noted. | General | No action
455 | 3-Waters | Vol 1 & Vol 2 | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Noted: no action required | Statement noted. Data transfer is not in scope. | No Specific Reference | No action
456 | 3-Waters | Vol 1 & Vol 2 | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference | No action
457 | 3-Waters | Vol 1 & Vol 2 | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | Noted: no action required | 1. Completed 2. Further information required from respondent. Codelists are now included 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General | No action
458 | 3-Waters & Buildings | Vol 1 & Vol 2 | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | Noted: no action required | Statement noted. Consideration for Volume 1. | General | No action
459 | 3-Waters & Buildings | Vol 1 & Vol 2 | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | Noted: no action required | Statement noted. No action required. | General | No action
460 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | Noted: no action required | Statement noted. No action required. | General | No action
461 | 3-Waters & Buildings | Vol 1 & Vol 2 | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | Noted: no action required | Statement noted. No action required. | General | No action
462 | 3-Waters & Buildings | Vol 1 & Vol 2 | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | Noted: no action required | Business case. | General | No action
463 | 3-Waters | Vol 1 & Vol 2 | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | Noted: no action required | Statement noted. | General | No action
464 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
465 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Included | These inconsistencies have been actioned in the draft standards | General | No action
466 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | These inconsistencies have been actioned in the draft standards | General | No action
467 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | Sector Discussion | To discuss | No Specific Reference | More information required for a decision |  | closed - part of the governance/ownership | OUT OF SCOPE |  | Close: - post release conversation
468 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | Noted: no action required | Action for volume 1. Codelists have been included defining the types of assets covered in each asset class. These codelists are dynamic in nature and over time will be added to as new materials, products etc enter the market | 1.7 Heirarchy | No action
469 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Sector Discussion | Tables to be discussed in Final Version Vol 1 | No Specific Reference | More information required for a decision Tunnels have been included |  | to be included | Refer to Volume 1 tab |  | Close: - discuss with volume 1
470 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy | No action
471 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
472 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
473 | 3-Waters | Vol 1 & Vol 2 | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Included | Tables will be referenced in Final Versions | General | No action
474 | 3-Waters | Vol 1 & Vol 2 | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | No action
475 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Noted: no action required | Statement Noted. Business case. | No Specific Reference | No action
476 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Noted: no action required | Statement noted. | No Specific Reference | No action
477 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Noted: no action required | Business case. | No Specific Reference | No action
478 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference | No action
479 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Noted: no action required | Implenmentation is not within scope | No Specific Reference | No action
480 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Noted: no action required | Business Case | No Specific Reference | No action
481 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Noted: no action required | Business Case. | No Specific Reference | No action
482 | 3-Waters | Vol 1 & Vol 2 | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
483 | 3-Waters | Vol 1 & Vol 2 | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
484 | 3-Waters | Vol 1 & Vol 2 | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | Included | Included in the draft Standards | General | No action
485 | 3-Waters | Vol 1 & Vol 2 | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | No action
486 | 3-Waters | Vol 1 & Vol 2 | The current drafts need additional work at the hierarchy level and better definition / guidance. | Sector Discussion | Asset Classifications have been defined in the Standards | General | More information required for a decision |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Close: - there is a general concensus on this already
487 | 3-Waters | Vol 1 & Vol 2 | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Included | This is about context for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | Further discussion with Sector
488 | 3-Waters | Vol 1 & Vol 2 | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | Included | Included in the draft Standards | General | change made document updated
489 | Potable water | Vol 1 | savvy - edit out slang words like this | Included | removed in current version | Executive Summary | Change made document updated
490 | Potable water | Vol 1 | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? | Included | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. | In Summary | Change made document updated
491 | Potable water | Vol 1 | Consultants - Replace by organisations? | Included | Term consultants now included in glossary. | 1.1 Register | Change made document updated
492 | Potable water | Vol 1 | Again, misuse of term 'consultants. edit through the document to correct this. | Included | Term consultants now included in glossary. | 1.4 Disclaimer | Change made document updated
493 | Potable water | Vol 1 | Is this still used? | Noted: no action required | optional supply | 1.5 Deliverables | No action
494 | Potable water | Vol 1 | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? | Noted: no action required | both schemata and schemas are both acceptible words for the plural of schema. | 1.6 Global Schemas | No action
495 | Potable water | Vol 1 | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? | Noted: no action required | This is not within the remit of the standards | No Specific Reference | No action
496 | Potable water | Vol 1 | how can the analytics standardise the data that has already been standardised? | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | No action
497 | Potable water | Vol 1 | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference | No action
498 | Potable water | Vol 1 | i.e. not fixed and topics can be added? | Included | Agree, asset classes can be added as agreed to | 1.8 Theme Structure | No action
499 | Potable water | Vol 1 | what does this mean? No? but no Y for yes? | Included | N changed to N/A | 1.9 Data Principles | Change made document updated
500 | Potable water | Vol 1 | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.1.1 Accuracy Requirements for Locating Assets | No action
501 | Potable water | Vol 1 | precisely? 'well' is a subjective term | Included | changed | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
502 | Potable water | Vol 1 | no 's' | Sector Discussion | cannot identify | 2.1.1 Accuracy Requirements for Locating Assets | More information required for a decision
503 | Potable water | Vol 1 | change 'issues' to 'risks' throughout document | Noted: no action required | not a risk but an issue | 2.1.10 Common Attributes | No action
504 | Potable water | Vol 1 | Well - change to 'bore' | Noted: no action required | term agreed to by TWG | 2.3.4 Well | No action
505 | Potable water | Vol 1 | does this create a 'node'/ if not then it is a problem for modelling. | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | More information required for a decision
506 | Potable water | Vol 1 | how is a locator or IP cable taped to the pipe represented? | Sector Discussion | Need more information and example | 2.4.5 Pipe | More information required for a decision
507 | Potable water | Vol 1 | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | No action
508 | Potable water | Vol 1 | Is a backflow preventer a mechanical equipment asset or a valve/ | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment | More information required for a decision
509 | Potable water | Vol 1 | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure | No action
510 | Potable water | Vol 1 | this could be much larger with additional definitions e.g.. 'trunk main' | Noted: no action required | Codelists are dynamic and wil expand over time | Glossary | No action
511 | 3-Waters | Vol 1 & Vol 2 | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
512 | 3-Waters | Vol 1 & Vol 2 | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
513 | 3-Waters | Vol 1 & Vol 2 | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
514 | 3-Waters | Vol 1 & Vol 2 | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | Noted: no action required | Volume 2 is now complete | No Specific Reference | No action
515 | 3-Waters | Vol 1 & Vol 2 | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General | No action
516 | 3-Waters | Vol 1 & Vol 2 | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Sector Discussion | Included in the draft Standards Asset Classes included that are relevant to each network. These can be added to over time. The pilot implementation phase will be used as a guide | 1.7 Heirarchy | More information required for a decision |  | Closed | Refer to Volume 1 tab |  | Close: - discuss with volume 1
517 | 3-Waters | Vol 1 & Vol 2 | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | No action
518 | 3-Waters | Vol 1 & Vol 2 | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Included | Tables will be referenced in Final Versions However it is upto each organisation to determine the most approapriate way to create these links based on their systems | General | No action
519 | 3-Waters | Vol 1 & Vol 2 | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
520 | 3-Waters | Vol 1 & Vol 2 | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
521 | 3-Waters | Vol 1 | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General | No action
522 | 3-Waters | Vol 1 | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. | Noted: no action required | Service level performance is included in Volume 2 | General | No action
523 | 3-Waters | Vol 1 | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes | More information required for a decision
524 | 3-Waters | Vol 1 | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
525 | 3-Waters | Vol 1 | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. | Noted: no action required | Please refer to Project and common data | General | No action
526 | 3-Waters | Vol 1 | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset owners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
527 | 3-Waters | Vol 1 | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes | No action
528 | 3-Waters | Vol 1 | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
529 | 3-Waters | Vol 1 | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. | Sector Discussion | More information is required to inform a way forward | General for Pump Station | More information required for a decision
530 | Stormwater | Vol 1 | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. | Noted: no action required | This will be catered for through recording the "Source" | General | No action
531 | Stormwater | Vol 1 | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. | Included | This is a derivation for Volume 3, including precision of survey data | General | No action
532 | Stormwater | Vol 1 | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. | Included | Now normalised and standardsed with Metaconnect | General | No action
533 | Stormwater | Vol 1 | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General | No action
534 | Stormwater | Vol 1 | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General | More information required for a decision
535 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure | No action
536 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). | Included | Already incorporated into the table | 2.3.1 Containment Structure | No action
537 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure | No action
538 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure | No action
539 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure | No action
540 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure | More information required for a decision
541 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall | More information required for a decision
542 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | No action
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment | More information required for a decision
544 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber | No action
545 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | Change made document updated
546 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber | More information required for a decision
547 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | No action
548 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision
549 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber | More information required for a decision
550 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision
551 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. | Sector Discussion | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | More information required for a decision
552 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). | Noted: no action required | Please refer to comment above | 2.4.2 Channels | No action
553 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. | Sector Discussion | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | More information required for a decision
554 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | No action
555 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe | No action
556 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | Haydn
557 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | Change made document updated
558 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe | More information required for a decision
559 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | No action
560 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | No action
561 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? | Included | yes in Volume 2 | 2.4.4 Pipe | No action
562 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | Change made document updated
563 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe | More information required for a decision
564 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). | Noted: no action required | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station | No action
565 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station | No action
566 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. | Included | Attribute fields are included in the Pump asset class for motors. Please review and provide details of additional | 2.5.2 Pump | No action
567 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | No action
568 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. | Sector Discussion | Will include for ratification by the reviewers. | 2.5.2 Pump | New attribute proposed | Trigger level
569 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve | More information required for a decision
570 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | No action
571 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve | No action
572 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment | No action
573 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | Change made document updated
574 | Potable water | Vol 1 | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date | Noted: no action required | Reviewed and Noted only | General | No action
575 | Potable water | Vol 1 | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General | New Code List proposed | Health & Safety Type
576 | Potable water | Vol 1 | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General | More information required for a decision
577 | Potable water | Vol 1 | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) | Noted: no action required | 10 character fields have been adopted to allow for expansion | General | No action
578 | Potable water | Vol 1 | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General | More information required for a decision
579 | Potable water | Vol 1 | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. | Sector Discussion | Need more information and example | General | More information required for a decision
580 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). | Sector Discussion | Need more information and example | 2.3.1 Containment Structure | More information required for a decision
581 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
582 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | No action
583 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | New Code List proposed | Burial Status Above ground Below ground Partially buried
584 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure | No action
585 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure | No action
586 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
587 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
588 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
589 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
590 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision
591 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | No action
592 | Potable water | Vol 1 | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment | No action
593 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL a. Include Ground Water Level | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well | No action
594 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL b. Resource Consent number | Included | Included in Project Attributes | 2.3.4 Well | No action
595 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading | Sector Discussion | Code lists for NZDWS could be included - for discussion | 2.3.4 Well | More information required for a decision
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | More information required for a decision
597 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed | Manufacturer
598 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | No action
599 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. | Included | Agreed | 2.4.3 Fitting | Change made document updated
600 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting | More information required for a decision
601 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe | New Asset Class proposed Detail of data requirements needed | Support Structures
602 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. | 2.4.5 Pipe | No action
603 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | No action
604 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. | Included | Already catered for | 2.4.5 Pipe | No action
605 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe | No action
606 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe | No action
607 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | No action
608 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. | Included | change in all documents | 2.4.5 Pipe | Change made document updated
609 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter | Included | removed nom_Bore | 2.4.5 Pipe | Removal of attribute proposed Have marked for removal in documents
610 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe | More information required for a decision
611 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe | More information required for a decision
612 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision
613 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision
614 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision
615 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber | More information required for a decision
616 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | More information required for a decision
617 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | New attribute proposed | Portable generator (Y/N)
618 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | New attribute proposed | Calculation
619 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve | More information required for a decision
620 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve | New Code List proposed | Valve Control & Automatic Control
621 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. | Sector Discussion | see 00620 | 2.5.3 Valve | New Code List proposed | Valve Power
622 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
623 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve | More information required for a decision
624 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | No action
625 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection
626 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
627 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Incoming Pressure
628 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Outgoing Pressure
629 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Headloss
630 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE l. Valve mechanism code list should be similar to: BFL Butterfly DIA Diaphragm SLC Sluice GAT Gate BAL Ball KNF Knifegate DAV Double air FLP Flap gate NED Needle SAV Single air SND Solenoid WSC Check PRV Pressure reducing RLV Pressure relief | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Mechanism Butterfly Diaphragm Sluice Gate Ball Knifegate Double air Flap gate Needle Single air Solenoid Check Pressure reducing Pressure relief
631 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow
632 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Include attribute fields describing how the pump is powered - electrical, diesel, petrol. | Sector Discussion | Does this relate to the motor or the pump? To be compared to the attributes of the motor | 2.5.2 Pump | More information required for a decision
633 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump | New attribute proposed | Pump oreintation
634 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP c. “Actual pump rate” will at times be meaningless because of Variable Speed Drive (VSD) pumps, that can run at different speeds. This field is therefore either irrelevant for VSD, although it may be an eventual ‘input’ of actual data from control systems. | Noted: no action required | Reviewed and Noted only | 2.5.2 Pump | No action
635 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty end date, Purchase date to be reviewed. | 2.5.1 Equipment | More information required for a decision
636 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. Include Capitalized cost as well as purchase cost | Included | ODRC / ORC / RC are included | 2.5.1 Equipment | No action
637 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT c. The abbreviated and full attribute names contained in this table are not related to each other (this is possible a typographical error). | Noted: no action required | Resolved in updated version | 2.5.1 Equipment | No action
638 | Potable water | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. An attribute field with an ability to include a SCADA reference should be included. | Noted: no action required | Refer to Telemetry | 2.5.1 Equipment | No action
639 | Potable water | Vol 1 | Asset Class: Electrical Asset - CABLING a. Ductwork poses a tricky question because it is separate from cabling. Ductwork can be a part of the structure, and can carry many cables. If it is going to be recorded, Ductwork needs to be an asset class in its own right. | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision
640 | Potable water | Vol 1 | Asset Class: Instrumentation - INSTRUMENTS a. SCADA and RTU (controllers) are not instruments, because they do not measure variables. Include them under electrical equipment. | Included | Reviewed and Noted for Inclusion | 2.7.1 Instruments | Change made document updated
641 | Wastewater | Vol 1 | All Asset Classes a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Will ensure that they are applied. | General | Change made document updated
642 | Wastewater | Vol 1 | All Asset Classes b. Missing asset classes: There are a number of missing asset classes in the Wastewater Standard – including “Containment Structures” and “Tunnels”. Wellington Water has 23 containment structures for Wastewater, which is material in terms of asset renewal. | Sector Discussion | Additional Assets and attributes will be added to final version | General | More information required for a decision
643 | Wastewater | Vol 1 | All Asset Classes c. It was uncertain how the ‘crossover’ between the Wastewater and Stormwater network is managed within the Standard (including weirs). | Noted: no action required | Otherwise please be specific about the uncertainty. | General | No action
644 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. A definition may be required in relation to “relative level”. Relationship of ladders to access chamber; H&S attributes may be required, as ladders need to be certified. Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. This should be considered for inclusion in Volume 2. | Included | Include H&S Attributes | 2.3.1 Access Chamber | Haydn
645 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. Vegetation should not form part of this asset class data attribute for the Wastewater network! | Sector Discussion | to be discussed with the TWG | 2.3.2 Channel | More information required for a decision
646 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b. Is this really an ‘asset class’ for Wastewater (open sewers?) | Noted: no action required | If they do not exist then this asset class will not be used | 2.3.2 Channel | No action
647 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. Generally felt to be a ‘solid’ set of data attributes related to pipes. | Noted: no action required | Reviewed and Noted only | 2.3.4 Pipe | No action
648 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. Is there scope for a new field called “expected remaining life” based on observations? | Included | Remaining life is 'expected', observed or otherwise (e.g. calculated) - related to intervention type | 2.3.4 Pipe | Haydn
649 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. How are ‘pipe supports’ treated within the Standard? | Sector Discussion | Please provide examples of the types of supports that are used | 2.3.4 Pipe | More information required for a decision
650 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. The “Material Description “ field contents need to be set at the correct level – a significant impact on design life results between different materials such as uPVC, mPVC and oPVC, MDPE, HDPE and HPPE | Included | Material is a mandatory attribute | 2.3.4 Pipe | No action
651 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Soil Type should also be captured as part of this Standard (impacts design life) and used to inform a wider geospatial dataset. We need to remember that a pipe may cross several soil types. | Sector Discussion | Was previously discussed and rejected by the TWG | 2.3.4 Pipe | Change made document updated
652 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Surface Material should be recorded as part of this Standard – impacts structural composition. We need to remember that this field must be an updatable attribute based on non-3W observations. Pipes will also cross several different surface material | Included | Add Surface Material | 2.3.4 Pipe | New attribute & associated Code List proposed | Surface Material Surface Material Type
653 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Included | This is a geospatial layer and can attribute accordingly | 2.3.4 Pipe | No action
654 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. In general, the focus group thought this was a well thought out set of attributes associated with Pump Stations. | Noted: no action required | Reviewed and Noted only | 2.3.5 Pump Station | No action
655 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Attributes related to power supply are important; elements of the “electrical” asset class are related to the pump station (see comments in section 2.9 related to the parent-child relationship inherent in pump stations). Attributes include (at least) an ICP number. | Included | Already included. | 2.3.5 Pump Station | No action
656 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION c. The Standard is silent on elements related to “Access” and/or “Easements” for this asset class. | Noted: no action required | Correct. Volume 1 focusses on recording asset data at practical completion | 2.3.5 Pump Station | No action
657 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station | More information required for a decision
658 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION e. The cost attribute is associated with a particular construction date – ie, the pump station is assumed to be ‘static’. This is not likely. (again – may relate to parent-child relationship of pump station to assets it contains). | Included | ODRC / ORC / RC are included | 2.3.5 Pump Station | No action
659 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION f. Safe working limits are a legal requirement  does this form part of the building standard? | Included | Depth is recorded | 2.3.5 Pump Station | No action
660 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION g. “Building Owner” could be split between multiple owners | Included | Owner vs manager fields available in the draft standard Catenate multiple owners in field Buildings are separate assets, see buildings | 2.3.5 Pump Station | More information required for a decision
661 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Elements of a pump may be regarded as a distinct asset – such as motors, impellors, control system, cabling. The attributes of a pump relate to the pump type – this field may need further expansion and/or definition. | Excluded | Detailed drawing and component information is provided in manuals on handover - a reference attribute is included | 2.4.2 Pump | No action
662 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. The line between a pump asset and maintenance is not discussed within the Standard – even though this could change the asset function. | Sector Discussion | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | 2.4.2 Pump | Change made document updated
663 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. The data attributes within this section seem to relate entirely to Electrical Equipment; this does not make sense for this asset class. For example, the “Serial #” field has a description related to “protective material”. | Included | To be resolved in all 3W tables. | 2.4.1 Equipment | More information required for a decision
664 | Wastewater | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. “Risk” should be a key field – with a strong relationship to a relevant Volume 2 table. Safety in Design elements (and residual risk) should form part of this also. | Noted: no action required | Links are not within the remit of these standards - this is an analytical element | 2.4.1 Equipment | No action
665 | 3-Waters | Vol 2 | Data Relationships: Linkages shown in charts between Schema are inconsistent. For example, the “Repairs & Maintenance” schema is shown as interfacing to “As-constructed” and “Condition” schemas. But other Schemas have “Repairs & Maintenance” as an interface. For example, “Financial Performance” and “Demand” both have “Repairs & Maintenance” as an interface. If interlinkages are not shown to be consistent then the validity of the Standard can be questioned. This aligns with the overall statement made in section 1.9 of this document. | Sector Discussion | Relationships are explained in depth in Vol 2 | No Specific Reference | No action |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Closed: - this is now addressed in the standards
666 | 3-Waters | Vol 2 | 2. Project Area: The project area artefact could apply to any business project over the 3 waters and not simply a new subdivision reticulation e.g. new facility or augmentation of WW or WS plant, refurbishment of upgrading of network etc. Understanding how projects/investments are delivered and perform is an important AM capability. The metadata schema should not constrain how assets are managed to meet desired outcomes. | Noted: no action required | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | No Specific Reference | No action
667 | 3-Waters | Vol 2 | 3. Delivery Risk: In order to generate valid information and outcomes the recording of data in a schema for national reporting will require consistency both within an organisation and between organisations over time. This should be recognised as a risk to the successful delivery of benefits by the Data Standard. | Noted: no action required | Delivery risk is a risk for Volume 3 - Methodology | 1.4.2 Intervention Methodologies (Volume 3) | No action
668 | 3-Waters | Vol 2 | 4. Units of measure in asset management would include flow, pressure, time - these are not in the Code list 1, but these and other units are referenced throughout the schemas. Note that different flow and pressure measurement units will apply to different assets or uses. | Included | Amended Code list | Table 2: Water Supply Service Attributes | No action
669 | 3-Waters | Vol 2 | 5. Date Range & Traceability: Similar to the comments made in section 2.1 related to Volume 1, key fields in Volume 2 should be auditable, giving the ability to track when changes are made, why and by whom. While a function of an information system, the requirement for such should be included in a metadata standard. | Sector Discussion | More information is required tofully iundertstand this feedback, but systems business rules (e.g. date ranges) are the place for defining extents, not these standards Assessors are included Data Table 1: Condition Attributes Assessor_N Assessor Name text | No Specific Reference | More information required for a decision |  | there was something to capture here that I missed | This is a systems requirement - not an element for the NZAMS as per our discussions in the workshops | N/A | Close: -
670 | 3-Waters | Vol 2 | 6. Code lists provided for Volume 2 generally require more work to develop consistent, full and meaningful references for use. We note that code lists have not been provided for Volume 1. | Included | Code lists have been updated for comment. | List of Code Lists | No action
671 | 3-Waters | Vol 2 | 7. Depreciation Data: Depreciation is an indicator of loss of service potential. Replacement value must reflect the true value of replacement in the current environment – which may be different to the environment at original installation. Changes to value and the rate of deterioration may be due to specific changes to asset attributes and environment over time. There must be fields to link changes to time and place. | Noted: no action required | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Code List 47: Financial Performance Metrics | No action
672 | 3-Waters | Vol 2 | 8. Lack of observation schema: As noted in section 4.4(a), the lack of an “Observations” schema hampers the ability for observation to inform multiple data schemas – such as condition or updates of asset attributes in the as-built schema. | Noted: no action required | Statement noted. Observations will feed into the attributes. | Data Table 1: Condition Attributes | No action
673 | 3-Waters | Vol 2 | 9. H&S Data: Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. | Included | Now included in Risk attributes Con_Rat_HS Consequence Rating Health and Safety | Table 7: Risk Attributes | More information required for a decision
674 | 3-Waters | Vol 2 | Condition a. Condition data is relevant for a range of decisions and processes in the asset lifecycle, most particularly around renewals, risk and valuations. The following comments consider these aspects but also apply to many of the other processes in some degree. | Included | Statement noted. | 2.2 Condition Schema
675 | 3-Waters | Vol 2 | Condition b. The inclusion of a calculated remaining useful life within the condition schema is fundamentally flawed because it does not account for other relevant asset life determining factors. Examples of such include criticality, demand, performance, optimisation and the asset’s operating environment. By linking condition grade directly to remaining useful life, the schema pre-supposes an end of life or replacement date decision. These conclusions should only be made while considering the wider factors as above. Noting this, Code List 6 linking condition grade to remaining useful life should be removed. | Sector Discussion | Let's discuss - these standards are not about decision-making - they are elements for decisionmaking - these standards define each of these elements. We are not suggesting you should make a decision on condition alone. But if your note is about definition of remaining useful life then let’s chat. | 2.2 Condition Schema | More information required for a decision |  | * need to beef up the wording around 'maximum' v 'predicted failure' * needs some wording around this is the expected life left based ONLY on condition * potentially need to take this conversation offline | Condition is only one decision element. The standards expect critical assets have an influence on the timing of replacement. Interoperability analytics allows you to consider criticality alongside condition (in the example). Unfortunately, currently there is no quantitative analysis between these elements. If the pipe up to the hospital is condition 4 (still has a reasonable expected life, maintenance is within normal levels), then you still might chose to replace it because it's the pipe up to the hospital and do not want to take the risk. | N/A | Close: - this information is needed to be captured
676 | 3-Waters | Vol 2 | Condition c. It is recommended that the schema be modified to take into account the level of confidence in condition grades. There is little or no recognition of the probabilistic nature of condition assessments and hence the confidence limits which apply to the grades. Any condition grade is made within a band of confidence at a point in time. The confidence level is relative to whether it is being applied to a subject asset or extrapolated to an asset group, and whether it is applied at the time of assessment or projected forward. | Noted: no action required | This is a calculable field, for example, stochasticity | No Specific Reference | No action
677 | 3-Waters | Vol 2 | Condition d. The basis of the interfaces with other schema (Table 5) is unclear and the linkages shown do not acknowledge the relationships between condition data and all other schema. Eg: i. Criticality determines priorities for condition data collection ii. Repairs and maintenance activities are a key potential source of condition data iii. Condition is indicative of likelihood of failure and hence helps determine risk iv. Service and financial performance are impacted by condition v. Demand and utilisation inform the criticality of an asset and hence priority for condition data collection. | Noted: no action required | These are analytical outputs of specific problems being solved. We can discuss | No Specific Reference | No action
678 | 3-Waters | Vol 2 | Condition e. Items included in the condition data attributes (Table 2) appear to be a mix of data at different levels of detail; some being at the assessment level and others at the observation level. Any hierarchy or relationship between these is not implied or explained however. The potential one-to-many linkages from asset to assessments and further to observations are not apparent. Any data required must be clarified in terms of how it relates to other data to enable practical processes for capture and storage. | Sector Discussion | Action: To be discussed with Wellington Water. | Data Table 1: Condition Attributes | More information required for a decision |  | * need to beef up the wording around 'maximum' v 'predicted failure' * needs some wording around this is the expected life left based ONLY on condition * potentially need to take this conversation offline | Condition can be determined a number of ways, the standards reflect this fact. | N/A | Action: Haydn and Nina to discuss (Haydn agreed to buy coffee/wine) and then revert with actions if needed | HAYDN
679 | 3-Waters | Vol 2 | Condition f. The description of condition grades against physical deterioration (Code List 2) is a good approach however the terminology is inconsistent. Most descriptors but not all relate to asset failure. All should be described on the same basis to allow for consistent interpretation. “Asset failure” in this sense also requires definition and is unclear in the schema. | Included | Uniform terminology now applies | Code List 16: Condition Rating | No action
680 | 3-Waters | Vol 2 | Condition g. The condition grade types (Code List 3) are unclear and do not give any sense of the distinctions or relationships between structural, service, mean, peak and overall grades. | Included | Condition code lists (e.g. structural, exterior, interior) are now included in Vol 2 | Code List 16: Condition Rating | No action
681 | 3-Waters | Vol 2 | Condition h. The condition grade assessment methodologies (Code List 4) and assessment types (Code List 5) are extremely limited and do not capture many methodologies that are currently available and in use. Terminology is not consistent with the purpose of the list, ie; “Cut out” is a sampling methodology rather than an assessment type as listed. A cut out may be assessed visually, by destructive and/or non-destructive testing, or other means. Code lists 7 – 10 are similarly limited and the purpose and usage of which are unclear. | Sector Discussion | See code list | Code List 17: Condition Rating – Methodology | More information required for a decision |  | update the documentation to state - there is an expectation that over time this code list will grow | This is an issue for volume 3 | N/A | Close: - standards will need to be updated during and after initial implementation
682 | 3-Waters | Vol 2 | Repairs and Maintenance a. The Proactive and Reactive Activity Type descriptions need additional clarification to minimise ambiguity. How should “impairment” be interpreted - breakdown, significant performance issue or just incipient failure only detectible with monitoring equipment (e.g. bearing vibration, thermographic image, etc)? Also “Scheduled” needs to exclude non-routine or one-off activities that are set to occur in the future. | Noted: no action required | See code list | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
683 | 3-Waters | Vol 2 | Repairs and Maintenance b. The schema does not support optimisation of maintenance tasks through RCM analyses or other FMECA based approaches. An example would be the need for a clear and unambiguous definition of asset function. This is not well covered in Part 1 attributes. Comment should be requested from an RCM practitioner. | Noted: no action required | Statement noted. This is not a maintenance management system. | No Specific Reference | No action
684 | 3-Waters | Vol 2 | Repairs and Maintenance c. Recording the “Image_ID” against activities does not cater for referencing other types of digital files. Suggest this optional attribute is made generic and capable of accepting hyperlinks to reference files in other systems. | Noted: no action required | This is an analytical requirement | No Specific Reference | No action
685 | 3-Waters | Vol 2 | Repairs and Maintenance d. Fail_Mode and Cause_Iss is important but must be specific to each asset type rather than generic across all assets. It’s not clear if this is the intention. | Noted: no action required | This is an analytical requirement and is matched to other elements (e.g. AssetID) to determine response | No Specific Reference | No action
686 | 3-Waters | Vol 2 | Repairs and Maintenance e. A key decision for every asset is to either run to failure or apply a scheduled maintenance/inspection plan. | Noted: no action required | This is an analytical requirement (i.e. both) | No Specific Reference | No action
687 | 3-Waters | Vol 2 | Repairs and Maintenance f. In Part 1 Condition Assessment Type is an asset attribute, but Condition is part of a different schema. Shouldn’t these go together to reflect the fact that the condition assessment approach may change over time? | Included | Yes, but in the analytical phase. | No Specific Reference | No action
688 | 3-Waters | Vol 2 | Repairs and Maintenance g. It isn’t clear how maintenance strategies are to be handled (i.e. managing maintenance work that has weekly/monthly/annual/ etc activities). AMIS functional requirements should be considered before fields like Recur and Recur_Cyc are established. | Noted: no action required | Standard is not intended to populate a maintenance plan. Code Lists are included to handle this requirement e.g. Recurrence Cycle | Code List 5: Recurrence Cycle Unit | No action
689 | 3-Waters | Vol 2 | Repairs and Maintenance h. Need quantity as well as cost information to be able to analyse trends and predict future costs. Need to record all resources – not restricted. | Noted: no action required | Code lists for quanitifying repairs included | Code List 6: Bases of Cost | New Code List from Working Group
690 | 3-Waters | Vol 2 | Repairs and Maintenance i. The combination of Activity Type, start date/time, end date/time does not appear to meet the requirements for DIA non-financial reporting for urgent/non-urgent callouts (i.e. need to separately record time to reach site and time to resolve issue). | Noted: no action required | Type of maintenance activity is included | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
691 | 3-Waters | Vol 2 | Repairs and Maintenance j. There needs to be a new Event Type similar to “Upgrade/Improvement”. Irrespective of the funding source (capital vs operational) assets need to have a full history of events recorded against them. If we exclude upgrades and rely solely on project registers to capture this information we make lifecycle management significantly more difficult. | Noted: no action required | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Code List 49: Description of Financial Performance Element | No action
692 | 3-Waters | Vol 2 | Repairs and Maintenance k. Why record overflows etc. in repairs and maintenance schema and not in the level of service? Overflows are recorded per financial year, different organisations have different financial years, is history recorded i.e. over time. Should other compliance activities i.e. RON and CDEM should also be coded. | Included | One is a record of the type event One is a record a service level e.g. overflows per year and an analytic | Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | No action
693 | 3-Waters | Vol 2 | Repairs and Maintenance l. Asset versus component issue can give rise to different design criteria and system performance i.e. a pump has a l/s design while a filer has (say) minimum pressure drop, but it is performing of the pumping station that is the issue. | Noted: no action required | Statement noted | No Specific Reference | No action
694 | 3-Waters | Vol 2 | Repairs and Maintenance m. Does not appear to allow for other investigation methods e.g. vibration analysis, DCVG results, thermal imaging, usage data analytics for identifying if an intervention is required. | Included | Code lists to be discussed against current code lists e.g. Condition (This is really a Volume 3 question) | Code List 17: Condition Rating – Methodology | No action
695 | 3-Waters | Vol 2 | Repairs and Maintenance n. As found and as left condition or status is useful for items like valves, could also apply to depth of cover, locks etc. | Included | Statement Noted: No action required. | No Specific Reference | No action
696 | 3-Waters | Vol 2 | Repairs and Maintenance o. Asset performance does not clearly link to key result areas or key performance indications set by organisations in the management of assets or demanded by consumers. | Sector Discussion | This is an anlytical question - discuss with sector | No Specific Reference | More information required for a decision |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Close: -
697 | 3-Waters | Vol 2 | Repairs and Maintenance p. Asset or service performance - it is not clear what is referred to or if this is consistent. | Sector Discussion | Section updated in Volume 2 | 5.4 Service Performance Schema | More information required for a decision |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Close: -
698 | 3-Waters | Vol 2 | Repairs and Maintenance q. How are components and soft parts etc linked to assets, is the lifecycle of O&M supported by this? | Noted: no action required | Component type is an attribute in the repair schema and captured under each asset. | 2.3.4 Components of Repairs, Maintenance and Operations | No action
699 | 3-Waters | Vol 2 | Repairs and Maintenance r. Benchmarking - same as identified in service levels schema, consistency is required for valid and useful outputs to be obtained. | Noted: no action required | Statement noted and agreed. | No Specific Reference | No action
700 | 3-Waters | Vol 2 | Repairs and Maintenance s. Outage duration - mandatory for all actions but what if no outage? Also what if the customers are reinstated over time ie 95% connected in 1 hour while the rest are out for days? Outage is linked to ' number of people' - this can be impossible to measure depending on each connection (as in an apartment block), would customer or property be a better measure. | Noted: no action required | Agreed. Then outage duration = 0. | No Specific Reference | No action
701 | 3-Waters | Vol 2 | Repairs and Maintenance t. Third party damage excluded from outage definition but included in repair schema as cause. | Included | Third Party attribute included | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
702 | 3-Waters | Vol 2 | Repairs and Maintenance u. Maintenance planning - focused on time based maintenance (elapsed), but could encompass operating hours or CBRM. A MMS would do a better job, would it be better not to specify these matters in the schema and just have an objective for an outcome based system in place. This could be applied throughout the data standard noting the issues with consistently in benchmarking. | Sector Discussion | Analytical elements included in standards to schieve this analytic | No Specific Reference | More information required for a decision |  | this is a volume 3 discussion - closed | OUT OF SCOPE |  | Close: -
703 | 3-Waters | Vol 2 | Repairs and Maintenance v. It would be desirable to have costs for maintenance collected on an area/project basis for performance analysis. | Included | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | No Specific Reference | No action
704 | 3-Waters | Vol 2 | Repairs and Maintenance w. Should complaints be linked to an issue or root cause rather than an address or asset - this would enable better linking and development of appropriate solutions and priority setting than a collection of disparate reports. Also need to know the outcome of the assessment of a compliant ie internal plumbing, no issue found etc before an organisation make decisions on number of complaints. Option of an outcome based CRM system rather than data standard? | Included | Linking CRM information to asset information is not in scope These root cause examples in the code list are asset related interrogations for asset management purposes. | No Specific Reference | No action
705 | 3-Waters | Vol 2 | Utilisation a. Asset utilisation needs to consider the level of redundancy in the network or asset system required to achieve the desired overall level of risk. The proposed calculation of utilisation could work for an individual pump, but would be of little/no value for a trunk main network. It could easily be misinterpreted. | Included | Redundancy is include in the codelists in Vol 2 as an analytical attribute (see vulnerability). | Code List 43: Global Resilience Rating Elements | No action
706 | 3-Waters | Vol 2 | Utilisation b. Until the intervention methodologies are proposed for each of the 3 waters we find it difficult to understand what fields may or may not be wanted for this schema. | Noted: no action required | Statement noted. | 3.2.5 Code Lists
707 | 3-Waters | Vol 2 | Demand a. Demand applies to collections of assets. Why would you want to record demand against an individual asset such as a pipe or valve? | Included | This is an analytics requirement, but may no be required agaist all asset components. | No Specific Reference
708 | 3-Waters | Vol 2 | Demand b. The fields offered are very limiting in this schema and the use of demand needs to be thought through in more depth. | Noted: no action required | Demand Section has been updated in Volume 2 | 3.3 Demand Schema
709 | 3-Waters | Vol 2 | Demand c. Peak demand at a system level is not the sum of zone demands due to the diversity/averaging effect as the study area increases in size. Average demand at a system level is the sum of the zone demands. The schema does not seem to recognise this. | Noted: no action required | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler | Data Table 4: Demand Attributes | No action
710 | 3-Waters | Vol 2 | Demand d. What analytics would this schema (as is) be used to support? | Noted: no action required | Future connections on flow (population demand) | Code List 33: Demand – Measure | No action
711 | 3-Waters | Vol 2 | Demand e. Should this schema exist in an AMIS? | Noted: no action required | Yes | 3.3 Demand Schema | No action
712 | 3-Waters | Vol 2 | Criticality a. Criticality is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | No change | 4.3 Criticality Schema | No action
713 | 3-Waters | Vol 2 | Criticality b. The current approach to criticality from Wellington Water uses criticality as an equivalent to consequence in the evaluation of risk. To this effect the criteria for criticality that we have developed uses cumulative weighted impacts in combination with importance (exposure) factors to derive risk. My view is that the criticality descriptors offered in the standards are only one component of the consequence variable in the risk equation ie the exposure factor. To this extent it is puzzling to identify how criticality as described could be used in the evaluation of risk – given the subsequent content of the risk schema. | Noted: no action required | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | 4.3 Criticality Schema | No action
714 | 3-Waters | Vol 2 | Criticality c. For example if the renewal of a pipe was being considered wrt risk of failure – condition is an indicator of probability, the potential impacts could be social, environmental or financial loss and the exposure is measured by the number of people or the importance of the facility affected by the loss of service. | Noted: no action required | These are analytical inferences which are attributed in code in algorithms by attributes these standards define | No Specific Reference | No action
715 | 3-Waters | Vol 2 | Criticality d. Until worked examples are provided as to how the consultants perceive criticality being used for different decisions we struggle to see how the schema as offered would be useful or at best would have limited value. | Noted: no action required | Explanation found in criticality schema | 4.3 Criticality Schema | No action
716 | 3-Waters | Vol 2 | Criticality e. The code list 27,28,29 tables have some potential flaws in our view. i. Special facilities is too vague as a term for Code 5. Few utilities would have munition storage or critical data centres and in most cases data centres would have back up. How is this derived for example if it was potential damage from blowing up a munitions store, how would compare to an LPG centre or holding tanks containing solvents ii. For a water utility is a hospital really less critical than a data centre? iii. What happens when an asset services 3 or 4 hospitals iv. Where is economic loss factored into these tables – they seem to be very “government” centric v. We struggle to think that decision making using criticality for small towns of less than 5000 people would only ever have code 3 assets as their most important asset. Risk is about context and the context must consider the community and the economic scale of their investment. We do not believe one size fits all. | Noted: no action required | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. | No Specific Reference | No action
717 | 3-Waters | Vol 2 | Risk a. Risk is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | Statement noted. | No Specific Reference | No action
718 | 3-Waters | Vol 2 | Risk b. We assume that the risk schema is intended to facilitate risk management within water utilities. | Noted: no action required | Yes, and for buildings per the Biulding Standard | 4.4 Risk Schema | No action
719 | 3-Waters | Vol 2 | Risk c. We have reviewed this schema with respect to the principles of risk management as outlined in Section 3 of the guideline document for AS/NZS 31000:2009 | Noted: no action required | Noted | 4.4 Risk Schema | No action
720 | 3-Waters | Vol 2 | Risk d. In particular the schema as drafted inhibits the following principles: | Noted: no action required | Noted | 4.4 Risk Schema | No action
721 | 3-Waters | Vol 2 | Risk e. 3(g) Risk management is aligned with the organisations external and internal context and risk profile | Sector Discussion | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Close: -
722 | 3-Waters | Vol 2 | Risk f. 3(h) Risk management recognises the capabilities, perceptions, and intentions of external and internal people that can facilitate or hinder the achievement of the organisations objectives | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
723 | 3-Waters | Vol 2 | Risk g. 3(j) Risk management continually senses and responds to change. As external and internal events occur, context and knowledge change, monitoring and review of risks takes place, new risks emerge, some change, others disappear | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
724 | 3-Waters | Vol 2 | Risk h. To propose a specific risk matrix into a national standard seems to conflict with these basic principles | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct And any organisation can taylor the analysis to the local context | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
725 | 3-Waters | Vol 2 | Risk i. Although interdependencies between other schemas are stated it is difficult to extract how they would be used together. Risk, criticality and condition must be interconnected but there is no indication as to how the application of these schemas would allow this | Noted: no action required | This would depend on the problem being solved and the analytical approach in doing so | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
726 | 3-Waters | Vol 2 | Risk j. The suggestion that probability scales for different events and water types are the same is unhelpful in the absence of worked examples. Are there examples to demonstrate a sensible cross relationship for the use of probability scales in water supply and stormwater? | Noted: no action required | Unclear of what this means, but the scales are adaptive to event type, but specifiuc to asset type | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
727 | 3-Waters | Vol 2 | Risk k. Other than flood risk, how do you assess time based probabilities? The use of the word “time to time” or “in your career” will lead to subjective assessments that will simply promote inconsistent investment decisions rather than secure them. | Noted: no action required | Code list updated | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
728 | 3-Waters | Vol 2 | Risk l. We believe the contents of the fields that describe 1- 5 consequences should be omitted. A decision to occupy these fields for a national risk schema to derive nationally consistent approaches to risk will do exactly the opposite – it promotes subjective assessment and also directly contravenes the principles of risk management as described in AS/NZS 31000. | Noted: no action required | To discuss, see code lists | Code List 41: Consequence Rating | More information required for a decision
729 | 3-Waters | Vol 2 | Resilience NO schema offered However, we urge you to consider a fundamental question when addressing resilience for water utilities. Is the assessment of an assets’ resilience important or is it more important to assess the resilience of the service provided to customers on a national scale? We would suggest the latter, and therefore question the merits of offering a schema for asset resilience. If it is the latter, we also suggest that resilience is better attributed to customers rather than assets. | Included | Schema updated | 4.5 Resilience Schema | No action
730 | 3-Waters | Vol 2 | Design Performance This schema is not required. We don’t need evaluative criteria here. Attributes should be in the as built schema and actual performance should be in service performance. Table 12 in all volume 2 documents (sections 9.3) refer to the linkages with the resilience schema not the design performance | Noted: no action required | Let's discuss this is important. Design performance is different than Service Performance | 5.2 Design Performance Schema | More information required for a decision
731 | 3-Waters | Vol 2 | Financial Performance a. General comment – It would be interesting to know what is determined to be core data requirements with regards to the attributes. There is a large set of attributes to collect a large number would only be relevant to a small number of organisations. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | 5.3 Financial Performance Schema | No action
732 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
733 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
734 | 3-Waters | Vol 2 | Financial Performance c. Valuation date doesn’t seem to appear anywhere. | Noted: no action required | Included in standards | Data Table 10c: Valuation Attributes Details (Collected Level Indicated) | No action
735 | 3-Waters | Vol 2 | Financial Performance d. Linking the financial information e.g. revised asset lives with condition data. | Noted: no action required | Attributes included in standards, this is an analytical exercise | No Specific Reference | No action
736 | 3-Waters | Vol 2 | Financial Performance e. Terminology is not consistent with the Repairs and Maintenance schema e.g. reactive/planned/etc. | Noted: no action required | Now consistently applied | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
737 | 3-Waters | Vol 2 | Service Performance Level of service is recorded against individual assets, this may cause issues where service level is required from a network, facility, project, contract or organisational levels. These levels of service may not directly relate to asset parameters or the level of service at an asset may relate to another asset upstream (e.g. minimum pressure at a downstream point relates to the upstream network and pumps/regulators etc). Also levels of service are not static and these may change (this change may be the result of internal or external drivers). | Noted: no action required | These are analytical constructs from an individual assetID dataset. How consolidated into geographic units os for the specific analysis, e.g. network, zone, catchement etc. | No Specific Reference | No action
738 | 3-Waters | Vol 2 | Service Performance a. Benchmarking relies on the consistency of inputs. In order to generate valid information and outcomes the recording of data in a scheme for national reporting will require consistency in an organisation, between organisations and over time. Other national standards have shown there are issues with this approach, will the benefits of a metadata standard be realised (what are the risks and assumptions to the achievement of this benefit)? | Noted: no action required | This is a reference to standardised analytical approaches | No Specific Reference | No action
739 | 3-Waters | Vol 2 | Service Performance b. Residential demand figure, valid for industrial or commercial areas, how updated and how is history against assets recorded? | Noted: no action required | This is a reference to an analytical approach. E.g. ParcelID District Plan Zone type and connection demand (or Level of Service). | No Specific Reference | No action
740 | 3-Waters | Vol 2 | Service Performance c. Is it feasible that the same assessor (individual) is used for all items in each asset i.e. cultural significance and technical design and financial measures? | Noted: no action required | The same or multiple | No Specific Reference | No action
741 | 3-Waters | Vol 2 | Service Performance d. Consents compliance is linked to an asset when consents are typically given on an activity/facility - correct linkages and business processes will need to be established and implemented to ensure that compliance is achieved in light of asset changes. | Noted: no action required | Consent attributes are captured at property level which is not inconsistent with reporting at network/zone level - i.e. it is a spatial query between the two data sets. The attributes are specified for capturing asset detail in the standards | No Specific Reference | No action
742 | 3-Waters | Vol 2 | Service Performance e. Third party damage is excluded from service measures (interruptions) for water supply. This is a valid facet of AM, and the scheme has this included in repair and maintenance for WW assets. | Noted: no action required | Included in the Standards | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
743 | 3-Waters | Vol 2 | Service Performance f. MoH grading should be linked to a time the grade was awarded, and possibly should be greater than just a single field i.e. who assessed etc. We question the merit of this as a valid asset performance measure as it is always system based. | Noted: no action required | Included in the Standards | Data Table 11: Service Performance Attributes – Functional | No action
744 | 3-Waters | Vol 2 | Service Performance g. The fact a health and safety assessment has been carried out is interesting, but it is the results that are important (have the risks been addressed or are there outstanding issues etc) and there is no mention of this. | Noted: no action required | Included in the Standards | Table 2: Water Supply Service Attributes & Code List 41: Consequence Rating | No action
745 | 3-Waters | Vol 2 | Maintenance Planning i. Will the scheme provide an effective (and efficient) link to maintenance management systems that are in use currently? | Included | Yes that is the intention for the future. | No Specific Reference | No action
746 | 3-Waters | Vol 2 | Maintenance Planning ii. Are all costs collected at an asset level, won't different treatments give rise to different outcomes, ie, where are staff or contractor costs added to a facility, item or asset. Is maintenance carried out on assets as they exist or on notional assets? | Included | Application of costs will be at the discretion of the rganisation, but likely to be applied to a cohort of assets when being maintained | No Specific Reference | No action
747 | 3-Waters | Vol 2 | Operational Performance i. Actual performance should also be recorded as well as consent compliance - is water quality improving over time or always just inside the limit? | Included | Action: add in to schema (design performance? Service performance) | Data Table 9: Design Performance Attributes | No action
748 | 3-Waters | Vol 2 | Operational Performance ii. There is reference to LAWA framework – is this commonly used throughout the country? Would it be better to refer to the National Policy Statement or specific Regional rules as applicable for the authority? | Noted: no action required | All regional councils use LAWA | No Specific Reference | No action
749 | 3-Waters | Vol 2 | Valuation and depreciation Asset life versus economic/accounting life, does asset structure match the chart of accounts used by all organisations and applied in all business models i.e. contracted services? | Noted: no action required | Yes - there are appropriate fields for ODRC, ORC, RC and Forecast, Actual and Budget financial information in Finance Performance sections | Code List 47: Financial Performance Metrics | No action
750 | 3-Waters | Vol 2 | Planning for growth or decline i. Assets will need lifecycle stages not just in service ie proposed (linked to project), out of service, in store, abandoned, leased for F/O etc (assets can provide other services, not just those implicit in the standard) | Included | Discuss with Sector - to consider schema | No Specific Reference | Create a code list of service types as suggested here?
751 | 3-Waters | Vol 2 | Planning for growth or decline ii. Levels of service can change over time on different assets, this will need to be understood/recorded | Noted: no action required | Atributes to do this are included in the standards | No Specific Reference | No action
752 | Wastewater | Vol 1 | In talking about As Managed, I assume this is for how the councils handle data rather than how the data supplied by survey from the field, as these are two different worlds? | Sector Discussion | This is a discussion in the development of Volume 3 | No Specific Reference | No action
753 | Wastewater | Vol 1 | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this | Included | Reviewed and Noted for Inclusion Included as part of the Project Attributes table Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | More information required for a decision
754 | Wastewater | Vol 1 | There is increased risk to data accuracy in companies that are not working all the time with software projection transformations. As the client, I would always want to receive the data in it original projection and transfer it myself | Included | The requirement is for each company to deliver the data in the final projection and datum | 1.5 Deliverables | No action
755 | Wastewater | Vol 1 | Why is this BIM Enabled? Should this not be BIM Enabled/Geospatial Representation as these still hold and display 3d information. | Noted: no action required | Update, asset management and facility management systems do…. | 1.9 Data Principles | No action
756 | Wastewater | Vol 1 | This surely should be "current parcel" boundaries. Not sure as to what a title/property boundary is, as what is the definition of property (residence, address, rating unit, parcel(s))? Also, is this relevant?You want the assets to be shown in true survey location even if this shows them being constructed illegally through private property. | Sector Discussion | For analytical purposes Have added 'geographical units' code list | 2.1 Technical Reference Information | More information required for a decision
757 | Wastewater | Vol 1 | I believe this is how data should be stored, but supply of data should be as captured. By forcing this to the supplier you are increasing the risk of error, with groups that will only project data occasionally more likely to make mistakes | Noted: no action required | The intent of this is to educate the indutsry in what capability it will need | 2.1.2 Projections and Datums | No action
758 | Wastewater | Vol 1 | Why would you develop a new specification and then allow for it to be supplied in a historic format such as shapefile. This also means that the defined "text" geometry type cannot be supplied and instead would need to be changed to a point | Noted: no action required | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF | 2.1.7 Metadata Definitions | No action
759 | Wastewater | Vol 1 | Is this cost of the asset or cost of the asset plus installation? Is this standard cost of the recommended price of the asset, rather than any discounts were achieved? | Noted: no action required | All replacement costs include installation | 2.1.10 Common Attributes | No action
760 | Wastewater | Vol 1 | Is the central location the centre of access (i.e. manhole lid)or the centre of the structure? | Included | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. | 2.3.1 Access Chamber | Change made document updated
761 | Wastewater | Vol 1 | Pipe length shown here is neither the length of the digital pipe feature or the length of the real world feature, as you are not taking into account the "faux" pipe connectors angle. The middle pipe length here is very confusing! | Sector Discussion | Need more information for a way forward | 2.3.1 Access Chamber | More information required for a decision
762 | Wastewater | Vol 1 | Does this mean covered by dirt and not readily accessible or below ground level? | Noted: no action required | Below ground level | 2.3.3 Fitting | No action
763 | Wastewater | Vol 1 | What happens when two separate pipes are installed between access points (e.g. different material etc). Also there are examples were pipes may not have access chambers (as defined by this document). While that may be not best practice, it does occur. | Noted: no action required | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists | 2.3.4 Pipe | No action
764 | Wastewater | Vol 1 | Is this the digital length or the real world length? | Included | This is the real world length as described in the QA validation field. | 2.3.4 Pipe | No action
765 | Wastewater | Vol 1 | What does this mean? What level of accuracy is defined as a discrepancy? | Included | Changes made to wording to reflect tolerances used in practice ('field') | 2.7.2 Matching to Existing Infrastructure | Change made document updated
766 | Potable water | Vol 1 | Asset Group: To be consistent with Section 1.8 Should this heading be changed to "Asset Category" ? (Or in section 1.8 change "Asset Category" to "Asset Group" | Included | Changed to Asset Group for consistency. | 1.7 Heirarchy | Change made document updated
767 | Potable water | Vol 1 | Asset Type: To be consistent with Section 1.8, should this be changed to "Asset Class" | Included | Changed to Asset Class. | 1.7 Heirarchy | Change made document updated
768 | Potable water | Vol 1 | The paragraph refers to "Asset Types", yet table 1.8 does not reference "Asset Types", only "Asset Class". If these are not interchange in relation to meaning, then I suggest a explanation of "Asset Type" and "Asset Class" be documented within the document somewhere. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
769 | Potable water | Vol 1 | My personal preference is to utilize "Asset Class" as standard terminology, and replace any instances of "Asset Type" within the document if they are inferring the same meaning. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
770 | Potable water | Vol 1 | My personal preference is to utilize "Asset Category" as standard terminology, and replace any instances of "Asset Group" within document. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
771 | Potable water | Vol 1 | Conflicts with section 2.3.4 states that a well is to be represented as a polygon | Included | Changed to Polygon | 1.8 Theme Structure | Change made document updated
772 | Potable water | Vol 1 | Listed here as a guide, but each definition of the asset class states the required spatial representation. ie 2.3.1 states polygon feature. Therefore for clarity, should this table also list the requirement of the standard for each asset class? | Sector Discussion | More information is needed for a way forward | 1.9 Data Principles | More information required for a decision
773 | Potable water | Vol 1 | I am assuming this only for Geo-spatial attributes? (As there may be different sources utilized across multiple attributes.) If this is correct, can this be added for clarity in the contents column. | Included | Defined by organisation | 2.1.10 Common Attributes | No action
774 | Potable water | Vol 1 | If the data source changes, is there a need to keep a date history of the changes. | Noted: no action required | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. | 2.1.10 Common Attributes | No action
775 | Potable water | Vol 1 | Common Attributes for your consideration: (We currently have the following 3 attributes fields across all our assets) - Manufacturer (of asset) - Supplier (of asset) - Installed By (Contractor who installed asset) Fields to be utilized to identify failing assets due to manufacturer/supplier and potential faulty installation by a contractor. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
776 | Potable water | Vol 1 | This field should be allowed to be empty. What if there is no photographic references available. Flows through to Asset Class definitions | Sector Discussion | consider N/A as an appropriate response. | 2.1.10 Common Attributes | More information required for a decision
777 | Potable water | Vol 1 | Define "Asset Classes" and "Asset Types" | Included | Asset Classifications have been defined in the Standards | 2.2 Asset Categories | No action
778 | Potable water | Vol 1 | RL: Add a definition of RL in the "Glossary of Terms and Definitions" in the document (Reduced Level) "RL" acronym used in multiple places in the document. | Included | Included in Glossary | 2.3.2 Embankment, Glossary | Change made document updated
779 | Potable water | Vol 1 | No Type field for Wells. ie Type_Well Is this an oversight or genuinely not needed? | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision
780 | Potable water | Vol 1 | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision
781 | Potable water | Vol 1 | Seem to be missing Chamber Diameter, for circular access chambers. (As it states that AC_Length and AC_width only to be used if chamber is non circular) | Sector Discussion | Needs some rework and clarifiation. | 2.4.1 Access Chamber | More information required for a decision
782 | Potable water | Vol 1 | Potential Attribute: Manufacturer of Fitting | Included | Already identified and will be refered to TWG. | 2.4.3 Fitting | New attribute proposed | Manufacturer
783 | Potable water | Vol 1 | Water flow direction is not absolute. I am assuming this is for a network operating under "normal" conditions. | Included | Correct. For a network operating under 'normal' conditions. | 2.4.5 Pipe | No action
784 | Potable water | Vol 1 | For clarity, perhaps include a diagram showing an irregular access chamber. Refer to page 20 in Vol 1 of the waster water meta-data standard (V1.2 DRAFT A - 14 July 2016) | Sector Discussion | Completed | 2.4.6 Pump Station | Change made document updated
785 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrectly matched. EG Serial_No => Protective Material This is carried through to the Waste Water and Storm Water manuals. | Included | Resolved in current version. | 2.5.1 Equipment | Change made document updated
786 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrect matched. | Included | Resolved in current version | 2.5.1 Equipment | Change made document updated
787 | Potable water | Vol 1 | In our AMIS we are planning to utilize two fields to describe valves. Valve Type: Eg Isolation, Scour, Toby, Pressure Reducing, etc .. Valve Mechanism: Eg Gate, Knife, Ball, Air Release, etc.. Rather than combine function and mechanism into one attribute field. | Sector Discussion | to be discussed with the TWG refer to 630, 631 | 2.5.3 Valve | More information required for a decision
788 | Potable water | Vol 1 | Where are readings recorded? Should there not be an attribute for the latest meter reading and date it was recorded. | Noted: no action required | As Constructed' data not operational data. | 2.7.1 Instruments | No action
789 | Potable water | Vol 1 | Incorrect reference: Should be 1.8 | Included | Resolved in current version. | 2.8.2 Matching to Existing Infrastructure | Change made document updated
790 | Potable water | Vol 2 | Terminology Constancy: In Vol 1, Section 1.8, a lot of the elements below are referred to as "Asset Classes" They are also referred to "Asset Classes" in the attribute and validation file format. Suggest change "Categories" to "Classes" | Noted: no action required | Standards updated to a consistent approach | Table 3: Asset Hierarchy Framework | No action
791 | Potable water | Vol 2 | I am unsure what this means. Can there be more explanation of the content in the Rules column. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
792 | Potable water | Vol 2 | What is Rule 2? Ensure on what this means. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
793 | Potable water | Vol 2 | How are these levels recorded in the date table 7? (ie Network, facility) Table 7 only links back to an individual asset level (Unique_ID) There does seem to be merit to applying Risk to a network level, sub-network level or at a facility level? Could also apply this thinking to Criticality definition? | Sector Discussion | Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance or criticality | No Specific Reference | More information required for a decision |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Close: -
794 | Potable water | Vol 1 | All three standards use this sentence correct for all 3 waters | Sector Discussion | Please provide further information. | Executive Summary | More information required for a decision
795 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.7 Heirarchy | Change made document updated
796 | Potable water | Vol 1 | Believe there should be a level between asset group and asset type (see my hierarchy tree). Also Asset Class & Asset Category is not specified in the hierarchy. | Sector Discussion | Please provide further information relating to your hierachy. | 1.7 Heirarchy | More information required for a decision
797 | Potable water | Vol 1 | Defined as Asset Type on previous page | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
798 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
799 | Potable water | Vol 1 | What information is required to determine if a tank/reservoir is a civil structure or not. i.e. How to determine if a tank/reservoir is a containment structure or a retaining structure. | Noted: no action required | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | 1.8 Theme Structure | No action
800 | Potable water | Vol 1 | Will there be reference documents for treatment plant assets? | Noted: no action required | Not at this point in time | 1.8.1 Other Asset Classes in the precinct of a Water Network | No action
801 | Potable water | Vol 1 | How would an asset that could be represented as more than one of these be represented. e.g. would a scour be a single asset (pipe) or two (pipe and fitting) or would that be up to the Client to determine | Sector Discussion | More information is required to inform a way forward | 1.9 Data Principles | More information required for a decision
802 | Potable water | Vol 1 | water | Included | changed to Water. | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
803 | Potable water | Vol 1 | water code lists | Included | Section under review. | 2.1.5 Attribute Data Fields | Change made document updated
804 | Potable water | Vol 1 | Definition etc missing | Included | Section under review. | 2.1.6 Attribute Data Type Definitions | Change made document updated
805 | Potable water | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils/contractors to use an ESRI based product, or something else? if not suggest removing ESRI from this sentence. | Noted: no action required | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for | 2.1.7 Metadata Definitions | No action
806 | Potable water | Vol 1 | Section 2.1.4 | Included | Section under review. | 2.1.7 Metadata Definitions | Change made document updated
807 | Potable water | Vol 1 | Does this code list include options for multiple networks? or is each network to be recorded as an individual project? | Included | ProjectID already included Yes it does - added multiples in Project Table | 2.1.9 Project Attributes | Change made document updated
808 | Potable water | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
809 | Potable water | Vol 1 | See note regarding Design Company above. | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
810 | Potable water | Vol 1 | Should this not be a code list? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
811 | Potable water | Vol 1 | What is the definition of cost for contractors? What is the value of capturing this when there are no controls around application of defining cost? | Included | Reviewed and Noted for Inclusion Financial code lists for ODRC, ORC and OC are included | 2.1.10 Common Attributes | haydn
812 | Potable water | Vol 1 | What exactly are the photographic references? This appears to be a 250 Char field so completely useless for using this data. Is this intended to be used in a similar way to 'Unique ID' as a reference number for the photo? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
813 | Potable water | Vol 1 | Again using a 250 character field means the data could be all over the place. Example uses this field to record specific instructions to access the asset. To me that should be a separately labelled field. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
814 | Potable water | Vol 1 | See note regarding this field on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
815 | Potable water | Vol 1 | See not for Design Company on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
816 | Potable water | Vol 1 | Would a T not be a fitting instead of a node? | Noted: no action required | T is a fitting but also an intersection so therefore a node. | 2.4.4 Node | No action
817 | Potable water | Vol 1 | Is there a particular reason that Valves etc do not 'break' pipes? When works are undertaken (renewals in particular) actual physical assets provide useful 'real world' demarcation points. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | 2.4.5 Pipe | No action
818 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram
819 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram
820 | Potable water | Vol 1 | What are the reasons for Internal Diameter, Nominal Diameter and Nominal Bore all being required? Are these all not essentially the same thing? | Sector Discussion | The range of diameter types are an analytical requirement for interogating assets through a range of lenses | 2.4.5 Pipe | More information required for a decision
821 | Potable water | Vol 1 | Would this class also cover assets that provide access but are not part of a dam or weir wall? Suggest that this be added to the wastewater specification as well. | Included | Agreed 9/3/2017 | 2.3.6 Tunnel | Comment clarifed in potable water document and tunnel asset class added to wastewater document
822 | Potable water | Vol 1 | Should purchase date be included? Do some warranties apply from date of purchase? | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision
823 | Potable water | Vol 2 | a' instead of 'the' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
824 | Potable water | Vol 2 | Why is infrastructure for collection and treatment not covered? These assets are integral to potable water supply and asset managers need quality information that they can use to make asset management decisions. Sentence also contradicts itself. "does not cover infrastructure...treatment of water, except in the case of..infrastructure to treat water". | Noted: no action required | There is a desire to create anoter standard which includes these assets, as there is in th ebuilding environment for Large Commercial Buildings and Industrial Buildings | No Specific Reference | No action
825 | Potable water | Vol 2 | Pressure is more of a Quality provision. Suggest moving this into Quality. | Noted: no action required | Pressure is a Design Attribute How it performs against that design is a Design Performance attribute | No Specific Reference | No action
826 | Potable water | Vol 2 | Delete extra "that" | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
827 | Potable water | Vol 2 | outlines' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
828 | Potable water | Vol 2 | investment' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
829 | Potable water | Vol 2 | replace' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
830 | Potable water | Vol 2 | Influences | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
831 | Potable water | Vol 2 | Replication | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
832 | Potable water | Vol 2 | General comment - risk and criticality are closely linked. Are they really different things? Just use one term and get rid of the other. | Noted: no action required | No action required. Decision to separate two schemas taken at project management level | No Specific Reference | No action
833 | Potable water | Vol 2 | Table is missing a 'comments' field | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
834 | Potable water | Vol 2 | Inconsistent with the wastewater and stormwater measure headings (Rating). Suggest same terminology is used across all three waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
835 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
836 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would" more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
837 | Potable water | Vol 2 | Is this a different manual than the 3rd Edition New Zealand Pipe Inspection Manual? If not use full document name as used in the wastewater and stormwater documents. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
838 | Potable water | Vol 2 | Should this not be in line with the wastewater and stormwater measures? (IIMM 2015) | Noted: no action required | No action required. This is the same document | No Specific Reference | No action
839 | Potable water | Vol 2 | If this information is to be completed by field (maintenance and operations) staff they are unlikely to know if works have been deferred or will be deferred. | Noted: no action required | Not an attribute of these standards | No Specific Reference | No action
840 | Potable water | Vol 2 | Replace "data" with "cost" | Included | Documents have undergone a full publishing edit | Haydn | No action
841 | Potable water | Vol 2 | Stormwater document includes complete code lists for these items. Water and wastewater do not. | Noted: no action required | Code lists updated | List of Code Lists | No action
842 | Potable water | Vol 2 | Not convinced that this is a useful or practical schema, at least for potable water assets. Perhaps don't bother with this and just use demand schema instead? They are similar. | Noted: no action required | Utilisation and Demand are different decision elements as explained in the standards. | 3.2 Utilisation Schema 3.3 Demand Schema | No action
843 | Potable water | Vol 2 | Missing sentence from WW and SW Volume two further explaining the utilisation schema. " Utilisation is measured using time or other base unit measured against a known availability." | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
844 | Potable water | Vol 2 | "Current Utilisation" at an asset by asset level would require an impractical amount of monitoring. i.e. are we really going to know average and peak flows through each and every length of water pipe? | Included | This is an analytical construct, and easily monitored in an analytical sense at whatever frequency required for intervention circumstances | 3.2 Utilisation Schema | An explanation of Data Science will be provided for at the Technical Working Groups
845 | Potable water | Vol 2 | Partly a function of the pressure in the pipe. Are we really going to know potential utilisation for each and every length of water pipe? | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
846 | Potable water | Vol 2 | Don't think it's possible to determine this for each and every asset. At least for potable water assets. | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
847 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets without extensive modelling. Alternatively would require data from modelling software. | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
848 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
849 | Potable water | Vol 2 | This does not seem to be an relevant measure for water demand in a metropolitan situation. | Included | Completed - see Demand section | 3.3 Demand Schema | No action
850 | Potable water | Vol 2 | Criticality varies across all three waters. While a data centre may have a higher water criticality than a hospital, the opposite would be true of wastewater. | Included | Correct, which is why each asst class is treated differently when an analysis of things like criticality are conducted across a network | No Specific Reference | No action
851 | Potable water | Vol 2 | Of risk & criticality, which are both similar schema, criticality is much quicker and easier to measure and much less subjective. I would be tempted to exclude risk or use it with caution in decision-making compared the use of other schema. | Noted: no action required | It will be required n some circumstances, and here it is defined when you do | No Specific Reference | No action
852 | Potable water | Vol 2 | Ln only needs to be 1 due to 1,5 rule | Included | Completed | No Specific Reference | No action
853 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
854 | Potable water | Vol 2 | Even at a score of 3 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
855 | Potable water | Vol 2 | Even at a score of 3 is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
856 | Potable water | Vol 2 | Even at a score of 4 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
857 | Potable water | Vol 2 | Not convinced there is much use in this table, at least for water assets. Most revenue is derived from consumption so would be associated with a meter and the usage of water. | Noted: no action required | No action required. Organisation can choose how revenue is recorded against an asset | No Specific Reference | No action
858 | Potable water | Vol 2 | So this is theoretical revenue? Not actual revenue? | Included | Actual, Forecast and Budget included in financial code lists | Code List 6: Bases of Cost | No action
859 | Potable water | Vol 2 | Delete this text. Captured in the field below. | Included | Completd | No Specific Reference | No action
860 | Potable water | Vol 2 | This whole section is confusing. It's trying to do two things at once. Individual asset attributes and whole of network attributes should be separated out. | Included | Network analytics are completed on individual asset analytical interogations | No Specific Reference | No action
861 | Potable water | Vol 2 | So its not intended to be used for decisions at an individual asset level? If not, strip out all the individual asset measures and move somewhere else. | Included | It is in some circumstances to be used on an individual assetID | No Specific Reference | No action
862 | Potable water | Vol 2 | This table seems to be a jumble of attributes for individual assets and DIA measures which are taken for the network / organisation as a whole. I'm not really sure the whole of network / organisation attributes are metadata. Delete DIA whole of network / organisation attributes or move to a separate table. dlane: Some data items are network wide while others are asset specific. If data capture is required these should be split into separate network and asset tables. | Included | Volume 2 is completed in these draft standards. Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance | No Specific Reference | No action
863 | Potable water | Vol 2 | How does this field work? Is it the duration of the most recent unplanned interruption, the the total duration of all unplanned interruptions (from field below) or the average unplanned interruption duration? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
864 | Potable water | Vol 2 | How does this field work? Is it the connections affected in the most recent unplanned interruption, the total connections affected in all unplanned interruptions (from field below) or the average number of connections affected in unplanned an unplanned interruption? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
865 | Potable water | Vol 2 | Delete this field. It makes no sense and is confusing. Field Ref 11.04 does the job. | Included | Table updated | No Specific Reference | Change made document updated
866 | Potable water | Vol 2 | Need to include the units of measure. kPa,psi etc | Included | Tables updated in code lists of Vol 2 | Code List 44: Description of Design Performance – Engineering Unit of Measure | psi to be added
867 | Potable water | Vol 2 | Surely this field would only be used for a reservoir asset. Not, say, a pipe supplied from the reservoir. Please clarify the use of this field. | Included | It can be both | No Specific Reference | No action
868 | Potable water | Vol 2 | Not sure it would come from Repairs and Maintenance Schema. | Noted: no action required | This MoH included in the Service Performance Attributes | Data Table 11: Service Performance Attributes – Functional | No action
869 | Potable water | Vol 2 | Confusing to have it on this table. So this field is used at a facility level not an individual asset level? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
870 | Potable water | Vol 2 | Confusing to have it in this table. So this field is used at an organisation level? The question of whether there is an adequate backflow prevention programme doesn't relate to individual assets? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
871 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
872 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
873 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
874 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
875 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
876 | Potable water | Vol 2 | This is not a demand attribute, its abstraction/take and is source based. as you've said that this is potable water assets only I don't think it's appropriate here. | Noted: no action required | A source is an asset (e.g. a reservoir), abstraction is the process, demand is the level of abstratcion on the asset - each are different and can apply to a pipe connection no less (e.g. a school) | No Specific Reference | No action
877 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
878 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
879 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated?. | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
880 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. Move to financial schema? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
881 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
882 | Potable water | Vol 2 | Differs from tables in the stormwater and wastewater specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Tables are very similar, with the asset specific elements being applied when required. Tables have been normalised where possible | No Specific Reference | No action
883 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
884 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
885 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
886 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
887 | Stormwater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Included | Reviewed and Noted for Inclusion | 2.1.7 Metadata Definitions | Change made document updated
888 | Stormwater | Vol 1 | 2.1.4 | Included | Reviewed and Noted for Inclusion | 2.1.6 Attribute Data Types Definitions 2.1.7 Metadata Definitions | Change made document updated
889 | Stormwater | Vol 1 | Does this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Noted: no action required | Either | 2.1.9 Project Attributes | No action
890 | Stormwater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
891 | Stormwater | Vol 1 | See note regarding Design Company above. | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
892 | Stormwater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
893 | Stormwater | Vol 2 | Heading (see water and wastewater) | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
894 | Stormwater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or at code should be a single character as per the water measures. Should be consistent across all 3 waters | Included | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
895 | Stormwater | Vol 2 | Differs from table in wastewater and water specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
896 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
897 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
898 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.8 Theme Structure | Change made document updated
899 | Wastewater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Noted: no action required | Not the intention. The intention is to outline why the field is structured in this way | 2.1.7 Metadata Definitions | No action
900 | Wastewater | Vol 1 | 2.1.4 | Included | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | 2.1.7 Metadata Definitions | Change made document updated
901 | Wastewater | Vol 1 | Doe this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Sector Discussion | This is an operational question related to an organisations ability to import data into their asset management systems. For immature organisations likely to be project by project, for mature ones project agnostics | 2.1.9 Project Attributes | More information required for a decision
902 | Wastewater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
903 | Wastewater | Vol 1 | See note regarding Design Company above. | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
904 | Wastewater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
905 | Wastewater | Vol 2 | Not a valid measure for wastewater utilisation. | Included | Updated | No Specific Reference | No action
906 | Wastewater | Vol 2 | Criticality varies across all three waters. for example, for wastewater a hospital would have a higher value than a data centre. while water could score differently | Noted: no action required | No action required, based on the importance of the building as defined in the Buildings standard | Code List 13: Facility Importance Rating
907 | Wastewater | Vol 2 | Heading is different from that used in water and stormwater documents. Suggest standardising for simplicity. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
908 | Wastewater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or code should be a single character as per the water measures. should be consistent across all 3 waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
909 | Wastewater | Vol 2 | Differs from tables in the stormwater and wastewater spec. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
910 | 3-Waters & Buildings | Vol 1 & Vol 2 | An obvious mistake in the Potable Water Metadata Std is that someone has put the Residential Executive Summary in it????. | Included | Included in the draft Standards | Executive Summary | Change made document updated
911 | 3-Waters & Buildings | Vol 1 & Vol 2 | You are asking for public to comment on missing attributes within meta data tables. Considering you have spent 12500 hours on this, could you please comment if all the attributes defined by Australian standard ADAC have been included? http://engicom.com.au/adac/government-organisations I appreciate your list of assets may be more comprehensive. If any of the asset attributes defined in ADAC are missing there are like to be areas where assets will miss vital information for future analysis. If you have used IPWEA in your decision making process it would be useful to include this information on your website so it doesn’t look like you are reinventing the wheel. Well done on sorting out the asset management data through the lifecycle of each asset. Local councils desperately need national standard for asset capture, storage and access to information. | Included | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. | General | No action
912 | 3-Waters & Buildings | Vol 1 & Vol 2 | I’d like to provide feedback on the proposed standard. However I caveat this as coming from a hands on GIS Practitioner View, which may be different to my colleagues here at LINZ. I think it will be incredibly important to incorporate good practice guidance at some stage on how these standards are practically implemented. Ideally providing an empty or working dataset that a person can take, open with their system and populate. Generally when you go to create the schema in a system you’ll follow it and interpret changing the types, field lengths, column names etc. My request is based on recent experience. Often this step is left out, and implementation of the standard fails. This was my experience with the ANZLIC geospatial metadata standard, 10 years after its release 95% of GIS practitioners in New Zealand could still not easily implement the standard within the most common desktop GIS software. The Australian based tool provided did not support NZ requirements. We ended up shoving the required text into a single desc field in an inappropriate manner, ending up with a total mess. This may require getting software providers onboard with adding these into their pre-defined templates for users of the most common software providers. If you could imagine in the same way we create a LINZ letterhead letter in MS Word. My 2 cents from a GIS data capture perspective and I am happy to discuss this further if appropriate, otherwise happy to leave it as this. | Noted: no action required | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | N/A | No action
913 | 3-Waters & Buildings | Vol 1 & Vol 2 | In each of these documents out for proposal, there is reference to standard codes for things like asset type and material (“the CODELIST”), but none of these are available yet – will this be available before consultation closes? | Included | Code lists are included Attributes to be discussed | General | Gauge input from next review
914 | 3-Waters & Buildings | Vol 1 & Vol 2 | This is a great initiative and will aid everybody involved in the area of Asset Management. I would ask is has there been any coordination with the Institute of Public Works Engineering Australasia as they have a system already in place called ADAC (http://www.engicom.com.au/adac). Could your framework be an extension to that so we can leverage what software companies have developed already to support that schema. It appears that a lot of the info you are capturing has already been covered, why reinvent the wheel? | Noted: no action required | IPEWA Australisia has representation around the table, and has had for 2 years | N/A | No action
915 | 3-Waters & Buildings | Vol 1 & Vol 2 | Structure of the standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes. Further to the split of water sectors there is an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group has specified that a single document that focusses on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. In terms of usability our end users are expecting a data framework that is easy to understand and use. In the proposed layout we are expecting the standards will be met with cost burdens. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
916 | 3-Waters & Buildings | Vol 1 & Vol 2 | 2. Applicability of volumes 1 and 2 The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was about creating an as-built data set for industry that can be used to collect field data, most of the workshops evolved around this input. Volume 2 for derived data has had limited industry input and we do not believe it is ready to be published. Further work on this volume is therefore required. | Noted: no action required | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. | General | No action
917 | 3-Waters & Buildings | Vol 1 & Vol 2 | 3. Data hierarchy The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. As presented at the workshops, an example of how this could be applied to the tables is outlined below: Level 0 (system/layout specific data – master data. Typically assigned by organisational systems and numbering or coding rules - contains the common data set) -Inventory identification number / -Functional location i.e. Network type (water, wastewater, stormwater) / -etc. Level 1: Data categories, in example: “Technical/physical” i.e. Containment structures (available technical core classes) (or) Operational data (or) Financial data etc. Level 2: (attributes) Minimum required attributes, in example: -Function / -Depth / -Material / -etc. Level 3: (attributes) Conditional attributes, in example: -Diameter if circular / -length and width if not circular / -Joint type (if the structure has joints) / -etc. Level 4: (attributes) Optional attributes, in example: -Manufacturer / -Model/part number / -etc. | Included | Asset Classifications have been defined in the Standards Tables are to be discussed at length | No Specific Reference | Sector discussion
918 | 3-Waters & Buildings | Vol 1 & Vol 2 | 4. Terminologies and definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need to be agreed. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
919 | 3-Waters & Buildings | Vol 1 & Vol 2 | 5. Graphical representation and its accuracy This subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. Graphical representation should be removed from the document; the purpose of this standard is collecting metadata of asset physical properties. Geospatial requirements are a standard in its own right and even providing these as guidelines does not seem appropriate. | Included | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH | General | No action
920 | 3-Waters & Buildings | Vol 1 & Vol 2 | 6. General content 1.“Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. 2. The units of measure have not been covered during the workshops. Further input may be required before the draft is ready for public release. 3. Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and the implementation may not be practical. 4. Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. In many instances data will be collected in-house. 5. Australian examples and photos should be replaced by New Zealand examples. Word choice such as “savvy” (used often) is not the best choice. Some of the language used needs to be reviewed in order to retain the standard’s professionalism. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included | General | No action
921 | 3-Waters & Buildings | Vol 1 & Vol 2 | 7. Implementation The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate has not been considered where organisations may choose not to collect certain information for low risk assets. An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard | Noted: no action required | This is not within the scope of these standards | N/A | No action
922 | 3-Waters & Buildings | Vol 1 & Vol 2 | We believe there is a reasonable amount of work that has not been completed, such as standard definitions, which may lead to inconsistencies between the water organisations. Without this work being completed the documentation that has been produced could only be used as a guideline or a code of practice. | Noted: no action required | All definitions have been standardised and normalised | No Specific Reference | No action
923 | 3-Waters | Vol 1 & Vol 2 | However, page 141 of Potable Water Volume 1 As-constructed/As-built references code lists for 3 waters assets that can be reviewed in a supplementary document called 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016 Is this document available for download or can it be emailed to me? I would like to cross-check what is in this code list against the attribute tables to assist with my review. | Included | Code lists are included | General | Change made document updated
924 | 3-Waters | Vol 1 & Vol 2 | As-constructed schema should not be a separate document, and should recognize that many assets are created though term contracts not just greenfield build. We should not separate “as-constructed” from other elements of the standard because this perpetuates last century’s practice of asset management being about the asset whereas it is about the service enabled by the asset. We should modify the “as-constructed” schema to recognise that construction happens both in new builds and in renewal term contracts and the information should support both efficiently. I am not convinced of the value of separating the standards into two parts. While as constructed data is central to an asset information system there are few transactions that use it in practice. Most construction projects will use subsets of the inventory tables, performance based construction projects will also use the condition and performance tables, term PPP or BOOT contracts will use almost the entire standard. This means there is no one to one connection between projects and elements of the entire data schemas so the split of the source documents is artificial. I think there is a serious downside to separating the two documents that drives us towards a combined view. Asset management is all about delivering services that require significant assets. Separating as-constructed from performance data perpetuates past practice that asset management was about having assets in good condition, whereas it is about having assets in sufficient condition to deliver targeted services. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
925 | 3-Waters | Vol 1 & Vol 2 | Another challenge with this proposed separation and the associated “constructor” reference fields is that for roads and 3 waters, though to a lesser extent buildings, much infrastructure is created through renewal or replacement programmes. For example for State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. This means that we need to think seriously about replacing the “constructor” record in the “as-constructed” table with a reference to an “Asset Intervention” record as described elsewhere in my comments. Unless this is done there will be not be normalisation of records relating responsibility for modification of inventory, a ridiculous amount of duplicate records created from term contracts where much inventory is created, and a mismatch between the constructor records in the “as-constructed” schema and those of the maintenance schema, when in term network management contracts these are the same constructor. The same duplication will occur when the same constructor creates many inventory records as occurs in term contracts | Noted: no action required | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | No Specific Reference | No action
926 | 3-Waters | Vol 1 & Vol 2 | The categories of data type should be simple, exhaustive and mutually exclusive so should vulnerability and resilience stand alone? The proposed “global meta data schemata” classifies data into several categories. This is a necessary and good thing because it help users appreciate the scope of the data and find the elements they may be interested in. To do this well the elements must be simple, described in commonly understood language, cover the field of interest, i.e. be exhaustive, and be mutually exclusive, i.e. not have definitions that overlap or require subtle nuancing. | Included | Included in the draft Standards | General | No action
927 | 3-Waters | Vol 1 & Vol 2 | Vulnerability - risk There is an open question in the document as to whether vulnerability should be drawn out as a standalone data category, when it influences risk. I do not think it should be standalone because this then makes “risk” become “risk other than vulnerability” and I think that is a bit silly. I certainly agree that vulnerability is important. I think it so important that we should draw it out in the risk or resilience categories. The high level approach to risk is to consider likelihood and consequence. Simplistically consequence conflates: • vulnerability of service, and • impact from reduction or loss of service and vulnerability of service conflates: • vulnerability of infrastructure (considering network effects), and • availability of alternate infrastructure or alternate services. I think we should draw out these or similar elements of risk for those elements of infrastructure type that potentially have a consequence greater than tolerable. This might mean (in the transport context) arterials and above in a transport world because of their importance to the economy and society. Effectively this creates a level of service gap around vulnerability, the very gap that rental companies advertise as being closed when they proclaim on their hoardings that a building to let is 85% EQ code compliant. | Included | Included in the draft Standards | 4.2 Vulnerability Schema | No action
928 | 3-Waters | Vol 1 & Vol 2 | Resilience - performance Resilience is a service level, or a strategic goal. As a service level it should be within the performance elements of the data standard. I know that it has prominence because it is an important element of performance, but so too are accessibility and safety for transport, or availability of supply or health for water. As a strategic goal it is a driver of service levels. | Included | Resilience is a state and requires measurement The level of service is subject to the level of service any organisation seeks to apply, and an invetment plan to meet that level | 4.5 Resilience Schema | No action
929 | 3-Waters | Vol 1 & Vol 2 | Utilisation is multifaceted and requires enhancement The definition of utilisation given in the draft standard is the proportion of an assets available capacity that is actually being used. I think that there will need to be some clever messaging to ensure that the unit of capacity chosen is understood for infrastructure in different circumstances. Using a transport example provides an illustration of this. Over 60% of New Zealand’s roads are classified as access or low volume access roads. This means that they have less than 1000 vehicles using them per day. A single lane has a capacity of about 1400 vehicles per hour, depending on its configuration, i.e. on the proposed definition of capacity most roads have a daily utilisation of about 1.5% yet these roads represent the last and/or first mile of most trips and so are critical to our economy and society. The level of utilisation will always be low simply because there are rural and urban areas with low population that are connected to market or work place. Even with planned intensification of central urban areas daily utilisation might only rise to 5%. This is analogous to the smallest element of supply or removal for potable or waste water. Also, where there is suppressed demand because demand exceeds supply, e.g. on congested transport networks (whether roads or busses), we may report 100% utilisation, but that is bad because the potential benefit of suppressed trips is being lost or costing more. In a water example we may constrain the development of business when supply is inadequate for development yet fully used by current development. Together these factors mean that we have to be careful about the utilisation measure and how we use it alongside other measures at a local and network level, a simplistic approach won’t do. I think this section of the draft standard needs work to draw out these issues. In addition we need to consider how utilisation and performance metrics are used to optimise asset investment decisions. | Noted: no action required | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | No Specific Reference | No action
930 | 3-Waters | Vol 1 & Vol 2 | Inventory Interventions At the moment there are two types of works records, those recorded as maintenance and those associated with the as-constructed fields. I think we should consider what we want from the recording of “works” or inventory interventions because I expect that will lead to an improved data structure with one form of works interventions record. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
931 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Planned, current, completed or abandoned works so we can fuel the nationwide forward and current works viewer enabling better coordination of works and reduced disruption of customers whether the works are construction, renewal or maintenance. Interventions on inventory are a process that creates or modifies inventory. Much information is required about the process as much as of the fact that it creates inventory. E.g. the forward works viewer being developed to display proposed and current works have time, duration, and place elements of information as well as descriptive information about the constructor and infrastructure being modified or created as reflected in the proposed “as-constructed” schema. | Included | Statement noted. Already done in Repairs and Maintenance schema. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
932 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Responsibility for management of infrastructure, noting that ownership may pass to a client when inventory enters service, but responsibility for maintenance may extend beyond the transfer date | Noted: no action required | Noted | No Specific Reference | No action
933 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • A hierarchy of works and tasks that distinguish a term contract (or work) from a work task within it so that the work identifies responsibility, type of work, stage of work etc, and the task the date and type of work done linked to the infrastructure impacted. I think this allows better alignment with supplier’s management systems, responsibility for work done, and supports many forms of contract from term based contracts to single task contracts. This also enables security to be built into system for data exchange. This is important because for most infrastructure networks (buildings aside) most new infrastructure arises due to renewal works and not due to greenfield construction. | Included | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
934 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
935 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
936 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Types of inventory intervention with appropriate records, including, but not limited to: o Physical works, probably the most common type o Waste or abandonment, associated with infrastructure being removed from the inventory and reflected in a valuation as a write-off o Inventory received from third parties, e.g. as a result of transfer from development of a new residential area to a council, or the transfer of responsibility of a road from a local authority to the Transport Agency as a State highway o Inventory transferred to third parties, e.g. the transfer of responsibility of a previous State highway to a local authority on completion of a State highway bypass. I acknowledge that “inventory interventions” is not the best term and that a better one should be found. | Included | Included in the draft Standards | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
937 | 3-Waters | Vol 1 & Vol 2 | Assessments There is an opportunity to introduce a concept of an intervention type of “Assessment”. This arises because there are many instances where responsibility for some parameter in many of the tables is explicitly referenced, yet is essentially the same information in each case. This information is who changed the parameter, when, why, as a result of what process…? This proposed approach will enable normalisation of data describing the assessment of condition or performance (whether current or forecast), valuation, risk or any other metric in a standard way. It will then identify the provenance and responsibility for each. This proposal is much the same as that for “inventory interventions” in that it suggests that the core information is about the process leading to the metric in the data and this should be recognised. | Noted: no action required | Assesments are (or interventions) are subject to the element being interrogated (e.g. condition). The standards have attributes which capture these. These will however be predominantly the focus of the work when develop-ing Volume 3 | Data Table 1: Condition Attributes & Code List 17: Condition Rating – Methodology | No action
938 | 3-Waters | Vol 1 & Vol 2 | Supply of as constructed data I think that we shouldn’t mandate the form for the supply of as constructed (or other data) but rather the relevant metadata describing its provenance, quality etc. If the form is mandated then it would require an absurd level of record keeping and compliance from term contractors who create many new assets. E.g. for State highways we use term contractors who create the vast majority of new surface infrastructure each year. For State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. Suitably qualified and quality assured staff from contractors enter the as-constructed data directly into our inventory system, and this isn’t shown as an acceptable method of delivery yet it patently is. One of the purported benefits of meta-data standards is that it enables business to business transfer of data. Defining the transfer of data on a disc seems to fly in the face of these benefits and the advance of B2B technology. Similarly I would think that NIU doesn’t want to be involved in contractual requirements for each form of contract, rather whether information is being managed well and is fit for purpose. I think the supply of data section starting on page 1 of volume 1 needs review. | Noted: no action required | Data format (form here) is not within the scope of these standards | General | No action
939 | 3-Waters | Vol 1 & Vol 2 | Asset management I think the sections of the standard on asset management need a revision to better reflect: 1. That customer service at least long term cost is the goal, and not maintenance of asset condition, noting that the two are related. 2. Investment decisions made in a customer service centric world. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
940 | 3-Waters | Vol 1 & Vol 2 | Customer service focus The various diagrams, for example figure 3 on page 24 of volume 2 is written in very economic language around the return for investment of public funds. This is of course critical, but loses the narrative that relates providing customer service that is economic. | Noted: no action required | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. | No Specific Reference | No action
941 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: I think the steps in the above referenced diagram, and the description on the preceding pages are missing an element and that is what is being targeted in terms of service levels and how this target is established. Or alternatively (as a poor second best) are missing the inputs describing the economic and social benefits of different service levels experienced by customers. If these were present then the analytics could do the required work. This step is required to establish the performance targets referenced in the performance elements of the standard. Eg what is the optimal economic service level for service outages considering investment to reduce the frequency, duration and impact of service outages against the social and economic impacts of these. This step is difficult and complex but needed none the less. It requires decisions about the relative weight to be given to quasi commercial models or economic models. It requires significant analytics to be undertaken to determine the relationships between costs and benefits of different levels of service for different types of customers in different circumstances. Much of these analytics are represented in the economic evaluation manual used to determine the economic value of transport proposals in New Zealand. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | No action
942 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: The service led approach enables a more informed discussion with customers about expectations of service level and the cost of these than a black box economic model. It essentially proposes a three stage approach: (See figure in word document) This recognizes that information is never perfect to enable ideal one off analytics because customers’ needs, systems and contexts change so what might be optimum now likely won’t be at another time. The aspect of service level target should be reflected in the analytics framework. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. | No Specific Reference | No action
943 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world I think that section 1.8 needs some rework though many aspects are worth keeping. There is significant reliance on the metaphor that as assets deteriorate and consequently the maintenance expense to sustain targeted service levels increases there is a sweet spot between condition and maintenance cost. I think we need to recast that metaphor in a customer centric world and recognize that the sweet spot is tautological because the definition used for condition grade 5 is that it has failed or soon will so it is no coincidence that replacement is needed there. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
944 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world The proposed standard presents a theoretical approach to stochastic analysis. This style of analysis is becoming common place. The standard might reference the UK’s Highways Efficiency Maintenance Programme website, especially this url: http://www.highwaysefficiency.org.uk/efficiency-resources/asset-management/life-cycling-planning-toolkit.html That site includes standard tools for “stochastic analysis” of renewal programmes using the “5-step condition rating”. While the text is all about roads the processes are generic. With translation, or a babel fish (as Douglass Adams might say) they are as applicable to buildings as to roads. The tools on that site are of course single factor analyses as condition based analytics generally are. There is no single or multifactor customer service optimisation (e.g. skid resistance and ride comfort for roads) that assists planning in a constrained environment or in an environment where value for money matters, but it is a straight forward approach to estimating the works required to sustain performance. That reference, or a more applicable one, or a derivative of it, would go some way to making the theoretical text in the proposed standard tangible. | Noted: no action required | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
945 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If the text were recast to be more customer service centric it might use the following approach. The two most important decisions to intervene with some form of monitoring or works when managing a network to provide customer service are: 1. When delivered service levels have or will drop below the targeted level or there is too great a risk that they will 2. When, despite the targeted service level being met, it is cheaper in the long run to intervene, or there is an unacceptable risk that costs will rise unless an intervention is made Intervention decisions can initially lead to a monitor, maintenance, renewal or improvement interventions, whichever is part of the least long term cost intervention strategy. A more colloquial way of putting this is only intervene if its broken, or cheaper in the long run. | Noted: no action required | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
946 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world Transport examples of the two decision types are: Ensuring the service is delivered to target. • Replacing the tires on your car when the tread depth has reduced and become unsafe, or ahead of winter when risk is greatest when tread depth has almost become unsafe • Continuing to monitor the change in direction of a river beside a roadway that may ultimately risk scouring of the road formation in order that preventive works can be taken when necessary and most cost effectively to preserve the transport route • Water cutting the excess bitumen off a road to restore the prominence of the chips so tyres grip these rather than “float” on the water film when the road is wet in order to restore the skid resistance of the road surface. • Resurfacing a road when the skid resistance of a road is falling and is either unsafe or will become unsafe before the next opportunity to intervene because the stones have polished Ensuring that delivery of the service is at the least possible long term cost. • Replacing the oil in your car engine even though it is performing well in order to forestall engine damage • Monitoring the condition and maintenance expenditure on deteriorating roads so that and expected renewal works can be designed and timed to be cost effective long term • Sealing cracks in an asphaltic concrete road surface to reduce water ingress to the pavement which would cause the pavement to deteriorate rapidly and require more expensive repairs • Rebuilding or replacing the structural layers in a pavement when this is the cheapest long term cost because deterioration in pavement strength is leading to the need for significant and increasingly frequent and costly repairs and resurfacing treatments to maintain service levels | Noted: no action required | And, is the intention of the analytical foundations set down for Volume 4. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
947 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If discussion of the type inferred in the above table were included then the standard would be more tangible to users and better focussed on customer service, the goal of asset management. I think it worth the discussion including reference to or guidance on the economic decision to continue to maintain infrastructure or to renew or replace it on a site specific basis. The IIMM might be suitably referenced. When funds can be used on other investments outside asset management of the infrastructure in question then we look for the sweet spot where the net present value of the renewal plus reduced subsequent maintenance stream is better than the present value of the continued and increasingly expensive maintenance stream. This should be included because it can be implemented site by site for significant investment, and needn’t rely on sophisticated network level analytics and data, though it requires some to describe the relationship between condition, time and maintenance cost. This analysis that maintenance costs typically increase as condition worsens is shown in the following indicative diagram as indicated in the draft standard metaphorical diagrams. This shows there isn’t a sweet spot from this relationship alone. Another factor is required for optimisation and that is the present value of the replacement cost option on a site specific basis, or long term budget on a network basis. (see figures in word document) | Noted: no action required | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
948 | 3-Waters | Vol 1 & Vol 2 | Global Schemata The global asset metadata schemata diagram on page 16 of volume 2 appears out of place with the prosaic listing of detailed data requirements. If it were fully developed as an idea in the text you would expect it to tell a story about why certain data elements are required. No such story is conveyed, so the inference is that whatever data is in the standard will enable such analysis, if that were true then the benefit of the advanced analytics would be small. That seems odd. Does this description add value? | Noted: no action required | The diagram provides context for the detail that follows There are some who are already applying this level of complexity to decision-making. | 1.4 Context of Asset Data and Analytics | No action
949 | 3-Waters | Vol 1 & Vol 2 | Network level performance targets The standard for service performance p101 vol 2 as proposed enables the measurement of performance against a target. This is good. However there is no reference to what good looks like so the measurements are just that. It may be useful to add records that: • Enables the categorisation of target service levels • Set service targets for each performance aspect for each category This would provide the data required to enable reporting of whether the service provided was good enough or not, in a situation where targets differ by category. The One Network Road Classification framework developed by REG for transport classifies roads into 8 categories and sets targets for each. | Noted: no action required | Levels of service are policy decisions, and are not within the scope of these standards However, where organisatoins provide these levels, these standards will attribute them and analyse them for decision-making purposes | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
950 | 3-Waters | Vol 1 & Vol 2 | Financial Performance The standard has sections on p88 vol2 and succeeding pages. It would be beneficial to review common good practice to understand what data elements should be here. The Australian Infrastructure Financial Management Guide is one such reference. Here as elsewhere the tables can be normalised by reference to an assessment record as proposed above, the type here being valuation. In addition I would have thought there would be considerable opportunity to normalise valuation approaches by assigning each asset a valuation type, and that type record containing the depreciation rates etc. applicable to it. I am not sure that the valuation section has been fully developed yet because some thought must be given to valuation components being different to asset register components. There is no need for them to be the same as they have different drivers. This sections contains data about construction cost that will be transferred to the “as constructed” tables. It asks that the cost of an asset be supplied and that supply is mandatory. However there is a challenge with this because almost all construction contacts cost elements at a higher level of aggregation than each asset. E.g.the construction of a sewage treatment plant does not lead to an estimated cost per inventory item created. Contracts with lump sum maintenance items likewise have no costs per maintenance work task. Therefore a review is required of how costs are acquired and stored and at what level. I suspect that it will be best to capture financial information at the financial/contractual transaction level and activity at the inventory affected level. The concept proposed above for having transactional records for works and tasks enables costs to be collected at that level. | Noted: no action required | There is an opportuity to reflect on the tables and code lists provided in the standards. There are some analytical assumptions being addressed here, which are for the analytics in which will be unpacked in more detail in Volume 4. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
951 | 3-Waters | Vol 1 & Vol 2 | Information required to manage well varies by criticality of network and context I expect that, as with roads, the information needs of managing a water network in a simple undemanding context differ from those of a demanding context. While the performance metrics around health and availability may be common the needs for sophisticated infrastructure and condition metrics would differ. Similarly the information needs for the critical elements in a complex network would be greater than for other elements. This would lead to a hierarchy of mandatory fields based on context. I think this should be considered. | Sector Discussion | To discuss | 5.4 Service Performance Schema | No action |  | closed | Discussed during the May 1-3 workshops Noted no further discussion or action required |  | Close: -
952 | 3-Waters | Vol 1 | pg 3: Validating the data submission: is this to go against each asset or an organisational process requirement? | Included | Against each asset and against each attribute | General | No action
953 | 3-Waters | Vol 1 | 1.8 They are requesting that “each asset type must be delivered on a separate level/layer and the files must be clearly labelled…” If this is in a CAD format this makes perfect sense, but then the attribute information that is being requesting won’t be able to put against the individual asset (when last I tried this, it can only be done with blocks, and blocks can be tricky to convert to a shape file). But if in a shape file format, it is a bit of an overkill, it is structuring back to the way we used to have it. And we will need to combine the information in order to import into Assetfinda. it is also implying that information from contractors will be to a High enough standard that we can suck it into our GIS and all points and lines will meet perfectly. In a perfect world that would be great, but from having a draughing background. I can guarantee you are going to get hydrants, valves etc. not matching perfectly with your pipes (this comes from the skill of the person doing the as built) and greater maintenance issues later. We would be relying on the project managers to insist on high quality as built. This then brings up the issue of disposals of existing infrastructure. Or the assigning of asset id numbers that have intelligence. | Noted: no action required | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | 1.8 Theme Structure | No action
954 | 3-Waters | Vol 1 | 1.11 Projects will need to be on board with this. | Noted: no action required | Noted, but out of scope. | 1.11 Acceptance Testing | No action
955 | 3-Waters | Vol 1 | 2.1.1 Precision needs to be clarified on what is acceptable. | Included | Precision is defined in the standards | 2.1.1 Accuracy Requirements for Locating Assets | No action
956 | 3-Waters | Vol 1 | 2.1.5 In the proposed structure, the data Code list fields will be limited to 10 characters, this is not going to allow us to use unabbreviated materials e.g.: uPVC instead of PVC Unplasticised. We need to decide on this now as it affects the look up tables and associated finance. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the Full Name once the asset data is provided. | 2.1.5 Attribute Data Fields | No action
957 | 3-Waters | Vol 1 | 2.1.8 The attribute fields they are suggesting may impact on Assetfinda fields e.g.: they are the same but have different criteria. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
958 | 3-Waters | Vol 1 | 2.4.1 For Access chamber of valves they are requesting one location point, which is what we have and one polygon of the same area representing a plan view of the valve pit. We have over 2000 valves, that is a lot of additional files, and I feel a duplication of work, as the plan view can already been seen as a schematic when viewing the reticulation. - The same as above goes for Storm water | Sector Discussion | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | General for Access Chambers and Valves | More information required for a decision
959 | 3-Waters | Vol 1 | 2.4.7 Says that pump stations should be a polygon feature and all attributes are to be attached to this polygon. Then in 2.5.2 which refers to Pumps it requires pumps to be a point feature with all attribute information attached to this point. So which is it. The Pump station, the pump, or both? - The same as above goes for Storm water | Noted: no action required | The pump station refers to site specific information. The pump is the asset specific information. | General for Pump and Pump Station | No action
960 | 3-Waters | Vol 1 | 2.6.2 Cathodic Protection- I don’t know what that is. | Noted: no action required | This refers to systems installed to protect water mains from corrosion. | 2.6.2 Cathodic Protection | No action
961 | 3-Waters | Vol 1 | 2.8.2 This puts all the responsibility on the contractor to provide all the specified information in the way the document wants it, with us only needing to import it. - The same as above goes for Storm water | Noted: no action required | It also puts the responsibility on the asset owner to specify it properly | General | No action
962 | 3-Waters | Vol 1 | All the attributes that are being requested of us seems to me to be a lot more information than will ever be needed or used, but if supplied by a contractor as suggested, is achievable. | Noted: no action required | Noted, for analytical purposes | General | No action
963 | 3-Waters | Vol 1 | Waste Water seems to be a repeat of the above. | Noted: no action required | Repeat | General | No action
964 | Potable water | Vol 1 | In Summary The main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed potable water assets as defined by asset managers in New Zealand. While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant. It’s not clear who is meant by consultants here. | Included | Note added in glossary 9/3/2017 | In Summary | Change made document updated
965 | Potable water | Vol 1 | The objective of the specification in Volume 1 is to provide geospatially savvy potable water asset “As Manufactured” and “As-constructed / As-built” digital data. The objective of the specification in Volume 2 is to provide geospatially savvy potable water asset “As Managed” digital data. I don’t like the use of the word savvy | Included | Reviewed and removed | General | Change made document updated
966 | Potable water | Vol 1 | Table 1.8 doesn’t appear to include an allowed category or descriptor for “back-flow preventer” | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | 1.8 Theme Structure | New Code List Entry proposed | Back-Flow Preventer
967 | Potable water | Vol 1 | I presume in Table 1.9 that “N” stands for No. I’m sure there will be some exceptions to the rule per asset | Noted: no action required | Reviewed and Noted only | 1.9 Data Principles | No action
968 | Potable water | Vol 1 | 2.1.1 The explanations on pages 6 and 7 between absolute accuracy, relative accuracy and spatial precision are useful; however I think the sector needs to derive one preferred conceptual practice i.e. is absolute accuracy more important than relative accuracy? Whose data set has primacy? E.g. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | 2.1.1 Accuracy Requirements for Locating Assets | No action
969 | Potable water | Vol 1 | I agree with the QA Validation field being a mandatory attribute in Table 2.1.5 | Noted: no action required | Reviewed and Noted only | 2.1.5 Attribute Data Fields | No action
970 | Potable water | Vol 1 | Not all fields in the project attribute table in 2.1.7 are practical. What about a project that is geographically separated (relining different pipes) or across different asset classes? (e.g. water mains and sewers) | Noted: no action required | Reviewed and Noted only | 2.1.9 Project Attributes | No action
971 | Potable water | Vol 1 | 2.1.1 Pg 17 . Ditto for “Area of Work” extent. | Noted: no action required | Reviewed and Noted only | 2.2.1 Area of Work Extent | No action
972 | Potable water | Vol 1 | 2.3.1 How will an open civil structure be represented? E.g. a settlement pond | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | 2.3.1 Containment Structure | More information required for a decision
973 | Potable water | Vol 1 | The repetitive use of the generic term “Health & Safety Issues” in the respective attribute tables should be revised to documented Health & Safety Risks. Or similar | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure trigger there are 'special circumstances'. A code list is proposed | General | More information required for a decision | Health & Safety Type
974 | Potable water | Vol 1 | I’m unsure what the use of a “Resilience field (as an open text field?) is in these tables. Too much variability and not enough guidance around what data and format to enter. This is an AM (Vol 2) derivation anyway and not an “As-Built” attribute in my view. Whereas “Design Life” is. | Noted: no action required | Resilience Rating is a measured a6ttribute | 4.5 Resilience Schema | No action
975 | Potable water | Vol 1 | 2.3.4 The term Well should be changed to “Bore” | Sector Discussion | Commented on this previoulsy | 2.3.4 Well | More information required for a decision
976 | Potable water | Vol 1 | 2.4.3 The point feature is to be “snapped” to the pipe asset it is associated with. Does the spatial representation snapped to the polyline create a node? If not then this creates problems when modelling. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed | 2.5.3 Valve | No action
977 | Potable water | Vol 1 | 2.4.5 How is a locator cable or Intrinsic Protection (IP) cable for anti-corrosion ruining with a pipe (e.g. taped to the pipe) to be represented? Why in the table do we have to submit pipe diameter, nominal diameter, external diameter and nominal bore? This is overkill and one wrong piece of information will lead to confusion i.e. which one is the correct one? | Sector Discussion | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | 2.4.5 Pipe & 2.6.2 Cathodic Protection | More information required for a decision
978 | Potable water | Vol 1 | 2.4.7 Should the spatial representation include and ancillary works e.g. dry wells, wet wells, filters, air scrubbers or bio-filters (more applicable to wastewater PS I realise) | Noted: no action required | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. | 2.4.6 Pump Station | No action
979 | Potable water | Vol 1 | 2.5.2 Pumps, can take many types and forms. I trust the fields in the table are flexible enough to accommodate the variety to be expected. | Noted: no action required | We hope so. This will be tested during the pilot phase | 2.5.2 Pump | No action
980 | Potable water | Vol 1 | Is a backflow preventer to be considered a mechanical equipment asset or a valve? | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | 2.5.1 Equipment & 2.5.3 Valve | More information required for a decision | Back-Flow Preventer
981 | Potable water | Vol 1 | 2.6.1 Electrical asset – table doesn’t look accommodating enough for the variety of electrical fittings and assets to be expected | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | 2.6.1 Cabling | More information required for a decision
982 | Potable water | Vol 1 | 2.6.2 Good to see Cathodic Protection systems included. | Noted: no action required | Reviewed and Noted only | 2.6.2 Cathodic Protection | No action
983 | Potable water | Vol 1 | 2.8.2 reporting Mismatches could be problematic depending upon the spatial base used – see 2.1.1 above. | Noted: no action required | Reviewed and Noted only | 2.8.2 Matching to Existing Infrastructure | No action
984 | Potable water | Vol 1 | There are a heap more Definitions that could be added to the Glossary e.g. “trunk main” for starters. | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Glossary | More information required for a decision
985 | Potable water | Vol 1 | Request for code lists: On page 158 of volume 1 of the potable water standard there is mention of supplementary document 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016. Even though this document is in draft, I’d really like to take a look at it. Can it be made available for download, or am I to a copy emailed to me? | Sector Discussion | Code lists now incorporated into document | General | Change made document updated
986 | 3-Waters & Buildings | Vol 1 & Vol 2 | We appreciate the work put in by your team and the various working groups in developing these documents. The process of evaluating the standards has also been useful for Education as an agency, in promoting a review of our data collection processes and considering how these align with a potential implementation of the standards. Our comments on the standards focus at the strategic level. For our organization, with over 30,000 buildings, the cost of changing data collection are high. We therefore need to consider very carefully what information we capture, what decisions we will need to take with information, how we control the quality of information and how it is updated. For that reason it is important to us that we understand the proposed benefits and implementation uses of the standards before taking firm decisions on data collection for their use. We look forward to further discussion on implementation. Your presentation at the last governance group was a helpful insight into your team’s thinking: we want to ensure that agencies understand each other before committing to implementation or advancing a business case with Ministers. For that reason our comments are interim, subject to these further discussions. | Noted: no action required | Statement noted. | General | No action
987 | 3-Waters & Buildings | Vol 1 & Vol 2 | Overview of the Metadata Standards Education recognises the importance of asset information in protecting New Zealand’s ability to provide services in a fast-changing national economy. We also endorse a commitment to standardising and sharing information between public agencies. However, we have concerns about the detail and structure of the data proposed in the metadata standards. A challenge in commenting on the proposed metadata standards is understanding the objectives of the data collection process. It remains unclear how this information will be used, what elements of the process will be compulsory and how the comparison between agencies will work. Education is concerned that the costs of collecting the information outlined in the metadata standards will exceed the benefits. Understanding the benefits derived from these comparisons is critical to determining what data should be collected and how it should be categorised. For instance, the data that is needed to promote All-of-Government procurement is very different from the data needed to identify major network risks within New Zealand | Noted: no action required | Statement noted. Business case. | General | No action
988 | 3-Waters & Buildings | Vol 1 & Vol 2 | Education is also concerned that the focus on the physical condition of the assets may be poorly targeted. Rapid changes in demographics profiles, technology and consumer preferences will also have a major impact on the ability of the current asset networks to meet the future needs of communities. We think that the metadata project should place as much emphasis on the ‘fitness for purpose’, as it does to the physical condition. | Noted: no action required | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | General | No action
989 | 3-Waters & Buildings | Vol 1 & Vol 2 | In addition, the metadata standards assume that decisions on asset maintenance are made centrally. Where maintenance decisions are made is a policy choice that is influenced by broader factors than asset management. In the case of Education, asset maintenance decisions are largely managed at a school level. This is a fundamental premise of how the management of schools is devolved to local communities. This is more responsive to the needs of local communities, as well as meaning minor maintenance decisions can be made in the context of education delivery. However, this also means that, while we fund schools for maintenance, we do not specifically control how that funding is spent. This limits the extent to which Education is able to track maintenance expenditure. | Noted: no action required | This standard does not assume where or how decisions are made, it is a set of metadata standards that define decision elements for analytics to support those decisions - in a standard way | No Specific Reference | No action
990 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: Education’s documentation for new construction includes much of the data outlined in the Metadata standards. However, while we collect and hold this information for each project, we do not capture this data into a central database. The nature of this information is useful when looking at the details of potential redevelopment of an asset but not for evaluation at a portfolio level. As with our response to the overall project, Education believes that clearly articulating the benefits of the process will better inform how and what information needs to be collected. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
991 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: We are aware that much of the information for as-built projects will be provided by the contractor. However, we have concerns that the rigorous specification of data may limit the pool of contractors to larger firms with the resources to provide information in a metadata standard. There is a risk that this reduces competition in the industry, and creates price increases especially in provincial centres where Education operates. Education’s exposure to price increases with small building firms is more pronounced than other government agencies who may build a smaller number of more complex facilities (e.g. Courts, Corrections, Defence). | Included | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | N/A | No action
992 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
993 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | Repeat | N/A | No action
994 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education’s ability to maintain the quality of data is also limited by the devolution of maintenance and minor capital works to schools. Most of the subsequent alterations to buildings are controlled by the schools. Reconfiguring teaching spaces is a regular occurrence across the portfolio but it is unlikely that these changes will be updated in as-built records. | Noted: no action required | Implementation considerations are out of scope | General | No action
995 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The detail of components specified in the metadata standards appear to be very granular for many of Education’s buildings – for instance there are about 200 fields to describe a building ceiling. The majority of Education’s building will be a simple domestic-scale or light industrial structures, where there is little benefit in collecting this level of detailed information. | Noted: no action required | Implementation considerations are out of scope | General | No action
996 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education would recommend that different levels of information are collected for different types of assets. For instance, complex multi-storey buildings with lifts, fire protection and science laboratories, would require more extensive data to be collected than single-storey wooden-structure school buildings. | Noted: no action required | Implementation considerations are out of scope | General | No action
997 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The information Education collects on underground services varies greatly depending on the scale and nature of the development. Many of Education’s developments are additions or small schools in provincial locations, with work undertaken by local building firms. The ability of small contracting firms to record in detail where underground services are located is poor, and records are unlikely to be available in an electronic format. Detailed collection of this data may be appropriate for major assets. However, we recommend that collection of geospatial information on underground services is restricted to the larger or more complex developments. | Included | Implementation considerations are out of scope | N/A | No action
998 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The risk assessment analysis in the proposed standards is difficult to interpret and evaluate especially for the type of assets being developed by Education. The scale of Ministry buildings tends to be domestic or light industrial in scale. The risk implications for different components of the assets (such as the roof) cannot be easily separated from the risk profile of other components of the building. We recommend this aspect of the risk criteria of the Metadata standards be critically reviewed. | Sector Discussion | The standards make the separation of components and the analysis of risk at a component level of granularity possible. There will be a further discussion about this level of recording with the technial working group. | No Specific Reference | More information required for a decision
999 | 3-Waters & Buildings | Vol 2 | Broad comments The focus of the data collection is around the building envelope (walls, roof) with significantly less focus on the interior assets. However, building interiors represent a large component of the total cost of providing assets and are the components with the shortest life expectancy. The interior configuration has a major influence on the ability of school buildings to generate positive educational and social outcomes. For these reasons, Education believes the metadata standards should have a greater focus on the interior assets and configuration. | Noted: no action required | All components are collected, including interior components | No Specific Reference | No action
1000 | 3-Waters & Buildings | Vol 2 | Broad comments As well as the definition of the data held, the metadata schema will need to outline the data structure and hierarchy. If information is not collected at a consistent level in the asset hierarchy it makes comparisons between entities difficult. For instance, it is difficult to compare what proportion of the portfolio has fitted wall insulation, if one agency collects the information by building and another by facility. This aspect of the standards should be reviewed. | Noted: no action required | Data Classification, Heirarchy and Structure are all outlined in the Draft Standards | No Specific Reference | No action
1001 | 3-Waters & Buildings | Vol 2 | Broad comments The amount of information collected about the assessor for each data category is unnecessary. It is always useful to know who undertook the assessment but the collection of qualification and experience against each asset is excessive. This detail should be replaced with a measure of confidence around the measures, such as whether it was the result of an exhaustive analysis or a desk-top assessment. | Noted: no action required | Each organisation will decide at what level of granularity (detail) it collects tdata to manage its assets. | No Specific Reference | No action
1002 | 3-Waters & Buildings | Vol 2 | Detailed comments on categories of data The metadata standard outlines the format and categorisation of data on the assets. The following considers each of the categories individually. It discusses these in broad terms and then outlines how Education collates and reports of these asset categories. | Noted: no action required | Statement noted, no action required. | No Specific Reference | No action
1003 | 3-Waters & Buildings | Vol 2 | Condition: The metadata standards propose that condition measures categorise assets by: structure; external; interior; services; and fittings. Separating external cladding and structure is a useful differentiation for some of the housing and light commercial categories. The detail captured on the interior is overly simplistic. The proposed metadata standards focus on cosmetic issues such as the quality of the paint finish, rather than configuration and functionality which is of greater importance for Education. As noted above, interior components represent around one-third of the total building cost and have the highest depreciation rates/shortest lives. Ministry measures: The broad asset categories used by Education are: external; interior; services; and roof. More detailed condition data is held for individual schools but the revaluation and portfolio reporting for Education uses these four categories. Education is currently reviewing options to measure how different building design and fabric choices impact on the light, air quality, temperature and noise levels in teaching spaces. | Noted: no action required | Condition Elements are covered in detail in the standards They do not differentiate buildings by type, beyond the Building Code definition of Facility Importance (which is not building type) These are asset metadata standards, not portfolio form / function and mix standards | 2.2 Condition Schema Code List 13: Facility Importance Rating | No action
1004 | 3-Waters & Buildings | Vol 2 | Repairs and Maintenance The definitions of repairs and maintenance defined in the metadata standards are reasonable and workable. 1. However, collecting data on deferred maintenance items is too complex and unproductive. Part of the issue is that subsequent work may override the maintenance items, but be difficult to identify and measure. Under-maintaining an asset may be best reflected in the condition assessment process. 2. Ministry measures: Education currently identifies programme maintenance items to be undertaken on a building, including recurrence timeframes. Education also categorises the reason for maintenance according to priority (i.e. health and safety, protection of building etc). While Education has a good knowledge of the budgeting for repairs and maintenance, it does not track specific expenditure, accountability for which has been devolved to schools. This means that the explicit scope of work that has been undertaken is not available in Education’s information systems. | Included | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
1005 | 3-Waters & Buildings | Vol 2 | Utilisation: The utilisation measures by nature need to be specific to the industry in which the agency operates and would tend to be for internal reporting only. There is limited advantage in establishing utilisation standards for comparison between entities with very different objectives. This is more appropriately a component of the annual reporting to stakeholders rather than a metadata measure. Ministry measures: Currently Education has a formula for entitlement of classrooms and other space based on school enrolments. Education measures schools’ provision of space compared to entitlement with an optimal target range of 85% to 105%. | Noted: no action required | Agreed, but the standards apply across all Sectoirs (e.g. Housing Providers) | 3.2 Utilisation | No action
1006 | 3-Waters & Buildings | Vol 2 | Demand There are several problems attempting to identify demand for an asset. These are compounded for school assets, which provide free and compulsory services. Commonly residential and light commercial facilities have a variety of different demand parameters. For instance a school hall will support school assemblies, indoor sports activities and community events. Each of these demands has different physical requirements. Measures of demand are therefore difficult to establish. Ministry measures: Education regularly needs to address circumstances where the demand for a school exceeds its capacity. This would commonly be dealt with by strategies such as the application of enrolment zones. Education uses local and regional demographic trends amongst other inputs to identify demand for additional learning spaces and/or new schools. | Noted: no action required | Demand Section has been updated in Volume 2 And, there are many examples of useful demand analytics for schools | 3.3 Demand Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1007 | 3-Waters & Buildings | Vol 2 | Criticality Applying criticality to residential and light commercial buildings is more difficult than with infrastructure. The metadata approach to defining communities being serviced by public sector buildings is not viable. Communities which use public sector buildings tend to be complex and overlapping and criticality dependent on other assets within the network. The definitions of criticality should therefore be limited to explicit requirements in supporting post-disaster response or recovery i.e. identifying assets which have an explicit function defined by Ministry of Civil Defence and Emergency Management plans. Ministry measures: The criticality for the school as a civil defence centre is an agreement between Civil Defence and the Board of Trustees. This will partially be dependent on other community infrastructure in the location. Schools which are Civil Defence centres are not identified within Education’s central information systems. | Noted: no action required | Critciality will be closely linked to Faclity Importance per the Building Code | Code List 13: Facility Importance Rating | No action
1008 | 3-Waters & Buildings | Vol 2 | Risk The metadata schema for risk measurement works to associate risks with asset components. For most of the risks (e.g. earthquake, flooding) it is more appropriate to associate the risk with a building or site, rather than individual component (e.g. roof). Ministry measures: Education has risk registers at a portfolio level and each school has a risk register. Some of the risks associated with the assets relate to the use of materials (e.g. asbestos). These are also logged on the school risk register but not captured centrally. | Included | Risk can be applied at any level of granularity Analytics enable Portfolio level of risk to be established | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1009 | 3-Waters & Buildings | Vol 2 | Resilience The resilience measures have yet to be developed within the metadata standards. The focus of the resilience measures appears to be around major civil defence and emergency events, such as earthquakes. It will be useful to identify the ‘Importance Level’ as defined in building legislation. A sole focus of the civil defence component of resilience is too narrow. We believe the issues should also encompass the ability to change the use of assets or to reconfigure them for different demand or purposes such Ministry measures: When Education developed the business plan for transportable modular classrooms it aimed for these to constitute a proportion of the network to allow flexibility to respond to demographic changes. | Included | Resilience has been updated in the standards | 4.5 Resilience Schema | No action
1010 | 3-Waters & Buildings | Vol 2 | Design Performance The majority of the design performance schema appears to relate to items of equipment, such as pumps and piping. This represents a relatively small proportion of the assets within Education’s network. The majority of the network is relatively uncomplicated, one and two storey buildings, with limited HVAC or specialist facilities. Collecting design performance at the level of individual items is therefore of limited value. Ministry Measures There are some specialised assets within Education’s portfolio, such as lifts in multi-storey buildings. However, these are few in number and are managed under a national contract. Details on the design performance of smaller components, such as heat pumps are typically held by the school. | Included | There are also mant examples of building design perfomance (Earthquake Rating, Energy Rating etc.) | Table 14: Design Performance Examples | An explanation of Data Science will be provided for at the Technical Working Groups
1011 | 3-Waters & Buildings | Vol 2 | Financial Performance There has been significant effort to develop measures for financial performance within the standards. The proposed standards outline a detailed basis for the collection of valuation, depreciation, time of payment information. Rather than replicate data held elsewhere, it would be more useful to ensure that there are linkages with the agency’s broader financial system. This has the advantage of enabling association of asset measures with other agency performance measures, for instance measuring the asset cost per visitor or student. Ministry Measures Education has recently established a new asset management system (Tribal K2) which tracks budgeting for maintenance and other property costs. The system links to Ministry’s property data warehouse system. This allows analysis and development of a broad range of performance measures. The result is the ability to compare asset performance measures to aspects such as student numbers (e.g. the percentage of students learning in buildings that fall into each asset condition category). | Noted: no action required | Organisation specific financial analytics will be supported by attribution within this standard. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1012 | 3-Waters & Buildings | Vol 2 | Service Performance The service performance schema appears to be a raft of unrelated criteria, which individually may be critical to the functionality of the asset, but do not belong in the same category. The result is measures which relate to different levels of assets from components (e.g. disabled access) through to facilities (e.g. iwi interest). A number of the proximity measures, such as kilometres to communities are difficult to establish without further definitions of community. The result is a wide range of criteria which does not allow comparison between different agencies. Similarly, the raft of measures around district plan criteria, such as provision of car parks, is difficult to update. For many public service assets the land will be designated so underlying zonings will be poor indicators of the use of the site. Some aspects of the data, such as iwi values, heritage considerations or community interests, cannot be easily summarised into a data base. It would be better to include an identifier which would highlight whether more detailed analysis is available on file. Overall Education would advocate for service performance to be restructured into a number of separate themes. Ministry measures Education has a basis for evaluating the service levels called the Innovative Learning Environment (ILE) assessment tool. The information is currently collected at a building level and is a requirement of the five yearly capital and maintenance planning process. Education is evaluating ways of standardising the capture of the information. The ILE assessment tool also has facility to include a range of qualitative measures such as ‘how well the design reflects the needs of the local community’ which may be developed in future. | Noted: no action required | No action required with regards to comment son the business case. The standard is intended to system and organisation agnostic. | 5.4 Service Performance Schema | No action
1013 | 3-Waters & Buildings | Vol 1 & Vol 2 | Introduction The Auckland Council family fully supports of the intention behind this standard and has actively contributed in the working groups for roads, residential housing and light commercial buildings and the three waters. The Auckland Council family welcomes the opportunity to provide feedback at this time, and the opportunity to participate in the further development of the standard. The metadata standard is a great opportunity to gain national consensus of what minimum level of data capture is required. This initiative will enable us to ensure that data can be applied in a consistent and repeatable way to make good asset management decisions based on acceptable levels of service, replacement and growth strategies. | Noted: no action required | Statement noted. | General | No action
1014 | 3-Waters & Buildings | Vol 1 & Vol 2 | Summary Feedback is currently sought with specific regards to the three waters and the residential housing and light commercial buildings standards. We have found it difficult to provide meaningful feedback in the absence of a clear strategic message, an understanding of which is shared by all reviewers. That message needs to link the standards to the business case and to recently held discussions with the Minister of Finance. A further opportunity to work on and develop the standard from the ground up, in the way that the transport group has developed the roads standard, would also help the Auckland Council family to feel more confident about the result. To that end we suggest that it would be useful to incorporate such an opportunity into the process from here. We would like: • To present our feedback to the combined governance group • The working groups to review and address all feedback on the standards • The resulting outputs to be made available for consideration by the governance group prior to any public release of the standards | Noted: no action required | Discussions will continue across the Infrastructure Sectors (Core and Social) | No Specific Reference | No action
1015 | 3-Waters & Buildings | Vol 1 | Volume 1 – As-built metadata standard What we like: • Provides reasonable coverage of possible data fields • As a collection of possible attributes it will help to drive a culture of good practice to capture metadata • It brings attention to the need for good base data What we consider could be further developed: • In its current format the standard is not adoptable due to the constraints it will place on systems and business processes this needs to be addressed before it can be adopted. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1016 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • The layout should be modified to clarify the distinctions between master data and metadata. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1017 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • A number of elements have been included but are not complete, and an understanding of industry definitions, hierarchies and processes is required to complete this volume. We would welcome the opportunity to assist with this. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1018 | 3-Waters & Buildings | Vol 2 | Volume 2 – Asset management performance standard What we like: • Recognition of the notion that data is only useful if it is used • An approach that recognises the value of rigorous analysis to inform decision making What we consider could be further developed: • In general, we consider that this volume is under developed with inconsistencies and cross-overs to Volume 1. We would welcome an opportunity to further input into its development, as we recognise that it can provide a useful tool, particularly for organisations with limited capability in this area. | Noted: no action required | Volume 2 is now a comprehensive document | No Specific Reference | No action
1019 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • This volume assumes generalist practices that are inadequate for non-linear assets and includes operational and derived data that is not suitable for inclusion in an AMIS system. | Noted: no action required | This volume is spatially aware, and will attribute point, line, ployline and 3D objects. It is also agnostic to any AMIS and GIS system | No Specific Reference | This will be discussed at the technical workshops
1020 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Needs to be carefully framed for the asset types that it relates to. | Noted: no action required | Asset types are specifically defined within the standards - See Volume 1 of each Group of Assets | No Specific Reference | No action
1021 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Replacement trigger points should be broadened from reliance on subjective visual condition to incorporate best practice for optimal replacement, that is, based on objective measurement and sound engineering judgement. | Included | Visual inspections are only one type of condition assessment to trigger an interventi. Capacity could be another (at Very High > 95%) | Code List 31: Demand – Capacity Unit of Measure | No action
1022 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Reference should also be made to failure mode effects analysis (FMEA/FMECA) as a means to support optimal replacement points. Our feedback does not further consider this volume due to the large disparity with practice and limited workshops to fully capture industry needs. | Included | The standards do not preclude failure mode analysis of any type. The standard captures some of the attributes for this analysis. | 2.3.5 Code Lists | This will be discussed at the technical workshops - mor ework is required here with the sector
1023 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 1. Create a separate volume that covers strategic fit and business needs across all asset categories. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1024 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 2. Focus on a business standard for assets including improving the hierarchy to cover both asset and data hierarchies and outline the relationship between them. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | No Specific Reference | No action
1025 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 3. Review publishing formats to maximise the impact of the standard. | Included | The drafts have now had a full publishing edit | General | No action
1026 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 4. Remove content that is not related to the business standard including those referring to implementation paths, delivery mechanisms and quality control rules. | Sector Discussion | To discuss - for example? | General | More information required for a decision |  | haydn to follow up offline | There are placeholders for Volume 3 / 4 / 5. These require context from time to time, so it is not inappropriate to describe the applicatrion circumstances. | N/A | Close: -
1027 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Workshops The working groups were presented with A-Spec as a straw-man and tasked to focus on the possible data that could be captured for individual asset types. The working groups started with limited traction and concern was raised early on as to the purpose of the workshops in diving into attribute detail that is quite easily obtainable from various sources. A basic data hierarchy was established that allowed the attributes to be tackled in a constructive manner. In hindsight, it would have been useful to consider other industry standards as part of the process. We feel that such consideration could still be undertaken as part of the follow on from this feedback. Despite the concerns mentioned above, the workshop groups generally worked well and came to agreement on the things that were required. It would be extremely useful for the working groups to go over the feedback and address it as appropriate. Strategic, governance and procedural feedback should also be reviewed by the governance groups. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | General | No action
1028 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Definitions of industry terminologies and attributes. | Sector Discussion | Examples required | General | More information required for a decision |  | haydn to follow up offline | This is a discussion for the Pilot. There are many commercial considerations here, alongside a variety of 'industry standards' as described by the 'industry'. | N/A | Close: - this is an alignment question which has been covered
1029 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Identification of business needs. | Noted: no action required | Business case will outline / describe benefits | N/A | No action
1030 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • An assessment of “fit for purpose” data capture. A matrix and understanding of the minimum data capture required based on organisational needs. | Noted: no action required | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | N/A | No action
1031 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Exploring the origin of the data and identifying whether it belongs to volume one (As constructed) of these standards or is better suited with other data sources, for example geotechnical data. | Noted: no action required | These data sets are what are required for asset management purposes | General | No action
1032 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Validation of the Codes list or optional pick lists. | Noted: no action required | Reviewed and implemented | General | No action
1033 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • The standard is required to be system agnostic. Identifying how the standard will be implemented has an effect on the data capture requirements. To enable this we need to understand what the systems and processes look like. The standard needs to be reconciled with these systems and processes at organisation level. | Noted: no action required | Updated | General | No action
1034 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Comparison to international practice and other complimentary standards. | Sector Discussion | Information to be provided for discussion | General | More information required for a decision |  | haydn to follow up offline | There has been a number of reviews against international standards. These (eg OGC) have been aligned to the standards. We will continue to review the standards throughout the pilot for application, due to the variable nature of these standards | N/A | Close: - this is an alignment question which has been covered
1035 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • There is a logical split between roads, buildings and three waters; however there is less logic to further splitting up the three waters when the majority of the components and attributes are the same. It would be sensible to consider consolidating these. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
1036 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Rather than repeating the introductory statements in both volumes of each version of the standard a covering or base document (as seen in most other standards) should be considered, as the principles of data collection are the same. This would also have the advantage of slimming the volumes down. | Noted: no action required | Format based on technical differentiation | General | No action
1037 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Common data sets are repeated at every asset class adding unnecessary volume. | Noted: no action required | Action on data scientists. | General | No action
1038 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • The standard seems to reference the manner in which data will be collected. This is the responsibility of the various organisations and should not form part of the standard. | Noted: no action required | This is not within the scope of these standards | General | No action
1039 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The document will benefit from a better structure around the rationale, strategic drivers and added benefits, of the standard. Some of this information is scattered across the introduction section but it could be strengthened and focused on the purpose of the standard, which is about agreeing on common classifications and definitions. We think there is general agreement that data standards are needed and this doesn’t need to be emphasised. | Noted: no action required | This is not a policy report, an asset management plan, nor a 30 Year Infratsructure Plan (where you would find this requirement). This is a metadata standard for assets at an assetID level of granularity. It does however capture the context of the analytics which inform these types of documents which support organisations asset management | No Specific Reference | No action
1040 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • We believe that the key purpose of this standard should be to outline data requirements that enable organisations to compare their performance and share asset lifecycle knowledge while continuing to measure their performance in a meaningful and cost effective manner in the context of their strategic objectives. | Noted: no action required | Statement noted. | General | No action
1041 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The intention of this standard development was to produce a metadata capture culture and identify the appropriate level of capture. This intention has been somewhat obscured by the very much “field-base” information that is supplied by suppliers and contractors on the physical attributes of assets. We believe that it would be useful to reconsider the audience of this standard and review it to ensure that the audience is appropriately targeted. In that way the business strategy can direct appropriate attribute fields, which will then be common sense as long as common definitions are understood. | Noted: no action required | This observation describes on audience, this is not the only audience, for example design engineers. | General | No action
1042 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Data capture, as acknowledged in the standard is but one component of good asset management and the ways in which this initiative will support organisational challenges such as achieving ISO 55001 accreditation could be made clearer within it. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1043 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The standard strategic goal is to enable organisations and the country “to collect locally and use globally”. It is unclear how this standard compares and incorporates international best practice. There are examples of other international metadata standards however only A-Spec was examined. | Noted: no action required | A number of other standards have been investigated. (Uniclass, Cbi, Omniclass, Master Spec etc. etc.) The strategic goal is to enable organisations and the country “to collect locally and use nationally” | No Specific Reference | No action
1044 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The way in which the standard is currently written presents the data capture requirements in a set manner and format thereby requiring business needs to be moulded for the data specific needs. These limitations are likely to prevent users from taking opportunities in system and process advances that may become available. Some of these initiatives already exist such as open data sources from product suppliers. We expect these advances to become more readily available in the future. It is not clear how the static two-dimensional model presented by this standard will allow business to incorporate these changes. | Noted: no action required | The standard does exactly the opposite to what this is suggesting. The question is not so much about how it is collected but how the data is manipulated into a common format when it is (see FME) | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1045 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Existing systems have been heavily invested in and are very diverse, even in the Auckland council family, to tailor for specific needs. With the possibility of the standard purely becoming a mapping exercise; it then does not support the need to prescribe data fields to intricate detail. The level of data capture required to complete the national level analytics is not identified. Anything else is considered optional and does not support the reason for capturing data at every level. | Noted: no action required | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. But Note use of tools like FME. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1046 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • In order to address the matters referred to in the point above, the standard could be reconfigured to provide the required performance outcome and guidance on how these requirements may be met, while allowing flexibility in means and methods of demonstrating compliance. | Noted: no action required | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. And, there are many analytcal options on the same data sets depending upon he problem being solved. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1047 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • As has been mentioned previously, the document uses terminology and jargon that is not consistent with those used in NZ. This is an easy fix, and appropriate language is a great factor in the ease of adopting new things. | Included | The drafts have now had a full publishing edit | General | More information required for a decision
1048 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • There are plenty of NZ examples of assets of each class and type, and we will be happy to provide some if required. Using Australian examples in a NZ standard is not appropriate where there is a suitable local example available. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | haydn to follow up offline | Will be updated by 30 June | N/A | Close: -
1049 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • It is also important that the examples used are relevant to the asset type contemplated in the standard. Building examples for the residential housing and light commercial standard will make the logic of the approach more apparent. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision
1050 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • Most of the terminology used in the attribute fields is not defined. Without these definitions data cannot be accurately mapped and the data collector will be left to assumptions that will compromise data integrity. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision
1051 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • At the beginning of the working group workshops we agreed that these are business standards – hence system agnostic; this is even mentioned in the document. At the same time the proposed standard – language, data formats and terminology – has been prepared for an easy input to a functional specification for a GIS application. It is evident that the asset classification and the attributes were “flattened” to fit this particular implementation. This has detrimentally affected the business value of the standard – we have a number of attributes that do not belong to the asset class they are listed against. An example: in stormwater, swale only attributes are elevated at channel level, at which level they are meaningless. | Sector Discussion | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | General | More information required for a decision
1052 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The current format of data requirements as a mix of business standard and specification is of particular concern. On one hand it makes the business part of the standard logic hard to follow, while on the other hand the document is not sufficiently detailed to be effective as a functional specification. As a consequence standard does not show the business what it needs to collect and the application vendors will not understand what they need to build. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1053 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The asset data hierarchy needs to be completed. Most importantly the way assets have been grouped for data capture needs to be reconsidered in order to represent the business asset hierarchy. Business hierarchy is of great importance for FMEA, operation and maintenance of complex assets, for example. The exclusion of business hierarchies from the standard will require every organisation to create another set of rules outside of the standard in order to maintain these relationships. | Sector Discussion | The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers that in turn will provide consistency to the asset owners. As each organisation has their own hierachy it is expected that they will categorise the data being provided according to their needs | General | More information required for a decision
1054 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • We strongly recommend that all implementation related fields be removed from the document, as outlined below: o Attribute abbreviations – these are in many cases system related setup and for instance instrumentation may be adopted by numbering systems such as ISA55 that is international practice. The purpose of these abbreviations is not clear. o Character length – This serves no purpose and is not supportive of being system agnostic. By providing full and proper definitions to the attribute field data may be mapped correctly, regardless of character lengths. o Comments – This filed has no purpose that cannot be fulfilled by either the unit filed or description fields o QA validation – These are rules set by business and specific software systems. It also does not serve any purpose to identify minimum capture level. This could be done in a better way through a developed hierarchy that identifies, master data from metadata and compulsory fields from conditional or optional fields | Included | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | General | No action
1055 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • To date geometrical and topology rules have not been discussed. Currently there are different requirements governing the way geospatial data is captured. As with the asset management systems, investment has been made in maintaining systems to these rules. From an analytics point this does not seem to have any impact on the analytic output. Development of such a standard is considered to be a separate endeavour in its own right and has the potential for having great cost impacts to organisations. In the same way one could argue other data sets must then be prescribed – such as geotechnical information, drawings and so on. Flexibility is key, as planning for known technology, given the pace of technological change, will mean that the standard is out of date before it is published. | Included | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | General | No action
1056 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • Attribute sets are not normalised across the asset classes. An example of this is the repetitive material types in the codes lists. (Note. Watercare, Wellington Water and Christchurch City Council were the only parties to receive the codes lists later on request. This was never published. | Included | It is acknowledged that codelists will need to be dynamic in nature and will be open to continued contribution from the sector. The code lists are now incorporated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | General | No action
1057 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • As-built data versus operational data versus derived data is crossed over between the volumes. Separation is required through the data hierarchy. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  | Refer to Volume 1 tab
1058 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 1. Create a separate volume for strategic fit and business needs | Noted: no action required | To discuss | No Specific Reference | More information required for a decision
1059 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Improve the Asset Hierarchy section to cover both asset and data hierarchy and to outline the relationship between them. | Included | Asset Classifications have been defined in the Standards | General | No action
1060 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and simplify attributes specifications; all attributes that do not belong to the As Built standard, such as demand, repair and maintenance, health and safety issues, service and financial performance should be removed. These are time related measures and events that are covered by other parts of the standard. Connecting these events and measures to assets is the subject of asset analytics, not the as built standard. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
1061 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and clean the attribute tables – remove all values that are included as they are not relevant. | Sector Discussion | The standards have harmonised and standardised data and hierarchies across the standards | General | More information required for a decision |  | haydn to follow up offline | An addition of explanation has been added to standards - completed | page 1 | Close: -
1062 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Clean the relationship between asset classes, attributes and values. One asset class has to belong to one asset category. | Included | Asset Classifications have been defined in the Standards | General | More information required for a decision
1063 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Outline a list of core asset characteristics – the whole concept of the standard as vehicle for comparability becomes meaningless if we don’t agree on a few critically important attributes that must be collected. | Noted: no action required | Mandatory, Optimal, Optional will be discussed with the sectors | No Specific Reference | More information required for a decision
1064 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Our recommendation is to add a section on asset geometry and topology for water networks – but not one that could be mistaken for a specification for GIS applications. This section needs to address the core rules for creating geometric networks and outline the participation of all assets in these networks. | Included | Included in the draft Standards | General | No action
1065 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Since all standards are related and are part of the same suite of documents it would make sense for them to be published as related volumes (chapters?) rather than independent books. | Included | This has been reviewed, and a decision to keep as separate documents made - at this time (the documents would be 300+ pages if combined | No Specific Reference | No action
1066 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Another approach to publishing standards which would be effective is by using links to look up the list of attribute values. | Included | Other access toolss will be reviewed before release in July 2017 | No Specific Reference | No action
1067 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Think about publishing the data tables in a data view in addition to the document | Included | Included in the draft Standards | General | More information required for a decision
1068 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 4. Remove content that is not related to the business asset data standard: • We strongly recommend that all references to implementation paths, delivery mechanisms and quality control rules be removed from this document. This should be a subject to a separate project/ research due to the variety of business models that can be applied. Unless there is a directive for a centralised implementation of these standards, they remain the responsibility of each organisation and have to be adapted to the particular technology platform. | Noted: no action required | Unclear of where there are examples of this | No Specific Reference | No action
1069 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1070 | 3-Waters | Vol 1 | Asset class definitions needed: Need clear definition of asset classes. Channels are particularly bad examples; they cover a range of assets with various function and purpose - and badly. Under current structure there is no way to describe sw treatment devices. | Sector Discussion | Classifications and types defined in the standards Refer to code lists | General | More information required for a decision
1071 | 3-Waters | Vol 1 | Attribute definitions needed: Many definitions are unclear or missing. Some appear to be database oriented - need to be business meaningful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1072 | 3-Waters | Vol 1 | Standard is about structured data, not any information about assets: This standard should cover the data that needs to be captured in as structured way for further analytical and reporting use. Hence all data that has no such value needs to be removed. In complex assets most of the asset specific data is kept in operation manuals and other operation related documentation. | Noted: no action required | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | General | No action
1073 | 3-Waters | Vol 1 | This is volume one - as constructed assets. Remove all data that is not relevant to as constructed - there are other volumes that this data is described | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1074 | 3-Waters | Vol 1 | Huge number of attributes that are not relevant and not agreed. Need to go back to the workshop discussions and agree how feedback following working sessions will be captured - cannot afford to continue like that. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1075 | 3-Waters | Vol 1 | Renewal material in pipes. This should be relabeled to say lining material. | Included | Attributes included, lining material included in standards see code lists | General for Pipes | No action
1076 | 3-Waters | Vol 1 | Missing attributes. Lining material installation data is critical | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
1077 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Noted: no action required | Information to be provided for discussion refer to ID1069 | General | More information required for a decision |  |  |  | Action: - Graeme to provide a new table to Haydn, who will copy and replace the existing table
NEW001 | 3-Waters | Vol 2 | Code List 9 - people with a spade won't understand the difference between these codes, as they are all the same thing to the person on the ground | Sector Discussion | Codelist 21 on page 45 | [5 empty] | understanding the importance of data, and what is essential v optional, will be determined during initial implementation | Graeme provide the codelist | Christchurch |  | DUPLICATE see NEW005
NEW002 | 3-Waters & Buildings | Vol 1 & Vol 2 | In volume 2 there is a space to define mandatory - but there isn't the same in volume 1. what's going on? | Sector Discussion |  | General |  |  |  | understanding the importance of data, and what is essential v optional, will be determined during initial implementation |  | Action: - Haydn Remove the mandatory field from volume 1 | Haydn |  | Completed
NEW003 | 3-Waters & Buildings | Vol 2 | Need to include an attribute where something hasn't been assessed yet | Sector Discussion |  | General |  |  |  | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty |  | Action: - George to add 'not assessed' as an attribute where needed | GISSA |  | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty
NEW004 | 3-Waters & Buildings | Vol 1 & Vol 2 | There are potentially occurances where the standards include code lists, where not enough information is known to make the code lists finite - suggestion that these code lists are flagged as being examples etc | Sector Discussion |  | General |  |  |  | Completed Added to standard |  | Action: All required additions/changes to code lists to be provided to GISSA by COB 2nd June 2016 | GISSA |  | Completed Added to standard
NEW005 | 3-Waters & Buildings | Vol 2 | Table 2 - looks more transactional than elemental, why connected to an 'event' rather than directly to the 'table'? | Sector Discussion |  | General |  |  |  | Multivariate analysis |  | Action: Nick and Haydn to discuss and determine if changes are needed to the standards pre relase | Haydn |  | No further action required

## Workshop 4 Buildings Vol 1
NZAMS - Sector Feedback - Final Version (Workshop 4 Buildings Vol 1)
ID | Standard | Volume | Feedback | Status Included, Excluded, Sector discussion, Noted: no action required | Final Comments for Publication | Section Reference in Final Version - per Contents page | Additional Work | Proposed Codelists / Attributes | Workshop Outcome LINZ notes 2 MAY | ACTION BY | Notes / Updates | Ref | Workshop Outcome 23-24/5/2017 | GISSA/Other | ACTION TAKEN
1 | Potable water | Vol 2 | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Completed with Metaconnect | No Specific Reference | No action
2 | Potable water | Vol 2 | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Included | Completed with Metaconnect | No Specific Reference | No action
3 | Potable water | Vol 2 | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Included | Completed with Metaconnect | No Specific Reference | No action
4 | Buildings | Vol 2 | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Included | Completed with Metaconnect | No Specific Reference | No action
5 | Stormwater | Vol 2 | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | Completed with Metaconnect | No Specific Reference | No action
6 | Stormwater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
7 | Wastewater | Vol 2 | Should be "coordinate reference system" as in ISO 19111 | Included | Standards are OGC spatial attribution compliant | Use of the Specification | No action
8 | Wastewater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
9 | Potable water | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | not required in this section, covered in later sections | Use of the Specification | No action
10 | Potable water | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
11 | Potable water | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
12 | Potable water | Vol 1 | or vertical datum | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
13 | Potable water | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | changed precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | Change made document updated
14 | Buildings | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Noted: no action required | Reviewed and Noted only | Use of the Specification | No action
15 | Buildings | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
16 | Stormwater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
17 | Stormwater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
18 | Stormwater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
19 | Stormwater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
20 | Wastewater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Updated in draft standards | Use of the Specification | No action
21 | Wastewater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
22 | Wastewater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
23 | Wastewater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Updated in draft standards | 2.1.2 Projections and Datums | Change made document updated
24 | Wastewater | Vol 1 | Update to NZVD2016 | Included | Updated in draft standards | Glossary | Change made document updated
25 | 3-Waters | Vol 1 & Vol 2 | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General | No action
26 | 3-Waters | Vol 1 & Vol 2 | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Noted: no action required | Reviewed and Noted only | General | No action
27 | 3-Waters | Vol 1 & Vol 2 | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference | No action
28 | 3-Waters | Vol 1 & Vol 2 | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | Included | The drafts have now had a full publishing edit | General | Change made document updated
29 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Noted: no action required | The adoption of extents of fields is determined ny each organisation | General | No action
30 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General | No action
31 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General | No action
32 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | Noted: no action required | Future work is yet to be determined | General | No action
33 | 3-Waters | Vol 1 & Vol 2 | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | Included | The classification has been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
34 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | Included | The classification has been defined in the Standards Code Lists included | General | No action
35 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | Included | The classification has been defined in the Standards | General | No action
36 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | Included | Asset Classifications have been defined in the Standards Code Lists included | General | No action
37 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy | No action
38 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Noted: no action required | The adoption of extents of fields is determined by each organisation | General for Hierarchy | No action
39 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference | No action
40 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference | No action
41 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics | No action
42 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums | No action
44 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Included | Adjustment will be made to standards | General | Change made document updated
45 | 3-Waters | Vol 1 & Vol 2 | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Noted: no action required | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. | General | No action
46 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Noted: no action required | Reviewed and Noted only | General | No action
47 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Included | Photographic Evidence is an optional attribute | General | change made document updated
48 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Noted: no action required | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General | New Code List proposed | Health & Safety Type
49 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Included | Adjustment will be made to standards | General | Change made document updated
50 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | No action
51 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | No action
52 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | Included | Code lists included in standards | 2.3.3 Retaining Structure | No action
53 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Sector Discussion | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | No action
54 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves | More information required for a decision
55 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Noted: no action required | These standards are not about Treatment Plants | General | No action
56 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | Included | Code lists included in standards | General Equipment | Gauge input from next review
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail.
58 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments | No action
59 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | Gauge input from next review
60 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General | No action
61 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | Change made document updated
62 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | Change made document updated
63 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA)
64 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | Noted: no action required | resolved in updated version | 2.5.1 Equipment | Change made document updated
65 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
66 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision
67 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision
68 | Stormwater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | AddCCTV & Laser Profiling testing to code list testing type | General | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
69 | Stormwater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Sector Discussion | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | New attribute proposed | Installer of Asset
70 | Stormwater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Sector Discussion | Reviewed and Noted for Inclusion | 2.3.4 Pipe | More information required for a decision
71 | Stormwater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | General | New Code List entry for Condition Assessment Type proposed | Deflection Test
72 | Stormwater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
73 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
74 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
75 | Stormwater | Vol 1 | Deflection Test result | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | New Code List entry for Condition Assessment Type proposed | Compaction Test
76 | Stormwater | Vol 1 | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not)
77 | Stormwater | Vol 1 | Seal Access Safety | Sector Discussion | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber | New Code List & entries proposed | Health & Safety Type
78 | Stormwater | Vol 1 | Manufacturer Manufacturing Standard Third Party QA Accreditation | Sector Discussion | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
79 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.4.4 Pipe | New attribute proposed | Rigid or Flexible as option
80 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling
81 | Stormwater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | Additional entries included in Code list Condition Assessment Type
82 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling
83 | Stormwater | Vol 1 | Rigid material standard and QA Separate Flexible material standard and it's QA | Sector Discussion | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA
84 | Stormwater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test
85 | Stormwater | Vol 1 | Compaction strength per NZS4566.2 | Sector Discussion | More information required for a way forward | 2.4.4 Pipe | More information required for a decision
86 | Stormwater | Vol 1 | Third Party QA for pipe material manufacturer | Sector Discussion | Third Party QA Accreditation to code lists | 2.4.4 Pipe | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list
87 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
88 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing
89 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing
90 | Wastewater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
91 | Wastewater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments | New attribute proposed | Installer of Asset
92 | Wastewater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
93 | Wastewater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | 1.7 Heirarchy | Create entries Desktop Visual cctv laser etc
94 | Wastewater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
95 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
96 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
97 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
98 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
99 | Wastewater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | More information is required to inform a way forward | 2.3.4 Pipe | More information required for a decision
100 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling
101 | Wastewater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Compaction Test per NZ4566.2 Foundation strength pre-install
102 | Wastewater | Vol 1 | Compaction strength per NZS4566.2 or NZS3725 | Sector Discussion | More information required for a way forward | 2.3.4 Pipe | More information required for a decision
103 | Wastewater | Vol 1 | Third Party QA for pipe material manufacturer | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
104 | Stormwater | Vol 1 | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure | More information required for a decision
105 | Stormwater | Vol 1 | Spillway should be its own Asset Class | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure | More information required for a decision
106 | Stormwater | Vol 1 | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles | More information required for a decision
107 | Stormwater | Vol 1 | Source for what? This should have more detail. | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | Change made document updated
108 | Stormwater | Vol 1 | Does this include forebay bunds and pond banks associated with ponds? | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks
109 | Stormwater | Vol 1 | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure | More information required for a decision
110 | Stormwater | Vol 1 | Bathymetry Attribute? | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | Haydn suggest this is excluded as I think it can be sourced from LINZ
111 | Buildings | Vol 1 | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable | Noted: no action required | Reviewed and Noted only | General | No action
112 | Buildings | Vol 1 | The Hierarchy table works well | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy | No action
113 | Buildings | Vol 1 | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. | Sector Discussion | Reviewed and Noted only for discussion | General | No action |  | to be addressed as part of implementation learnings | nil | This is an output from the pilots, as agreed at the workshops
114 | Buildings | Vol 1 | Complex requirement for such a large property portfolio | Noted: no action required | Reviewed and Noted only | General | No action
115 | Buildings | Vol 1 | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles | No action
116 | Buildings | Vol 1 | This is a huge task for as constructed / as built for a large portfolio | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
117 | Buildings | Vol 1 | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | Reviewed and Noted only | General | No action
118 | Buildings | Vol 1 | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General | No action
119 | Buildings | Vol 1 | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | No action
120 | Buildings | Vol 1 | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes | More information required for a decision |  | Noted | nil | Discussed during the may 1-3 workshops Noted no further discussion or action required |  | Closed: - |  | No further action
121 | Buildings | Vol 1 | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) | Noted: no action required | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General | No action
122 | Buildings | Vol 1 | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
123 | Buildings | Vol 1 | V_Proc  what is this and what is it to relate to? | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
124 | Buildings | Vol 1 | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? | Included | Tables will be referenced in Final Versions | General | No action
125 | Buildings | Vol 1 | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 | More information required for a decision |  | capture the rating specification (code) and the year of the specification | GISSA | Created new attribute in Project Table post publication of document dated May 23 2017. (Now in v3) |  | Closed : - |  | No further action
126 | Buildings | Vol 1 | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof | More information required for a decision |  | GISSA to review wording to ensure clarity | GISSA | Reviewed wording no change |  | Closed : - |  | No further action
127 | Buildings | Vol 1 | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision |  | GISSA to review wording to ensure clarity | GISSA | Reviewed wording no change |  | Closed : - |  | No further action
128 | Buildings | Vol 1 | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision |  | GISSA to review wording to ensure clarity | GISSA | The schemas are designed for recording of data at time of construction. |  |  |  | No further action
129 | Buildings | Vol 1 | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone | Noted: no action required | This detail is to be provided at the time it was built not at time of capture This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint | No action
130 | Buildings | Vol 1 | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
131 | Buildings | Vol 1 | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint | Change made document updated |  | External data set - out of scope | speak to haydn | Point to (i) Geotechnical investigation and testing. Laboratory testing of soil and (ii) Determination of particle density and Geotechnical investigation and testing. Field testing. Ménard pressuremeter test | N/A
132 | Buildings | Vol 1 | Graffiti  irrelevant | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint | No action
133 | Buildings | Vol 1 | Flood  applicable only in related areas, and this information is on local council records | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint | No action
134 | Buildings | Vol 1 | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint | No action
135 | Buildings | Vol 1 | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint | No action
136 | Buildings | Vol 1 | Design life how is this applied to existing property | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
137 | Buildings | Vol 1 | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling | No action
138 | Buildings | Vol 1 |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
139 | Buildings | Vol 1 | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling | No action
140 | Buildings | Vol 1 | Finish  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
141 | Buildings | Vol 1 | Finish condition assessment, condition and repairs  ✓ The rest is superfluous | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
142 | Buildings | Vol 1 | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satisfy both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling | No action
143 | Buildings | Vol 1 | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
144 | Buildings | Vol 1 | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
145 | Buildings | Vol 1 | Design life  If new = Ok | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
146 | Buildings | Vol 1 | Cost  Not needed? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
147 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
148 | Buildings | Vol 1 | Too much detail required for ceilings. Condition, material, surface finish = Yes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
149 | Buildings | Vol 1 | Risk, Resilience, and Financial performance  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
150 | Buildings | Vol 1 | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
151 | Buildings | Vol 1 | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling | More information required for a decision |  | GISSA to review wording to make more expilicit | haydn | An addition of explanation has been added to standards - completed | page 1 | Closed : - |  | No further action
152 | Buildings | Vol 1 | Smoke_Barr  Smoke relevant to multiunit development only. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
153 | Buildings | Vol 1 | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling | Change made document updated |  | Implementation to identify optional/mandatory split of these fields | nil | This is an output from the pilots, as agreed at the workshops
154 | Buildings | Vol 1 | Des_Life - ? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
155 | Buildings | Vol 1 | Cost ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
156 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
157 | Buildings | Vol 1 | Whole page  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
158 | Buildings | Vol 1 | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor | No action
159 | Buildings | Vol 1 | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
160 | Buildings | Vol 1 | Live load rating of floor à too difficult to define | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
161 | Buildings | Vol 1 | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
162 | Buildings | Vol 1 | Repairs and Maintenance à what’s the need for this? | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema | No action |  | close, analytics to provide value for money | nil | Discussed during the may 1-3 workshops Noted no further discussion or action required
163 | Buildings | Vol 1 | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference | No action |  | close, analytics to provide value for money | nil | Discussed during the may 1-3 workshops Required to determine value for money Noted no further discussion or action required
164 | Buildings | Vol 1 | First 5 rows à Very detailed for residential use. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
165 | Buildings | Vol 1 | Bracing is as per ceiling notes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
166 | Buildings | Vol 1 | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision |  | close, this is an optional field | GISSA | Discussed during the may 1-3 workshops Noted no further discussion or action required Noted no further discussion or action required |  |  |  | No further action
167 | Buildings | Vol 1 | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision |  | close, cost is part of asset management requirements | nil | Discussed during the may 1-3 workshops Cost is a required asset management requirement Noted no further discussion or action required |  |  |  | No further action
168 | Buildings | Vol 1 | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
169 | Buildings | Vol 1 | Third row à Maybe | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
170 | Buildings | Vol 1 | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
171 | Buildings | Vol 1 | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
172 | Buildings | Vol 1 | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
173 | Buildings | Vol 1 | Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
174 | Buildings | Vol 1 | - Multi storey application only. Too much detail required. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
175 | Buildings | Vol 1 | Last 5 yellow rows à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
176 | Buildings | Vol 1 | - 2nd row à ? Building Code complaint for new works. Unknown for much existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
177 | Buildings | Vol 1 | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
178 | Buildings | Vol 1 | Thermal barrier à ? Floor insulation is all that is relevant in residential. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
179 | Buildings | Vol 1 | All pages à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
180 | Buildings | Vol 1 | Whole page à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
181 | Buildings | Vol 1 | Acoustic row, content  maybe Cost  X Rest of page  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
182 | Buildings | Vol 1 | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
183 | Buildings | Vol 1 | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
184 | Buildings | Vol 1 | Whole page  undefinable in existing housing. | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
185 | Buildings | Vol 1 | Vents  ✓ Membrane rows  Define what membrane? | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation | No action
186 | Buildings | Vol 1 | Foundation area, content à ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation | No action
187 | Buildings | Vol 1 | à See previous foundation notes | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision |  | close | provide feedback | Discussed during the may 1-3 workshops Optional will depend on an organisations ability to capture Noted no further discussion or action required |  |  |  | No further action
188 | Buildings | Vol 1 | All pages à ✕ | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision |  | close | nil | Discussed during the may 1-3 workshops Optional will depend on an organisations ability to capture Noted no further discussion or action required |  |  |  | No further action
189 | Buildings | Vol 1 | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof | No action
190 | Buildings | Vol 1 | Load wind/fix  Not known in existing stock | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof | No action
191 | Buildings | Vol 1 | Frame_Tr  not always identifiable Frame_ Sp  why? | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
192 | Buildings | Vol 1 | Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
193 | Buildings | Vol 1 | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
194 | Buildings | Vol 1 | Last 3 rows  Is this needed and how is it defined? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision |  | H&S, Photos, Comments - these are all optional -= close | nil | Discussed during the may 1-3 workshops Optional will depend on an organisations ability to capture Noted no further discussion or action required |  |  |  | No further action
195 | Buildings | Vol 1 | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
196 | Buildings | Vol 1 | First row, QA Validation  N/A needs to be applied here | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof | No action
197 | Buildings | Vol 1 | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
198 | Buildings | Vol 1 | Last 5 rows  as per previous notes | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision |  | 194 + Financial Performance + service performance are optional, close | nil | Discussed during the may 1-3 workshops Optional will depend on an organisations ability to capture Noted no further discussion or action required |  |  |  | No further action
199 | Buildings | Vol 1 | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
200 | Buildings | Vol 1 | Whole page  ✓ apart from: Cost row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
201 | Buildings | Vol 1 | First 3 rows  ? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision |  | optional - close | nil | Discussed during the may 1-3 workshops Optional will depend on an organisations ability to capture Noted no further discussion or action required |  |  |  | No further action
202 | Buildings | Vol 1 | Last row, QA validation à Critical | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof | More information required for a decision |  | need to follow up with submittor as to exactly what they are after in this field | follow up by GISSA | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED JUNE |  | Action: - George to chase up | GISSA | No further information provided
203 | Buildings | Vol 1 | Risk  ✓ Resil, Des_Perf  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
204 | Buildings | Vol 1 | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
205 | Buildings | Vol 1 | Whole page à ✓ Apart from Cost row à ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
206 | Buildings | Vol 1 | First 3 rows à? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
207 | Buildings | Vol 1 | critically, QA Validation à Critical | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
208 | Buildings | Vol 1 | All 3 rows  ? Row 3  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
209 | Buildings | Vol 1 | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
210 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
211 | Buildings | Vol 1 | All 4 rows  ✕, ?, ?, ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
212 | Buildings | Vol 1 | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
213 | Buildings | Vol 1 | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | No action
214 | Buildings | Vol 1 | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
215 | Buildings | Vol 1 | Whole page à✕. Risk – could relate to a water risks | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
216 | Buildings | Vol 1 | Whole page à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
217 | Buildings | Vol 1 | Classifications, Masterpec, Enclosure à not sure what this is representing? | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof | No action
218 | Buildings | Vol 1 | Ins-Type, R_Value à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
219 | Buildings | Vol 1 | Whole page  ✓ Insulation installer and warranty  maybe | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
220 | Buildings | Vol 1 | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
221 | Buildings | Vol 1 | Whole pink pages/part  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
222 | Buildings | Vol 1 | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls | No action
223 | Buildings | Vol 1 | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
224 | Buildings | Vol 1 | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
225 | Buildings | Vol 1 | Grout and Wall Structure Joint  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
226 | Buildings | Vol 1 | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
227 | Buildings | Vol 1 | Condition  ✓ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
228 | Buildings | Vol 1 | Structure, Bracing à As per floor and roof bracing | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
229 | Buildings | Vol 1 | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
230 | Buildings | Vol 1 | Wall, Design Life à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
231 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
232 | Buildings | Vol 1 | Fire barrier à Multiunit. May not be known on existing stock | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
233 | Buildings | Vol 1 | Orange à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
234 | Buildings | Vol 1 | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
235 | Buildings | Vol 1 |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor | No action
236 | Buildings | Vol 1 | Whole page à why would we use this information? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
237 | Buildings | Vol 1 | Acoustic and Thermal rating à Not used. Where applicable? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
238 | Buildings | Vol 1 | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor | No action
239 | Buildings | Vol 1 | à Why / how would we use this? Too much information required. | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs | No action
240 | Buildings | Vol 1 | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs | No action
241 | Buildings | Vol 1 | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
242 | Buildings | Vol 1 | Pages  ✕ | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
243 | Buildings | Vol 1 | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision |  | optional - close | provide feedback | Discussed during the may 1-3 workshops Optional will depend on an organisations ability to capture Noted no further discussion or action required |  |  |  | No further action
244 | Buildings | Vol 1 | Framed and Frame material à not defined in window anatomy page 149 | Sector Discussion | Update diagram on p149 | 2.5.3 Windows | Modify Diagram |  | update the diagram | GISSA | Will be updated by June 30 |  | Action: - George to update in the standards | GISSA | Diagram updated
245 | Buildings | Vol 1 | Height of windows in mm à what value? | Noted: no action required | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | No action
246 | Buildings | Vol 1 | Condition  ✓ Width  why needed? | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision |  | close | nil | Discussed during the may 1-3 workshops Noted no further discussion or action required |  |  |  | No further action
247 | Buildings | Vol 1 | Manufacturer, warranty, installation date, installer àUnknown on existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
248 | Buildings | Vol 1 | Design life à How to define? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
249 | Buildings | Vol 1 | Repairs à ? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
250 | Buildings | Vol 1 | Page à✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
251 | Buildings | Vol 1 | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
252 | Buildings | Vol 1 | Hardware à Locks, Yes. Lever/knobs maybe. | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
253 | Buildings | Vol 1 | Whole Column Name – Full is circled à Not always known on existing. Why needed? | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows | No action
254 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
255 | Buildings | Vol 1 | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | No action
256 | Buildings | Vol 1 | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
257 | Buildings | Vol 1 | Services, pink section àmore commercial application. | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
258 | Buildings | Vol 1 | à No! How is this captured realistically and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components | No action
259 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
260 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
261 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
262 | Buildings | Vol 1 | à Would we use this at a per item attribute? | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
263 | Buildings | Vol 1 | Type à ✓ Last row, content à NA | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
264 | Buildings | Vol 1 | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
265 | Buildings | Vol 1 | àToo difficult and unnecessary info | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
266 | Buildings | Vol 1 | à Stove have heater fans | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment | No action
267 | Buildings | Vol 1 | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment | No action
268 | Buildings | Vol 1 | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment | No action
269 | Buildings | Vol 1 | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) | No action
270 | Buildings | Vol 1 | Pink section  Not sure how much of this is required/useful | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) | No action
271 | Buildings | Vol 1 | Blue section - ✓ | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings | No action
272 | Buildings | Vol 1 | Asset type à ✓ Kitchen Vanities in contents | Included | Add to codelist | 2.7.4 Fixtures & Fittings | New Code List entry for Fittings Type proposed | Kitchen Vanities
273 | Buildings | Vol 1 | Length, Height, Width à Why? | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings | More information required for a decision |  | close | nil | Discussed during the may 1-3 workshops Noted no further discussion or action required |  |  |  | No further action
274 | Buildings | Vol 1 | Whole page à Doubt this would be known | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings | No action
275 | Buildings | Vol 1 | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) | No action
276 | Buildings | Vol 1 | à Covered in Building WOF. *Specialist area = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components | No action
277 | Buildings | Vol 1 | àSpecialists information and only applicable to multi-unit/storey complexes. | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts | No action
278 | Buildings | Vol 1 | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. | Noted: no action required | Reviewed and Noted only | 2.7.9 Security | No action
279 | Buildings | Vol 1 | à Not so useful in residential and difficult to maintain/update. | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage | No action
280 | Buildings | Vol 1 | à Not really applicable to existing housing. Maybe some use in multi-unit development. | Noted: no action required | Reviewed and Noted only | 2.8.1 Space | No action
281 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
282 | Buildings | Vol 1 | à ✕ | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | No action
283 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
284 | Buildings | Vol 1 | Material à ✓ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
285 | Buildings | Vol 1 | Pipe type à ✕ | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data | No action
286 | Buildings | Vol 1 | Water type à ? | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data | No action
287 | Buildings | Vol 2 | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference | No action
288 | Buildings | Vol 2 | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Included | Edited to make clearer | No Specific Reference | Change made document updated
289 | Buildings | Vol 2 | This document excludes industrial buildings and Ancillary building’s  provide examples | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
290 | Buildings | Vol 2 | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
291 | Buildings | Vol 2 | Added Laundry to Outbuildings, included in the Residential standard | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
292 | Buildings | Vol 2 | The bullet points à are they attributes or measures? | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | Haydn
293 | Buildings | Vol 2 | What is Boolean data type? | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type | No action
294 | Buildings | Vol 2 | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | Change made document updated
295 | Buildings | Vol 2 | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | no action
296 | Buildings | Vol 2 | The third and fourth suite of analytics à seems very granular? | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
297 | Buildings | Vol 2 | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | References are being considerd | No Specific Reference | No action
298 | Buildings | Vol 2 | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | Haydn
299 | Buildings | Vol 2 | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference | No action
300 | Buildings | Vol 2 | Table 4. à unclear what this actually shows? | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas | No action
301 | Buildings | Vol 2 | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | No action
302 | Buildings | Vol 2 | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Included | Updated in draft Standards | Code List 16: Condition Rating | No action
303 | Buildings | Vol 2 | Operations definition à What does this mean? Is this routine/preventative maintenance? | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
304 | Buildings | Vol 2 | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
305 | Buildings | Vol 2 | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
306 | Buildings | Vol 2 | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Sector Discussion | Mandatory / Optimal and Optional will be discussed | No Specific Reference | No action
307 | Buildings | Vol 2 | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) | No action
308 | Buildings | Vol 2 | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
309 | Buildings | Vol 2 | 1st bullet point à E.g. roof? Fire alarms? | Noted: no action required | Can be as granular as needed. | No Specific Reference | No action
310 | Buildings | Vol 2 | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Included | Updated in Draft Standards | No Specific Reference | Haydn
311 | Buildings | Vol 2 | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference | No action
312 | Buildings | Vol 2 | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
313 | Buildings | Vol 2 | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | No action
314 | Buildings | Vol 2 | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
315 | Buildings | Vol 2 |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
316 | Buildings | Vol 2 | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes | No action
317 | Buildings | Vol 2 | Code G, Malicious damage à Does this include tenant damage? | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
318 | Buildings | Vol 2 | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating | No action
319 | Buildings | Vol 2 |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating | No action
320 | Buildings | Vol 2 |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference | No action
321 | Buildings | Vol 2 |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
322 | Buildings | Vol 2 |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema | No action
323 | Buildings | Vol 2 | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference | No action
324 | Buildings | Vol 2 | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Noted: no action required | No action required. Understood. | No Specific Reference | No action
325 | Buildings | Vol 2 | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | Haydn
326 | Buildings | Vol 2 | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element | To discuss with technical Working Groups
327 | Buildings | Vol 2 | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Noted: no action required | The attribute is optional. | No Specific Reference | No action
328 | Buildings | Vol 2 | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference | No action
329 | Buildings | Vol 2 | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference | No action
330 | Buildings | Vol 2 | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Noted: no action required | These are at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists | No action
331 | Potable water | Vol 1 | Add USB memory sticks/hard drives to this list. | Included | Changed in all documents | 1.5 Deliverables | Change made document updated
332 | Potable water | Vol 1 | Question: Are there requirements for developers to retain information after transmission? | Noted: no action required | We see this as something for the developer to make the call if they retain a copy or not. | 1.5 Deliverables | No action
333 | Potable water | Vol 1 | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. | Excluded | keep current practice. | 2.1.5 Attribute Data Fields | No action
334 | Potable water | Vol 1 | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. | 2.1.10 Common Attributes | No action
335 | Potable water | Vol 1 | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters | 2.2.1 Area of Work Extent | More information required for a decision
336 | Potable water | Vol 1 | For circular assets, should length and width both be populated and be the same (diameter)? | Included | For circular assets, length is not required and will be made conditional | 2.3.1 Containment Structure | Change made document updated
337 | Potable water | Vol 1 | Rename to Length Metres for consistency | Included | Changed all instances to length metres and length millimetres as appropriate | 2.3.1 Containment Structure | Change made document updated
338 | Potable water | Vol 1 | Overflow = OS? What does OS stand for? Should this be OF? | Noted: no action required | This term was agreed to by the TWG, retained | 2.3.1 Containment Structure | No action
339 | Potable water | Vol 1 | Earlier wells were requested to be polygon type. Is the point supplementary? | Included | Typo corrected, is to be polygon. | 2.3.4 Well | Change made document updated
340 | Potable water | Vol 1 | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station | More information required for a decision
341 | Potable water | Vol 1 | I believe this table and its attribute names have become mis-aligned. | Sector Discussion | Looks OK, need more information | 2.5.1 Equipment | More information required for a decision
342 | Wastewater | Vol 1 | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe | No action
343 | Wastewater | Vol 1 | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. | Noted: no action required | The standards are recording as-constructed | 1.8 Theme Structure | No action
344 | Wastewater | Vol 1 | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? | Noted: no action required | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure | No action
345 | Wastewater | Vol 1 | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
346 | Wastewater | Vol 1 | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets | No action
347 | Wastewater | Vol 1 | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent | More information required for a decision
348 | Wastewater | Vol 1 | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent | No action
349 | Wastewater | Vol 1 | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | Change made document updated
350 | Wastewater | Vol 1 | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
351 | Wastewater | Vol 1 | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
352 | Wastewater | Vol 1 | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber | No action
353 | Wastewater | Vol 1 | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. | 2.3.3 Fitting | No action
354 | Wastewater | Vol 1 | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting | No action
355 | Wastewater | Vol 1 | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting | More information required for a decision
356 | Wastewater | Vol 1 | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. | Sector Discussion | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe | More information required for a decision
357 | Wastewater | Vol 1 | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe | More information required for a decision
358 | Wastewater | Vol 1 | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. | Included | Precision is defined in the standards | 2.3.4 Pipe | No action
359 | Wastewater | Vol 1 | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision
360 | Wastewater | Vol 1 | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe | No action
361 | Wastewater | Vol 1 | These changes should be coded into the pipe geometry, not as separate notes about the pipe. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision
362 | Wastewater | Vol 1 | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | Change made document updated
363 | Wastewater | Vol 1 | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe | More information required for a decision
364 | Wastewater | Vol 1 | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe | No action
365 | Wastewater | Vol 1 | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. | Noted: no action required | Reviewed and Noted only | General | No action
366 | Wastewater | Vol 1 | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | No action
367 | Wastewater | Vol 1 | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe | More information required for a decision
368 | Wastewater | Vol 1 | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? | Included | The intent of the schema is to record what has been contructed at practical completion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | No action
369 | Wastewater | Vol 1 | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe | More information required for a decision
370 | Wastewater | Vol 1 | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General | More information required for a decision
371 | Stormwater | Vol 1 & Vol 2 | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General | More information required for a decision
372 | 3-Waters & Buildings | Vol 1 & Vol 2 | What are the timeframes for this being adopted as mandatory? | Noted: no action required | Business Case. | General | No action
373 | 3-Waters & Buildings | Vol 1 & Vol 2 | Will there be a further round of submissions / comments? | Noted: no action required | Yes. Seminars in November. | N/A | No action
374 | 3-Waters & Buildings | Vol 1 & Vol 2 | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Included | Mandatory, Optimal, Optional will be discussed with the sectors and addressed during the pilot implementation phase | General | More information required for a decision | [7 empty] | No further action
375 | 3-Waters & Buildings | Vol 1 & Vol 2 | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General | No action
376 | 3-Waters & Buildings | Vol 1 & Vol 2 | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference | Sector discussion
377 | 3-Waters & Buildings | Vol 1 & Vol 2 | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Noted: no action required | Treatment is not included | No Specific Reference | No action
378 | 3-Waters & Buildings | Vol 1 & Vol 2 | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | Included | Asset Classifications have been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
379 | 3-Waters & Buildings | Vol 1 & Vol 2 | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | Noted: no action required | Included in Instruments | Instruments | No action
380 | 3-Waters & Buildings | Vol 1 & Vol 2 | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | Noted: no action required | Separate sections of data cohorts | General | No action
381 | 3-Waters & Buildings | Vol 1 & Vol 2 | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | Sector Discussion | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments | More information required for a decision |  |  |  | Refer to 3 Waters |  | Closed in 3 waters |  | Refer to 3 Waters
382 | 3-Waters & Buildings | Vol 1 & Vol 2 | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | Included | Statement noted. To be actioned. | General | Change made document updated
383 | 3-Waters & Buildings | Vol 1 & Vol 2 | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well | No action |  |  |  | Refer to 3 Waters |  | Closed in 3 waters
384 | 3-Waters & Buildings | Vol 1 & Vol 2 | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | Included | Suggestion adopted Standards will be updated | 1.5 Deliverables | Change made document updated
385 | 3-Waters & Buildings | Vol 1 & Vol 2 | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Sector Discussion | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | More information required for a decision |  |  |  | This is an output from the pilots, as agreed at the workshops |  |  |  | No further action
386 | Wastewater | Vol 1 | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. | Noted: no action required | Reviewed and Noted only | General | No action
387 | Wastewater | Vol 1 | a standardised approach to the collation of data relating to As Built (As Constructed) asset information | Noted: no action required | Reviewed and Noted only | Abstract | No action
388 | Wastewater | Vol 1 | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. | Included | Will consdider for final edit - happy to add in. | Executive Summary | Haydn
389 | Potable water | Vol 1 | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. | Sector Discussion | Need recommended maximum attachment size | 1.5 Deliverables | More information required for a decision
390 | Potable water | Vol 1 | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. | 2.1.1 Accuracy Requirements for Locating Assets | No action
391 | Potable water | Vol 1 | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. | Included | picked up previously | 2.1.2 Projections and Datums | Change made document updated
392 | Potable water | Vol 1 | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. | Noted: no action required | agreed, but per pipe section, there is a from-node and a to-node, one of each. | 2.4.4 Node | No action
393 | Potable water | Vol 1 | We split pipes when there is a valve or hydrant on them. While other councils may not | Noted: no action required | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. | 2.4.5 Pipe | No action
394 | Potable water | Vol 1 | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. | Sector Discussion | need examples | 2.4.5 Pipe | More information required for a decision
395 | Potable water | Vol 1 | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | No action
396 | Potable water | Vol 1 | A lot of the attributes seem to be duplicated | Noted: no action required | attributes are all different | 2.5.2 Pump | No action
397 | Potable water | Vol 1 | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. | Included | agreed, diagram will be corrected | 2.7.1 Instruments | No action
398 | 3-Waters | Vol 1 & Vol 2 | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | Included | Updated | General | Change made document updated
399 | 3-Waters | Vol 1 & Vol 2 | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | Included | Updated | General | Change made document updated
400 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General | No action
401 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Noted: no action required | This is a metadata standard not asset management standards. | General | No action
402 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Included | Updated | General | Change made document updated
403 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | Noted: no action required | These are differentr in some cases / in others they are not, not the same definitions across sectors | General | No action
404 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | Noted: no action required | Updated and acknowledge that this will be upto the individual organisation to address | 1.5 Deliverables | No action
405 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | No action
406 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | Noted: no action required | References to be removed. | No Specific Reference | No action
407 | 3-Waters | Vol 1 & Vol 2 | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Noted: no action required | Treatment facilities are not included as part of these standards | No Specific Reference | No action
408 | 3-Waters | Vol 1 & Vol 2 | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Noted: no action required | Out of scope. However resourse consents maybe recorded against the specifc works for each project. | No Specific Reference | No action
409 | 3-Waters | Vol 1 & Vol 2 | Content: • Land – no parameters are set for the recoding of land information. | Excluded | Out of scope. | No Specific Reference | No action
410 | 3-Waters | Vol 1 & Vol 2 | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | No action
411 | 3-Waters | Vol 1 & Vol 2 | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | No action
412 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Noted: no action required | Detailed in business case only | No Specific Reference | No action
413 | 3-Waters | Vol 1 & Vol 2 | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Noted: no action required | Applies to all assets. Mandatory and optional fields to be determined during implementation. The benefits to costs covered in business case. | General | No action
414 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Noted: no action required | Covered in business case. | General | No action
415 | 3-Waters | Vol 1 & Vol 2 | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Noted: no action required | Covered in business case. | General | No action
416 | 3-Waters | Vol 1 & Vol 2 | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General | No action
417 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | Noted: no action required | Noted Will be further addressed during the pilot implementation phase | General | No action
418 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | Noted: no action required | This is not within the scope of these standards | General | No action
419 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | Noted: no action required | This is not within the scope of these standards | General | No action
420 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | No action
421 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
422 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Noted: no action required | Included in the draft Standards | General | No action
424 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums | No action
425 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Included | Included in the draft Standards | 2.1.2 Projections and Datums | Change made document updated
426 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Included | Included in the draft Standards Asset categories included as guidance for each organisation | General | No action
427 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure | No action
428 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | Included | Included in the draft Standards | General | No action
429 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Included | Included in the draft standards | General | No action
430 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General | No action
431 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference | No action
432 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Included | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General | No action
433 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes | No action
434 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) | General for Pipes | More information required for a decision
435 | 3-Waters | Vol 1 & Vol 2 | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings | No action
436 | 3-Waters | Vol 1 & Vol 2 | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General | No action
437 | 3-Waters | Vol 1 & Vol 2 | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes | No action
438 | 3-Waters | Vol 1 & Vol 2 | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | Sector Discussion | More information is required to inform a way forward | General for Nodes | More information required for a decision
439 | 3-Waters | Vol 1 & Vol 2 | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure | No action
440 | 3-Waters | Vol 1 & Vol 2 | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General | No action
441 | 3-Waters | Vol 1 & Vol 2 | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General | No action
442 | 3-Waters | Vol 1 & Vol 2 | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure | No action
443 | 3-Waters | Vol 1 & Vol 2 | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles | No action
444 | 3-Waters | Vol 1 & Vol 2 | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW | No action
445 | 3-Waters | Vol 1 & Vol 2 | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | Noted: no action required | Data collection is out of scope from these standards | General | No action
446 | 3-Waters | Vol 1 & Vol 2 | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference
447 | 3-Waters | Vol 1 & Vol 2 | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node | No action
448 | 3-Waters | Vol 1 & Vol 2 | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Excluded | Junctions / end points are not assets. | General | No action
449 | 3-Waters | Vol 1 & Vol 2 | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Noted: no action required | Junctions / end points are not assets. | No Specific Reference | No action
450 | 3-Waters | Vol 1 & Vol 2 | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
451 | 3-Waters | Vol 1 & Vol 2 | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | Noted: no action required | The ID proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes | No action
452 | 3-Waters | Vol 1 & Vol 2 | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | Included | Included in the draft standards Code lists have been supplied | General | Change made document updated
453 | 3-Waters | Vol 1 & Vol 2 | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Noted: no action required | Action on volume 1 and business case. The definition of a node has been reviewed and clarified | General | No action
454 | 3-Waters | Vol 1 & Vol 2 | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Noted: no action required | Statement noted. | General | No action
455 | 3-Waters | Vol 1 & Vol 2 | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Noted: no action required | Statement noted. Data transfer is not in scope. | No Specific Reference | No action
456 | 3-Waters | Vol 1 & Vol 2 | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference | No action
457 | 3-Waters | Vol 1 & Vol 2 | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | Noted: no action required | 1. Completed 2. Further information required from respondent. Codelists are now included 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General | No action
458 | 3-Waters & Buildings | Vol 1 & Vol 2 | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | Noted: no action required | Statement noted. Consideration for Volume 1. | General | No action
459 | 3-Waters & Buildings | Vol 1 & Vol 2 | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | Noted: no action required | Statement noted. No action required. | General | No action
460 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | Noted: no action required | Statement noted. No action required. | General | No action
461 | 3-Waters & Buildings | Vol 1 & Vol 2 | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | Noted: no action required | Statement noted. No action required. | General | No action
462 | 3-Waters & Buildings | Vol 1 & Vol 2 | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | Noted: no action required | Business case. | General | No action
463 | 3-Waters | Vol 1 & Vol 2 | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | Noted: no action required | Statement noted. | General | No action
464 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
465 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Included | These inconsistencies have been actioned in the draft standards | General | No action
466 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | These inconsistencies have been actioned in the draft standards | General | No action
467 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | Sector Discussion | To discuss | No Specific Reference | More information required for a decision
468 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | Noted: no action required | Action for volume 1. Codelists have been included defining the types of assets covered in each asset class. These codelists are dynamic in nature and over time will be added to as new materials, products etc enter the market | 1.7 Heirarchy | No action
469 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Sector Discussion | Tables to be discussed in Final Version Vol 1 | No Specific Reference | More information required for a decision Tunnels have been included
470 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy | No action
471 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
472 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
473 | 3-Waters | Vol 1 & Vol 2 | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Included | Tables will be referenced in Final Versions | General | No action
474 | 3-Waters | Vol 1 & Vol 2 | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | No action
475 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Noted: no action required | Statement Noted. Business case. | No Specific Reference | No action
476 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Noted: no action required | Statement noted. | No Specific Reference | No action
477 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Noted: no action required | Business case. | No Specific Reference | No action
478 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference | No action
479 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Noted: no action required | Implenmentation is not within scope | No Specific Reference | No action
480 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Noted: no action required | Business Case | No Specific Reference | No action
481 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Noted: no action required | Business Case. | No Specific Reference | No action
482 | 3-Waters | Vol 1 & Vol 2 | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
483 | 3-Waters | Vol 1 & Vol 2 | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
484 | 3-Waters | Vol 1 & Vol 2 | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | Included | Included in the draft Standards | General | No action
485 | 3-Waters | Vol 1 & Vol 2 | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | No action
486 | 3-Waters | Vol 1 & Vol 2 | The current drafts need additional work at the hierarchy level and better definition / guidance. | Sector Discussion | Asset Classifications have been defined in the Standards | General | More information required for a decision
487 | 3-Waters | Vol 1 & Vol 2 | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Included | This is about context for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | Further discussion with Sector
488 | 3-Waters | Vol 1 & Vol 2 | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | Included | Included in the draft Standards | General | change made document updated
489 | Potable water | Vol 1 | savvy - edit out slang words like this | Included | removed in current version | Executive Summary | Change made document updated
490 | Potable water | Vol 1 | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? | Included | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. | In Summary | Change made document updated
491 | Potable water | Vol 1 | Consultants - Replace by organisations? | Included | Term consultants now included in glossary. | 1.1 Register | Change made document updated
492 | Potable water | Vol 1 | Again, misuse of term 'consultants. edit through the document to correct this. | Included | Term consultants now included in glossary. | 1.4 Disclaimer | Change made document updated
493 | Potable water | Vol 1 | Is this still used? | Noted: no action required | optional supply | 1.5 Deliverables | No action
494 | Potable water | Vol 1 | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? | Noted: no action required | both schemata and schemas are both acceptible words for the plural of schema. | 1.6 Global Schemas | No action
495 | Potable water | Vol 1 | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? | Noted: no action required | This is not within the remit of the standards | No Specific Reference | No action
496 | Potable water | Vol 1 | how can the analytics standardise the data that has already been standardised? | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | No action
497 | Potable water | Vol 1 | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference | No action
498 | Potable water | Vol 1 | i.e. not fixed and topics can be added? | Included | Agree, asset classes can be added as agreed to | 1.8 Theme Structure | No action
499 | Potable water | Vol 1 | what does this mean? No? but no Y for yes? | Included | N changed to N/A | 1.9 Data Principles | Change made document updated
500 | Potable water | Vol 1 | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.1.1 Accuracy Requirements for Locating Assets | No action
501 | Potable water | Vol 1 | precisely? 'well' is a subjective term | Included | changed | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
502 | Potable water | Vol 1 | no 's' | Sector Discussion | cannot identify | 2.1.1 Accuracy Requirements for Locating Assets | More information required for a decision
503 | Potable water | Vol 1 | change 'issues' to 'risks' throughout document | Noted: no action required | not a risk but an issue | 2.1.10 Common Attributes | No action
504 | Potable water | Vol 1 | Well - change to 'bore' | Noted: no action required | term agreed to by TWG | 2.3.4 Well | No action
505 | Potable water | Vol 1 | does this create a 'node'/ if not then it is a problem for modelling. | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | More information required for a decision
506 | Potable water | Vol 1 | how is a locator or IP cable taped to the pipe represented? | Sector Discussion | Need more information and example | 2.4.5 Pipe | More information required for a decision
507 | Potable water | Vol 1 | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | No action
508 | Potable water | Vol 1 | Is a backflow preventer a mechanical equipment asset or a valve/ | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment | More information required for a decision
509 | Potable water | Vol 1 | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure | No action
510 | Potable water | Vol 1 | this could be much larger with additional definitions e.g.. 'trunk main' | Noted: no action required | Codelists are dynamic and wil expand over time | Glossary | No action
511 | 3-Waters | Vol 1 & Vol 2 | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
512 | 3-Waters | Vol 1 & Vol 2 | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
513 | 3-Waters | Vol 1 & Vol 2 | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
514 | 3-Waters | Vol 1 & Vol 2 | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | Noted: no action required | Volume 2 is now complete | No Specific Reference | No action
515 | 3-Waters | Vol 1 & Vol 2 | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General | No action
516 | 3-Waters | Vol 1 & Vol 2 | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Sector Discussion | Included in the draft Standards Asset Classes included that are relevant to each network. These can be added to over time. The pilot implementation phase will be used as a guide | 1.7 Heirarchy | More information required for a decision
517 | 3-Waters | Vol 1 & Vol 2 | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | No action
518 | 3-Waters | Vol 1 & Vol 2 | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Included | Tables will be referenced in Final Versions However it is upto each organisation to determine the most approapriate way to create these links based on their systems | General | No action
519 | 3-Waters | Vol 1 & Vol 2 | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
520 | 3-Waters | Vol 1 & Vol 2 | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
521 | 3-Waters | Vol 1 | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General | No action
522 | 3-Waters | Vol 1 | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. | Noted: no action required | Service level performance is included in Volume 2 | General | No action
523 | 3-Waters | Vol 1 | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes | More information required for a decision
524 | 3-Waters | Vol 1 | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
525 | 3-Waters | Vol 1 | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. | Noted: no action required | Please refer to Project and common data | General | No action
526 | 3-Waters | Vol 1 | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset owners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
527 | 3-Waters | Vol 1 | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes | No action
528 | 3-Waters | Vol 1 | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
529 | 3-Waters | Vol 1 | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. | Sector Discussion | More information is required to inform a way forward | General for Pump Station | More information required for a decision
530 | Stormwater | Vol 1 | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. | Noted: no action required | This will be catered for through recording the "Source" | General | No action
531 | Stormwater | Vol 1 | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. | Included | This is a derivation for Volume 3, including precision of survey data | General | No action
532 | Stormwater | Vol 1 | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. | Included | Now normalised and standardsed with Metaconnect | General | No action
533 | Stormwater | Vol 1 | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General | No action
534 | Stormwater | Vol 1 | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General | More information required for a decision
535 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure | No action
536 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). | Included | Already incorporated into the table | 2.3.1 Containment Structure | No action
537 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure | No action
538 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure | No action
539 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure | No action
540 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure | More information required for a decision
541 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall | More information required for a decision
542 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | No action
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment | More information required for a decision
544 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber | No action
545 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | Change made document updated
546 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber | More information required for a decision
547 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | No action
548 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision
549 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber | More information required for a decision
550 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision
551 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. | Sector Discussion | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | More information required for a decision
552 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). | Noted: no action required | Please refer to comment above | 2.4.2 Channels | No action
553 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. | Sector Discussion | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | More information required for a decision
554 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | No action
555 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe | No action
556 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | Haydn
557 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | Change made document updated
558 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe | More information required for a decision
559 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | No action
560 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | No action
561 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? | Included | yes in Volume 2 | 2.4.4 Pipe | No action
562 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | Change made document updated
563 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe | More information required for a decision
564 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). | Noted: no action required | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station | No action
565 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station | No action
566 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. | Included | Attribute fields are included in the Pump asset class for motors. Please review and provide details of additional | 2.5.2 Pump | No action
567 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | No action
568 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. | Sector Discussion | Will include for ratification by the reviewers. | 2.5.2 Pump | New attribute proposed | Trigger level
569 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve | More information required for a decision
570 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | No action
571 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve | No action
572 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment | No action
573 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | Change made document updated
574 | Potable water | Vol 1 | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date | Noted: no action required | Reviewed and Noted only | General | No action
575 | Potable water | Vol 1 | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General | New Code List proposed | Health & Safety Type
576 | Potable water | Vol 1 | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General | More information required for a decision
577 | Potable water | Vol 1 | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) | Noted: no action required | 10 character fields have been adopted to allow for expansion | General | No action
578 | Potable water | Vol 1 | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General | More information required for a decision
579 | Potable water | Vol 1 | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. | Sector Discussion | Need more information and example | General | More information required for a decision
580 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). | Sector Discussion | Need more information and example | 2.3.1 Containment Structure | More information required for a decision
581 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
582 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | No action
583 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | New Code List proposed | Burial Status Above ground Below ground Partially buried
584 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure | No action
585 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure | No action
586 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
587 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
588 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
589 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
590 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision
591 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | No action
592 | Potable water | Vol 1 | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment | No action
593 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL a. Include Ground Water Level | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well | No action
594 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL b. Resource Consent number | Included | Included in Project Attributes | 2.3.4 Well | No action
595 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading | Sector Discussion | Code lists for NZDWS could be included - for discussion | 2.3.4 Well | More information required for a decision
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | More information required for a decision
597 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed | Manufacturer
598 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | No action
599 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. | Included | Agreed | 2.4.3 Fitting | Change made document updated
600 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting | More information required for a decision
601 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe | New Asset Class proposed Detail of data requirements needed | Support Structures
602 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. | 2.4.5 Pipe | No action
603 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | No action
604 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. | Included | Already catered for | 2.4.5 Pipe | No action
605 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe | No action
606 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe | No action
607 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | No action
608 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. | Included | change in all documents | 2.4.5 Pipe | Change made document updated
609 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter | Included | removed nom_Bore | 2.4.5 Pipe | Removal of attribute proposed Have marked for removal in documents
610 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe | More information required for a decision
611 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe | More information required for a decision
612 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision
613 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision
614 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision
615 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber | More information required for a decision
616 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | More information required for a decision
617 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | New attribute proposed | Portable generator (Y/N)
618 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | New attribute proposed | Calculation
619 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve | More information required for a decision
620 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve | New Code List proposed | Valve Control & Automatic Control
621 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. | Sector Discussion | see 00620 | 2.5.3 Valve | New Code List proposed | Valve Power
622 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
623 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve | More information required for a decision
624 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | No action
625 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection
626 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
627 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Incoming Pressure
628 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Outgoing Pressure
629 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Headloss
630 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE l. Valve mechanism code list should be similar to: BFL Butterfly DIA Diaphragm SLC Sluice GAT Gate BAL Ball KNF Knifegate DAV Double air FLP Flap gate NED Needle SAV Single air SND Solenoid WSC Check PRV Pressure reducing RLV Pressure relief | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Mechanism Butterfly Diaphragm Sluice Gate Ball Knifegate Double air Flap gate Needle Single air Solenoid Check Pressure reducing Pressure relief
631 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow
632 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Include attribute fields describing how the pump is powered - electrical, diesel, petrol. | Sector Discussion | Does this relate to the motor or the pump? To be compared to the attributes of the motor | 2.5.2 Pump | More information required for a decision
633 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump | New attribute proposed | Pump oreintation
634 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP c. “Actual pump rate” will at times be meaningless because of Variable Speed Drive (VSD) pumps, that can run at different speeds. This field is therefore either irrelevant for VSD, although it may be an eventual ‘input’ of actual data from control systems. | Noted: no action required | Reviewed and Noted only | 2.5.2 Pump | No action
635 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty end date, Purchase date to be reviewed. | 2.5.1 Equipment | More information required for a decision
636 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. Include Capitalized cost as well as purchase cost | Included | ODRC / ORC / RC are included | 2.5.1 Equipment | No action
637 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT c. The abbreviated and full attribute names contained in this table are not related to each other (this is possible a typographical error). | Noted: no action required | Resolved in updated version | 2.5.1 Equipment | No action
638 | Potable water | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. An attribute field with an ability to include a SCADA reference should be included. | Noted: no action required | Refer to Telemetry | 2.5.1 Equipment | No action
639 | Potable water | Vol 1 | Asset Class: Electrical Asset - CABLING a. Ductwork poses a tricky question because it is separate from cabling. Ductwork can be a part of the structure, and can carry many cables. If it is going to be recorded, Ductwork needs to be an asset class in its own right. | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision
640 | Potable water | Vol 1 | Asset Class: Instrumentation - INSTRUMENTS a. SCADA and RTU (controllers) are not instruments, because they do not measure variables. Include them under electrical equipment. | Included | Reviewed and Noted for Inclusion | 2.7.1 Instruments | Change made document updated
641 | Wastewater | Vol 1 | All Asset Classes a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Will ensure that they are applied. | General | Change made document updated
642 | Wastewater | Vol 1 | All Asset Classes b. Missing asset classes: There are a number of missing asset classes in the Wastewater Standard – including “Containment Structures” and “Tunnels”. Wellington Water has 23 containment structures for Wastewater, which is material in terms of asset renewal. | Sector Discussion | Additional Assets and attributes will be added to final version | General | More information required for a decision
643 | Wastewater | Vol 1 | All Asset Classes c. It was uncertain how the ‘crossover’ between the Wastewater and Stormwater network is managed within the Standard (including weirs). | Noted: no action required | Otherwise please be specific about the uncertainty. | General | No action
644 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. A definition may be required in relation to “relative level”. Relationship of ladders to access chamber; H&S attributes may be required, as ladders need to be certified. Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. This should be considered for inclusion in Volume 2. | Included | Include H&S Attributes | 2.3.1 Access Chamber | Haydn
645 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. Vegetation should not form part of this asset class data attribute for the Wastewater network! | Sector Discussion | to be discussed with the TWG | 2.3.2 Channel | More information required for a decision
646 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b. Is this really an ‘asset class’ for Wastewater (open sewers?) | Noted: no action required | If they do not exist then this asset class will not be used | 2.3.2 Channel | No action
647 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. Generally felt to be a ‘solid’ set of data attributes related to pipes. | Noted: no action required | Reviewed and Noted only | 2.3.4 Pipe | No action
648 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. Is there scope for a new field called “expected remaining life” based on observations? | Included | Remaining life is 'expected', observed or otherwise (e.g. calculated) - related to intervention type | 2.3.4 Pipe | Haydn
649 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. How are ‘pipe supports’ treated within the Standard? | Sector Discussion | Please provide examples of the types of supports that are used | 2.3.4 Pipe | More information required for a decision
650 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. The “Material Description “ field contents need to be set at the correct level – a significant impact on design life results between different materials such as uPVC, mPVC and oPVC, MDPE, HDPE and HPPE | Included | Material is a mandatory attribute | 2.3.4 Pipe | No action
651 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Soil Type should also be captured as part of this Standard (impacts design life) and used to inform a wider geospatial dataset. We need to remember that a pipe may cross several soil types. | Sector Discussion | Was previously discussed and rejected by the TWG | 2.3.4 Pipe | Change made document updated
652 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Surface Material should be recorded as part of this Standard – impacts structural composition. We need to remember that this field must be an updatable attribute based on non-3W observations. Pipes will also cross several different surface material | Included | Add Surface Material | 2.3.4 Pipe | New attribute & associated Code List proposed | Surface Material Surface Material Type
653 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Included | This is a geospatial layer and can attribute accordingly | 2.3.4 Pipe | No action
654 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. In general, the focus group thought this was a well thought out set of attributes associated with Pump Stations. | Noted: no action required | Reviewed and Noted only | 2.3.5 Pump Station | No action
655 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Attributes related to power supply are important; elements of the “electrical” asset class are related to the pump station (see comments in section 2.9 related to the parent-child relationship inherent in pump stations). Attributes include (at least) an ICP number. | Included | Already included. | 2.3.5 Pump Station | No action
656 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION c. The Standard is silent on elements related to “Access” and/or “Easements” for this asset class. | Noted: no action required | Correct. Volume 1 focusses on recording asset data at practical completion | 2.3.5 Pump Station | No action
657 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station | More information required for a decision
658 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION e. The cost attribute is associated with a particular construction date – ie, the pump station is assumed to be ‘static’. This is not likely. (again – may relate to parent-child relationship of pump station to assets it contains). | Included | ODRC / ORC / RC are included | 2.3.5 Pump Station | No action
659 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION f. Safe working limits are a legal requirement  does this form part of the building standard? | Included | Depth is recorded | 2.3.5 Pump Station | No action
660 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION g. “Building Owner” could be split between multiple owners | Included | Owner vs manager fields available in the draft standard Catenate multiple owners in field Buildings are separate assets, see buildings | 2.3.5 Pump Station | More information required for a decision
661 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Elements of a pump may be regarded as a distinct asset – such as motors, impellors, control system, cabling. The attributes of a pump relate to the pump type – this field may need further expansion and/or definition. | Excluded | Detailed drawing and component information is provided in manuals on handover - a reference attribute is included | 2.4.2 Pump | No action
662 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. The line between a pump asset and maintenance is not discussed within the Standard – even though this could change the asset function. | Sector Discussion | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | 2.4.2 Pump | Change made document updated
663 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. The data attributes within this section seem to relate entirely to Electrical Equipment; this does not make sense for this asset class. For example, the “Serial #” field has a description related to “protective material”. | Included | To be resolved in all 3W tables. | 2.4.1 Equipment | More information required for a decision
664 | Wastewater | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. “Risk” should be a key field – with a strong relationship to a relevant Volume 2 table. Safety in Design elements (and residual risk) should form part of this also. | Noted: no action required | Links are not within the remit of these standards - this is an analytical element | 2.4.1 Equipment | No action
665 | 3-Waters | Vol 2 | Data Relationships: Linkages shown in charts between Schema are inconsistent. For example, the “Repairs & Maintenance” schema is shown as interfacing to “As-constructed” and “Condition” schemas. But other Schemas have “Repairs & Maintenance” as an interface. For example, “Financial Performance” and “Demand” both have “Repairs & Maintenance” as an interface. If interlinkages are not shown to be consistent then the validity of the Standard can be questioned. This aligns with the overall statement made in section 1.9 of this document. | Sector Discussion | Relationships are explained in depth in Vol 2 | No Specific Reference | No action
666 | 3-Waters | Vol 2 | 2. Project Area: The project area artefact could apply to any business project over the 3 waters and not simply a new subdivision reticulation e.g. new facility or augmentation of WW or WS plant, refurbishment of upgrading of network etc. Understanding how projects/investments are delivered and perform is an important AM capability. The metadata schema should not constrain how assets are managed to meet desired outcomes. | Noted: no action required | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | No Specific Reference | No action
667 | 3-Waters | Vol 2 | 3. Delivery Risk: In order to generate valid information and outcomes the recording of data in a schema for national reporting will require consistency both within an organisation and between organisations over time. This should be recognised as a risk to the successful delivery of benefits by the Data Standard. | Noted: no action required | Delivery risk is a risk for Volume 3 - Methodology | 1.4.2 Intervention Methodologies (Volume 3) | No action
668 | 3-Waters | Vol 2 | 4. Units of measure in asset management would include flow, pressure, time - these are not in the Code list 1, but these and other units are referenced throughout the schemas. Note that different flow and pressure measurement units will apply to different assets or uses. | Included | Amended Code list | Table 2: Water Supply Service Attributes | No action
669 | 3-Waters | Vol 2 | 5. Date Range & Traceability: Similar to the comments made in section 2.1 related to Volume 1, key fields in Volume 2 should be auditable, giving the ability to track when changes are made, why and by whom. While a function of an information system, the requirement for such should be included in a metadata standard. | Sector Discussion | More information is required tofully iundertstand this feedback, but systems business rules (e.g. date ranges) are the place for defining extents, not these standards Assessors are included Data Table 1: Condition Attributes Assessor_N Assessor Name text | No Specific Reference | More information required for a decision
670 | 3-Waters | Vol 2 | 6. Code lists provided for Volume 2 generally require more work to develop consistent, full and meaningful references for use. We note that code lists have not been provided for Volume 1. | Included | Code lists have been updated for comment. | List of Code Lists | No action
671 | 3-Waters | Vol 2 | 7. Depreciation Data: Depreciation is an indicator of loss of service potential. Replacement value must reflect the true value of replacement in the current environment – which may be different to the environment at original installation. Changes to value and the rate of deterioration may be due to specific changes to asset attributes and environment over time. There must be fields to link changes to time and place. | Noted: no action required | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Code List 47: Financial Performance Metrics | No action
672 | 3-Waters | Vol 2 | 8. Lack of observation schema: As noted in section 4.4(a), the lack of an “Observations” schema hampers the ability for observation to inform multiple data schemas – such as condition or updates of asset attributes in the as-built schema. | Noted: no action required | Statement noted. Observations will feed into the attributes. | Data Table 1: Condition Attributes | No action
673 | 3-Waters | Vol 2 | 9. H&S Data: Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. | Included | Now included in Risk attributes Con_Rat_HS Consequence Rating Health and Safety | Table 7: Risk Attributes | More information required for a decision
674 | 3-Waters | Vol 2 | Condition a. Condition data is relevant for a range of decisions and processes in the asset lifecycle, most particularly around renewals, risk and valuations. The following comments consider these aspects but also apply to many of the other processes in some degree. | Included | Statement noted. | 2.2 Condition Schema
675 | 3-Waters | Vol 2 | Condition b. The inclusion of a calculated remaining useful life within the condition schema is fundamentally flawed because it does not account for other relevant asset life determining factors. Examples of such include criticality, demand, performance, optimisation and the asset’s operating environment. By linking condition grade directly to remaining useful life, the schema pre-supposes an end of life or replacement date decision. These conclusions should only be made while considering the wider factors as above. Noting this, Code List 6 linking condition grade to remaining useful life should be removed. | Sector Discussion | Let's discuss - these standards are not about decision-making - they are elements for decisionmaking - these standards define each of these elements. We are not suggesting you should make a decision on condition alone. But if your note is about definition of remaining useful life then let’s chat. | 2.2 Condition Schema | More information required for a decision
676 | 3-Waters | Vol 2 | Condition c. It is recommended that the schema be modified to take into account the level of confidence in condition grades. There is little or no recognition of the probabilistic nature of condition assessments and hence the confidence limits which apply to the grades. Any condition grade is made within a band of confidence at a point in time. The confidence level is relative to whether it is being applied to a subject asset or extrapolated to an asset group, and whether it is applied at the time of assessment or projected forward. | Noted: no action required | This is a calculable field, for example, stochasticity | No Specific Reference | No action
677 | 3-Waters | Vol 2 | Condition d. The basis of the interfaces with other schema (Table 5) is unclear and the linkages shown do not acknowledge the relationships between condition data and all other schema. Eg: i. Criticality determines priorities for condition data collection ii. Repairs and maintenance activities are a key potential source of condition data iii. Condition is indicative of likelihood of failure and hence helps determine risk iv. Service and financial performance are impacted by condition v. Demand and utilisation inform the criticality of an asset and hence priority for condition data collection. | Noted: no action required | These are analytical outputs of specific problems being solved. We can discuss | No Specific Reference | No action
678 | 3-Waters | Vol 2 | Condition e. Items included in the condition data attributes (Table 2) appear to be a mix of data at different levels of detail; some being at the assessment level and others at the observation level. Any hierarchy or relationship between these is not implied or explained however. The potential one-to-many linkages from asset to assessments and further to observations are not apparent. Any data required must be clarified in terms of how it relates to other data to enable practical processes for capture and storage. | Sector Discussion | Action: To be discussed with Wellington Water. | Data Table 1: Condition Attributes | More information required for a decision
679 | 3-Waters | Vol 2 | Condition f. The description of condition grades against physical deterioration (Code List 2) is a good approach however the terminology is inconsistent. Most descriptors but not all relate to asset failure. All should be described on the same basis to allow for consistent interpretation. “Asset failure” in this sense also requires definition and is unclear in the schema. | Included | Uniform terminology now applies | Code List 16: Condition Rating | No action
680 | 3-Waters | Vol 2 | Condition g. The condition grade types (Code List 3) are unclear and do not give any sense of the distinctions or relationships between structural, service, mean, peak and overall grades. | Included | Condition code lists (e.g. structural, exterior, interior) are now included in Vol 2 | Code List 16: Condition Rating | No action
681 | 3-Waters | Vol 2 | Condition h. The condition grade assessment methodologies (Code List 4) and assessment types (Code List 5) are extremely limited and do not capture many methodologies that are currently available and in use. Terminology is not consistent with the purpose of the list, ie; “Cut out” is a sampling methodology rather than an assessment type as listed. A cut out may be assessed visually, by destructive and/or non-destructive testing, or other means. Code lists 7 – 10 are similarly limited and the purpose and usage of which are unclear. | Sector Discussion | See code list | Code List 17: Condition Rating – Methodology | More information required for a decision
682 | 3-Waters | Vol 2 | Repairs and Maintenance a. The Proactive and Reactive Activity Type descriptions need additional clarification to minimise ambiguity. How should “impairment” be interpreted - breakdown, significant performance issue or just incipient failure only detectible with monitoring equipment (e.g. bearing vibration, thermographic image, etc)? Also “Scheduled” needs to exclude non-routine or one-off activities that are set to occur in the future. | Noted: no action required | See code list | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
683 | 3-Waters | Vol 2 | Repairs and Maintenance b. The schema does not support optimisation of maintenance tasks through RCM analyses or other FMECA based approaches. An example would be the need for a clear and unambiguous definition of asset function. This is not well covered in Part 1 attributes. Comment should be requested from an RCM practitioner. | Noted: no action required | Statement noted. This is not a maintenance management system. | No Specific Reference | No action
684 | 3-Waters | Vol 2 | Repairs and Maintenance c. Recording the “Image_ID” against activities does not cater for referencing other types of digital files. Suggest this optional attribute is made generic and capable of accepting hyperlinks to reference files in other systems. | Noted: no action required | This is an analytical requirement | No Specific Reference | No action
685 | 3-Waters | Vol 2 | Repairs and Maintenance d. Fail_Mode and Cause_Iss is important but must be specific to each asset type rather than generic across all assets. It’s not clear if this is the intention. | Noted: no action required | This is an analytical requirement and is matched to other elements (e.g. AssetID) to determine response | No Specific Reference | No action
686 | 3-Waters | Vol 2 | Repairs and Maintenance e. A key decision for every asset is to either run to failure or apply a scheduled maintenance/inspection plan. | Noted: no action required | This is an analytical requirement (i.e. both) | No Specific Reference | No action
687 | 3-Waters | Vol 2 | Repairs and Maintenance f. In Part 1 Condition Assessment Type is an asset attribute, but Condition is part of a different schema. Shouldn’t these go together to reflect the fact that the condition assessment approach may change over time? | Included | Yes, but in the analytical phase. | No Specific Reference | No action
688 | 3-Waters | Vol 2 | Repairs and Maintenance g. It isn’t clear how maintenance strategies are to be handled (i.e. managing maintenance work that has weekly/monthly/annual/ etc activities). AMIS functional requirements should be considered before fields like Recur and Recur_Cyc are established. | Noted: no action required | Standard is not intended to populate a maintenance plan. Code Lists are included to handle this requirement e.g. Recurrence Cycle | Code List 5: Recurrence Cycle Unit | No action
689 | 3-Waters | Vol 2 | Repairs and Maintenance h. Need quantity as well as cost information to be able to analyse trends and predict future costs. Need to record all resources – not restricted. | Noted: no action required | Code lists for quanitifying repairs included | Code List 6: Bases of Cost | New Code List from Working Group
690 | 3-Waters | Vol 2 | Repairs and Maintenance i. The combination of Activity Type, start date/time, end date/time does not appear to meet the requirements for DIA non-financial reporting for urgent/non-urgent callouts (i.e. need to separately record time to reach site and time to resolve issue). | Noted: no action required | Type of maintenance activity is included | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
691 | 3-Waters | Vol 2 | Repairs and Maintenance j. There needs to be a new Event Type similar to “Upgrade/Improvement”. Irrespective of the funding source (capital vs operational) assets need to have a full history of events recorded against them. If we exclude upgrades and rely solely on project registers to capture this information we make lifecycle management significantly more difficult. | Noted: no action required | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Code List 49: Description of Financial Performance Element | No action
692 | 3-Waters | Vol 2 | Repairs and Maintenance k. Why record overflows etc. in repairs and maintenance schema and not in the level of service? Overflows are recorded per financial year, different organisations have different financial years, is history recorded i.e. over time. Should other compliance activities i.e. RON and CDEM should also be coded. | Included | One is a record of the type event One is a record a service level e.g. overflows per year and an analytic | Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | No action
693 | 3-Waters | Vol 2 | Repairs and Maintenance l. Asset versus component issue can give rise to different design criteria and system performance i.e. a pump has a l/s design while a filer has (say) minimum pressure drop, but it is performing of the pumping station that is the issue. | Noted: no action required | Statement noted | No Specific Reference | No action
694 | 3-Waters | Vol 2 | Repairs and Maintenance m. Does not appear to allow for other investigation methods e.g. vibration analysis, DCVG results, thermal imaging, usage data analytics for identifying if an intervention is required. | Included | Code lists to be discussed against current code lists e.g. Condition (This is really a Volume 3 question) | Code List 17: Condition Rating – Methodology | No action
695 | 3-Waters | Vol 2 | Repairs and Maintenance n. As found and as left condition or status is useful for items like valves, could also apply to depth of cover, locks etc. | Included | Statement Noted: No action required. | No Specific Reference | No action
696 | 3-Waters | Vol 2 | Repairs and Maintenance o. Asset performance does not clearly link to key result areas or key performance indications set by organisations in the management of assets or demanded by consumers. | Sector Discussion | This is an anlytical question - discuss with sector | No Specific Reference | More information required for a decision
697 | 3-Waters | Vol 2 | Repairs and Maintenance p. Asset or service performance - it is not clear what is referred to or if this is consistent. | Sector Discussion | Section updated in Volume 2 | 5.4 Service Performance Schema | More information required for a decision
698 | 3-Waters | Vol 2 | Repairs and Maintenance q. How are components and soft parts etc linked to assets, is the lifecycle of O&M supported by this? | Noted: no action required | Component type is an attribute in the repair schema and captured under each asset. | 2.3.4 Components of Repairs, Maintenance and Operations | No action
699 | 3-Waters | Vol 2 | Repairs and Maintenance r. Benchmarking - same as identified in service levels schema, consistency is required for valid and useful outputs to be obtained. | Noted: no action required | Statement noted and agreed. | No Specific Reference | No action
700 | 3-Waters | Vol 2 | Repairs and Maintenance s. Outage duration - mandatory for all actions but what if no outage? Also what if the customers are reinstated over time ie 95% connected in 1 hour while the rest are out for days? Outage is linked to ' number of people' - this can be impossible to measure depending on each connection (as in an apartment block), would customer or property be a better measure. | Noted: no action required | Agreed. Then outage duration = 0. | No Specific Reference | No action
701 | 3-Waters | Vol 2 | Repairs and Maintenance t. Third party damage excluded from outage definition but included in repair schema as cause. | Included | Third Party attribute included | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
702 | 3-Waters | Vol 2 | Repairs and Maintenance u. Maintenance planning - focused on time based maintenance (elapsed), but could encompass operating hours or CBRM. A MMS would do a better job, would it be better not to specify these matters in the schema and just have an objective for an outcome based system in place. This could be applied throughout the data standard noting the issues with consistently in benchmarking. | Sector Discussion | Analytical elements included in standards to schieve this analytic | No Specific Reference | More information required for a decision
703 | 3-Waters | Vol 2 | Repairs and Maintenance v. It would be desirable to have costs for maintenance collected on an area/project basis for performance analysis. | Included | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | No Specific Reference | No action
704 | 3-Waters | Vol 2 | Repairs and Maintenance w. Should complaints be linked to an issue or root cause rather than an address or asset - this would enable better linking and development of appropriate solutions and priority setting than a collection of disparate reports. Also need to know the outcome of the assessment of a compliant ie internal plumbing, no issue found etc before an organisation make decisions on number of complaints. Option of an outcome based CRM system rather than data standard? | Included | Linking CRM information to asset information is not in scope These root cause examples in the code list are asset related interrogations for asset management purposes. | No Specific Reference | No action
705 | 3-Waters | Vol 2 | Utilisation a. Asset utilisation needs to consider the level of redundancy in the network or asset system required to achieve the desired overall level of risk. The proposed calculation of utilisation could work for an individual pump, but would be of little/no value for a trunk main network. It could easily be misinterpreted. | Included | Redundancy is include in the codelists in Vol 2 as an analytical attribute (see vulnerability). | Code List 43: Global Resilience Rating Elements | No action
706 | 3-Waters | Vol 2 | Utilisation b. Until the intervention methodologies are proposed for each of the 3 waters we find it difficult to understand what fields may or may not be wanted for this schema. | Noted: no action required | Statement noted. | 3.2.5 Code Lists
707 | 3-Waters | Vol 2 | Demand a. Demand applies to collections of assets. Why would you want to record demand against an individual asset such as a pipe or valve? | Included | This is an analytics requirement, but may no be required agaist all asset components. | No Specific Reference
708 | 3-Waters | Vol 2 | Demand b. The fields offered are very limiting in this schema and the use of demand needs to be thought through in more depth. | Noted: no action required | Demand Section has been updated in Volume 2 | 3.3 Demand Schema
709 | 3-Waters | Vol 2 | Demand c. Peak demand at a system level is not the sum of zone demands due to the diversity/averaging effect as the study area increases in size. Average demand at a system level is the sum of the zone demands. The schema does not seem to recognise this. | Noted: no action required | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler | Data Table 4: Demand Attributes | No action
710 | 3-Waters | Vol 2 | Demand d. What analytics would this schema (as is) be used to support? | Noted: no action required | Future connections on flow (population demand) | Code List 33: Demand – Measure | No action
711 | 3-Waters | Vol 2 | Demand e. Should this schema exist in an AMIS? | Noted: no action required | Yes | 3.3 Demand Schema | No action
712 | 3-Waters | Vol 2 | Criticality a. Criticality is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | No change | 4.3 Criticality Schema | No action
713 | 3-Waters | Vol 2 | Criticality b. The current approach to criticality from Wellington Water uses criticality as an equivalent to consequence in the evaluation of risk. To this effect the criteria for criticality that we have developed uses cumulative weighted impacts in combination with importance (exposure) factors to derive risk. My view is that the criticality descriptors offered in the standards are only one component of the consequence variable in the risk equation ie the exposure factor. To this extent it is puzzling to identify how criticality as described could be used in the evaluation of risk – given the subsequent content of the risk schema. | Noted: no action required | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | 4.3 Criticality Schema | No action
714 | 3-Waters | Vol 2 | Criticality c. For example if the renewal of a pipe was being considered wrt risk of failure – condition is an indicator of probability, the potential impacts could be social, environmental or financial loss and the exposure is measured by the number of people or the importance of the facility affected by the loss of service. | Noted: no action required | These are analytical inferences which are attributed in code in algorithms by attributes these standards define | No Specific Reference | No action
715 | 3-Waters | Vol 2 | Criticality d. Until worked examples are provided as to how the consultants perceive criticality being used for different decisions we struggle to see how the schema as offered would be useful or at best would have limited value. | Noted: no action required | Explanation found in criticality schema | 4.3 Criticality Schema | No action
716 | 3-Waters | Vol 2 | Criticality e. The code list 27,28,29 tables have some potential flaws in our view. i. Special facilities is too vague as a term for Code 5. Few utilities would have munition storage or critical data centres and in most cases data centres would have back up. How is this derived for example if it was potential damage from blowing up a munitions store, how would compare to an LPG centre or holding tanks containing solvents ii. For a water utility is a hospital really less critical than a data centre? iii. What happens when an asset services 3 or 4 hospitals iv. Where is economic loss factored into these tables – they seem to be very “government” centric v. We struggle to think that decision making using criticality for small towns of less than 5000 people would only ever have code 3 assets as their most important asset. Risk is about context and the context must consider the community and the economic scale of their investment. We do not believe one size fits all. | Noted: no action required | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. | No Specific Reference | No action
717 | 3-Waters | Vol 2 | Risk a. Risk is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | Statement noted. | No Specific Reference | No action
718 | 3-Waters | Vol 2 | Risk b. We assume that the risk schema is intended to facilitate risk management within water utilities. | Noted: no action required | Yes, and for buildings per the Biulding Standard | 4.4 Risk Schema | No action
719 | 3-Waters | Vol 2 | Risk c. We have reviewed this schema with respect to the principles of risk management as outlined in Section 3 of the guideline document for AS/NZS 31000:2009 | Noted: no action required | Noted | 4.4 Risk Schema | No action
720 | 3-Waters | Vol 2 | Risk d. In particular the schema as drafted inhibits the following principles: | Noted: no action required | Noted | 4.4 Risk Schema | No action
721 | 3-Waters | Vol 2 | Risk e. 3(g) Risk management is aligned with the organisations external and internal context and risk profile | Sector Discussion | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
722 | 3-Waters | Vol 2 | Risk f. 3(h) Risk management recognises the capabilities, perceptions, and intentions of external and internal people that can facilitate or hinder the achievement of the organisations objectives | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
723 | 3-Waters | Vol 2 | Risk g. 3(j) Risk management continually senses and responds to change. As external and internal events occur, context and knowledge change, monitoring and review of risks takes place, new risks emerge, some change, others disappear | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
724 | 3-Waters | Vol 2 | Risk h. To propose a specific risk matrix into a national standard seems to conflict with these basic principles | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct And any organisation can taylor the analysis to the local context | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
725 | 3-Waters | Vol 2 | Risk i. Although interdependencies between other schemas are stated it is difficult to extract how they would be used together. Risk, criticality and condition must be interconnected but there is no indication as to how the application of these schemas would allow this | Noted: no action required | This would depend on the problem being solved and the analytical approach in doing so | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
726 | 3-Waters | Vol 2 | Risk j. The suggestion that probability scales for different events and water types are the same is unhelpful in the absence of worked examples. Are there examples to demonstrate a sensible cross relationship for the use of probability scales in water supply and stormwater? | Noted: no action required | Unclear of what this means, but the scales are adaptive to event type, but specifiuc to asset type | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
727 | 3-Waters | Vol 2 | Risk k. Other than flood risk, how do you assess time based probabilities? The use of the word “time to time” or “in your career” will lead to subjective assessments that will simply promote inconsistent investment decisions rather than secure them. | Noted: no action required | Code list updated | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
728 | 3-Waters | Vol 2 | Risk l. We believe the contents of the fields that describe 1- 5 consequences should be omitted. A decision to occupy these fields for a national risk schema to derive nationally consistent approaches to risk will do exactly the opposite – it promotes subjective assessment and also directly contravenes the principles of risk management as described in AS/NZS 31000. | Noted: no action required | To discuss, see code lists | Code List 41: Consequence Rating | More information required for a decision
729 | 3-Waters | Vol 2 | Resilience NO schema offered However, we urge you to consider a fundamental question when addressing resilience for water utilities. Is the assessment of an assets’ resilience important or is it more important to assess the resilience of the service provided to customers on a national scale? We would suggest the latter, and therefore question the merits of offering a schema for asset resilience. If it is the latter, we also suggest that resilience is better attributed to customers rather than assets. | Included | Schema updated | 4.5 Resilience Schema | No action
730 | 3-Waters | Vol 2 | Design Performance This schema is not required. We don’t need evaluative criteria here. Attributes should be in the as built schema and actual performance should be in service performance. Table 12 in all volume 2 documents (sections 9.3) refer to the linkages with the resilience schema not the design performance | Noted: no action required | Let's discuss this is important. Design performance is different than Service Performance | 5.2 Design Performance Schema | More information required for a decision
731 | 3-Waters | Vol 2 | Financial Performance a. General comment – It would be interesting to know what is determined to be core data requirements with regards to the attributes. There is a large set of attributes to collect a large number would only be relevant to a small number of organisations. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | 5.3 Financial Performance Schema | No action
732 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
733 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
734 | 3-Waters | Vol 2 | Financial Performance c. Valuation date doesn’t seem to appear anywhere. | Noted: no action required | Included in standards | Data Table 10c: Valuation Attributes Details (Collected Level Indicated) | No action
735 | 3-Waters | Vol 2 | Financial Performance d. Linking the financial information e.g. revised asset lives with condition data. | Noted: no action required | Attributes included in standards, this is an analytical exercise | No Specific Reference | No action
736 | 3-Waters | Vol 2 | Financial Performance e. Terminology is not consistent with the Repairs and Maintenance schema e.g. reactive/planned/etc. | Noted: no action required | Now consistently applied | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
737 | 3-Waters | Vol 2 | Service Performance Level of service is recorded against individual assets, this may cause issues where service level is required from a network, facility, project, contract or organisational levels. These levels of service may not directly relate to asset parameters or the level of service at an asset may relate to another asset upstream (e.g. minimum pressure at a downstream point relates to the upstream network and pumps/regulators etc). Also levels of service are not static and these may change (this change may be the result of internal or external drivers). | Noted: no action required | These are analytical constructs from an individual assetID dataset. How consolidated into geographic units os for the specific analysis, e.g. network, zone, catchement etc. | No Specific Reference | No action
738 | 3-Waters | Vol 2 | Service Performance a. Benchmarking relies on the consistency of inputs. In order to generate valid information and outcomes the recording of data in a scheme for national reporting will require consistency in an organisation, between organisations and over time. Other national standards have shown there are issues with this approach, will the benefits of a metadata standard be realised (what are the risks and assumptions to the achievement of this benefit)? | Noted: no action required | This is a reference to standardised analytical approaches | No Specific Reference | No action
739 | 3-Waters | Vol 2 | Service Performance b. Residential demand figure, valid for industrial or commercial areas, how updated and how is history against assets recorded? | Noted: no action required | This is a reference to an analytical approach. E.g. ParcelID District Plan Zone type and connection demand (or Level of Service). | No Specific Reference | No action
740 | 3-Waters | Vol 2 | Service Performance c. Is it feasible that the same assessor (individual) is used for all items in each asset i.e. cultural significance and technical design and financial measures? | Noted: no action required | The same or multiple | No Specific Reference | No action
741 | 3-Waters | Vol 2 | Service Performance d. Consents compliance is linked to an asset when consents are typically given on an activity/facility - correct linkages and business processes will need to be established and implemented to ensure that compliance is achieved in light of asset changes. | Noted: no action required | Consent attributes are captured at property level which is not inconsistent with reporting at network/zone level - i.e. it is a spatial query between the two data sets. The attributes are specified for capturing asset detail in the standards | No Specific Reference | No action
742 | 3-Waters | Vol 2 | Service Performance e. Third party damage is excluded from service measures (interruptions) for water supply. This is a valid facet of AM, and the scheme has this included in repair and maintenance for WW assets. | Noted: no action required | Included in the Standards | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
743 | 3-Waters | Vol 2 | Service Performance f. MoH grading should be linked to a time the grade was awarded, and possibly should be greater than just a single field i.e. who assessed etc. We question the merit of this as a valid asset performance measure as it is always system based. | Noted: no action required | Included in the Standards | Data Table 11: Service Performance Attributes – Functional | No action
744 | 3-Waters | Vol 2 | Service Performance g. The fact a health and safety assessment has been carried out is interesting, but it is the results that are important (have the risks been addressed or are there outstanding issues etc) and there is no mention of this. | Noted: no action required | Included in the Standards | Table 2: Water Supply Service Attributes & Code List 41: Consequence Rating | No action
745 | 3-Waters | Vol 2 | Maintenance Planning i. Will the scheme provide an effective (and efficient) link to maintenance management systems that are in use currently? | Included | Yes that is the intention for the future. | No Specific Reference | No action
746 | 3-Waters | Vol 2 | Maintenance Planning ii. Are all costs collected at an asset level, won't different treatments give rise to different outcomes, ie, where are staff or contractor costs added to a facility, item or asset. Is maintenance carried out on assets as they exist or on notional assets? | Included | Application of costs will be at the discretion of the rganisation, but likely to be applied to a cohort of assets when being maintained | No Specific Reference | No action
747 | 3-Waters | Vol 2 | Operational Performance i. Actual performance should also be recorded as well as consent compliance - is water quality improving over time or always just inside the limit? | Included | Action: add in to schema (design performance? Service performance) | Data Table 9: Design Performance Attributes | No action
748 | 3-Waters | Vol 2 | Operational Performance ii. There is reference to LAWA framework – is this commonly used throughout the country? Would it be better to refer to the National Policy Statement or specific Regional rules as applicable for the authority? | Noted: no action required | All regional councils use LAWA | No Specific Reference | No action
749 | 3-Waters | Vol 2 | Valuation and depreciation Asset life versus economic/accounting life, does asset structure match the chart of accounts used by all organisations and applied in all business models i.e. contracted services? | Noted: no action required | Yes - there are appropriate fields for ODRC, ORC, RC and Forecast, Actual and Budget financial information in Finance Performance sections | Code List 47: Financial Performance Metrics | No action
750 | 3-Waters | Vol 2 | Planning for growth or decline i. Assets will need lifecycle stages not just in service ie proposed (linked to project), out of service, in store, abandoned, leased for F/O etc (assets can provide other services, not just those implicit in the standard) | Included | Discuss with Sector - to consider schema | No Specific Reference | Create a code list of service types as suggested here?
751 | 3-Waters | Vol 2 | Planning for growth or decline ii. Levels of service can change over time on different assets, this will need to be understood/recorded | Noted: no action required | Atributes to do this are included in the standards | No Specific Reference | No action
752 | Wastewater | Vol 1 | In talking about As Managed, I assume this is for how the councils handle data rather than how the data supplied by survey from the field, as these are two different worlds? | Sector Discussion | This is a discussion in the development of Volume 3 | No Specific Reference | No action
753 | Wastewater | Vol 1 | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this | Included | Reviewed and Noted for Inclusion Included as part of the Project Attributes table Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | More information required for a decision
754 | Wastewater | Vol 1 | There is increased risk to data accuracy in companies that are not working all the time with software projection transformations. As the client, I would always want to receive the data in it original projection and transfer it myself | Included | The requirement is for each company to deliver the data in the final projection and datum | 1.5 Deliverables | No action
755 | Wastewater | Vol 1 | Why is this BIM Enabled? Should this not be BIM Enabled/Geospatial Representation as these still hold and display 3d information. | Noted: no action required | Update, asset management and facility management systems do…. | 1.9 Data Principles | No action
756 | Wastewater | Vol 1 | This surely should be "current parcel" boundaries. Not sure as to what a title/property boundary is, as what is the definition of property (residence, address, rating unit, parcel(s))? Also, is this relevant?You want the assets to be shown in true survey location even if this shows them being constructed illegally through private property. | Sector Discussion | For analytical purposes Have added 'geographical units' code list | 2.1 Technical Reference Information | More information required for a decision
757 | Wastewater | Vol 1 | I believe this is how data should be stored, but supply of data should be as captured. By forcing this to the supplier you are increasing the risk of error, with groups that will only project data occasionally more likely to make mistakes | Noted: no action required | The intent of this is to educate the indutsry in what capability it will need | 2.1.2 Projections and Datums | No action
758 | Wastewater | Vol 1 | Why would you develop a new specification and then allow for it to be supplied in a historic format such as shapefile. This also means that the defined "text" geometry type cannot be supplied and instead would need to be changed to a point | Noted: no action required | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF | 2.1.7 Metadata Definitions | No action
759 | Wastewater | Vol 1 | Is this cost of the asset or cost of the asset plus installation? Is this standard cost of the recommended price of the asset, rather than any discounts were achieved? | Noted: no action required | All replacement costs include installation | 2.1.10 Common Attributes | No action
760 | Wastewater | Vol 1 | Is the central location the centre of access (i.e. manhole lid)or the centre of the structure? | Included | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. | 2.3.1 Access Chamber | Change made document updated
761 | Wastewater | Vol 1 | Pipe length shown here is neither the length of the digital pipe feature or the length of the real world feature, as you are not taking into account the "faux" pipe connectors angle. The middle pipe length here is very confusing! | Sector Discussion | Need more information for a way forward | 2.3.1 Access Chamber | More information required for a decision
762 | Wastewater | Vol 1 | Does this mean covered by dirt and not readily accessible or below ground level? | Noted: no action required | Below ground level | 2.3.3 Fitting | No action
763 | Wastewater | Vol 1 | What happens when two separate pipes are installed between access points (e.g. different material etc). Also there are examples were pipes may not have access chambers (as defined by this document). While that may be not best practice, it does occur. | Noted: no action required | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists | 2.3.4 Pipe | No action
764 | Wastewater | Vol 1 | Is this the digital length or the real world length? | Included | This is the real world length as described in the QA validation field. | 2.3.4 Pipe | No action
765 | Wastewater | Vol 1 | What does this mean? What level of accuracy is defined as a discrepancy? | Included | Changes made to wording to reflect tolerances used in practice ('field') | 2.7.2 Matching to Existing Infrastructure | Change made document updated
766 | Potable water | Vol 1 | Asset Group: To be consistent with Section 1.8 Should this heading be changed to "Asset Category" ? (Or in section 1.8 change "Asset Category" to "Asset Group" | Included | Changed to Asset Group for consistency. | 1.7 Heirarchy | Change made document updated
767 | Potable water | Vol 1 | Asset Type: To be consistent with Section 1.8, should this be changed to "Asset Class" | Included | Changed to Asset Class. | 1.7 Heirarchy | Change made document updated
768 | Potable water | Vol 1 | The paragraph refers to "Asset Types", yet table 1.8 does not reference "Asset Types", only "Asset Class". If these are not interchange in relation to meaning, then I suggest a explanation of "Asset Type" and "Asset Class" be documented within the document somewhere. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
769 | Potable water | Vol 1 | My personal preference is to utilize "Asset Class" as standard terminology, and replace any instances of "Asset Type" within the document if they are inferring the same meaning. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
770 | Potable water | Vol 1 | My personal preference is to utilize "Asset Category" as standard terminology, and replace any instances of "Asset Group" within document. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
771 | Potable water | Vol 1 | Conflicts with section 2.3.4 states that a well is to be represented as a polygon | Included | Changed to Polygon | 1.8 Theme Structure | Change made document updated
772 | Potable water | Vol 1 | Listed here as a guide, but each definition of the asset class states the required spatial representation. ie 2.3.1 states polygon feature. Therefore for clarity, should this table also list the requirement of the standard for each asset class? | Sector Discussion | More information is needed for a way forward | 1.9 Data Principles | More information required for a decision
773 | Potable water | Vol 1 | I am assuming this only for Geo-spatial attributes? (As there may be different sources utilized across multiple attributes.) If this is correct, can this be added for clarity in the contents column. | Included | Defined by organisation | 2.1.10 Common Attributes | No action
774 | Potable water | Vol 1 | If the data source changes, is there a need to keep a date history of the changes. | Noted: no action required | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. | 2.1.10 Common Attributes | No action
775 | Potable water | Vol 1 | Common Attributes for your consideration: (We currently have the following 3 attributes fields across all our assets) - Manufacturer (of asset) - Supplier (of asset) - Installed By (Contractor who installed asset) Fields to be utilized to identify failing assets due to manufacturer/supplier and potential faulty installation by a contractor. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
776 | Potable water | Vol 1 | This field should be allowed to be empty. What if there is no photographic references available. Flows through to Asset Class definitions | Sector Discussion | consider N/A as an appropriate response. | 2.1.10 Common Attributes | More information required for a decision
777 | Potable water | Vol 1 | Define "Asset Classes" and "Asset Types" | Included | Asset Classifications have been defined in the Standards | 2.2 Asset Categories | No action
778 | Potable water | Vol 1 | RL: Add a definition of RL in the "Glossary of Terms and Definitions" in the document (Reduced Level) "RL" acronym used in multiple places in the document. | Included | Included in Glossary | 2.3.2 Embankment, Glossary | Change made document updated
779 | Potable water | Vol 1 | No Type field for Wells. ie Type_Well Is this an oversight or genuinely not needed? | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision
780 | Potable water | Vol 1 | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision
781 | Potable water | Vol 1 | Seem to be missing Chamber Diameter, for circular access chambers. (As it states that AC_Length and AC_width only to be used if chamber is non circular) | Sector Discussion | Needs some rework and clarifiation. | 2.4.1 Access Chamber | More information required for a decision
782 | Potable water | Vol 1 | Potential Attribute: Manufacturer of Fitting | Included | Already identified and will be refered to TWG. | 2.4.3 Fitting | New attribute proposed | Manufacturer
783 | Potable water | Vol 1 | Water flow direction is not absolute. I am assuming this is for a network operating under "normal" conditions. | Included | Correct. For a network operating under 'normal' conditions. | 2.4.5 Pipe | No action
784 | Potable water | Vol 1 | For clarity, perhaps include a diagram showing an irregular access chamber. Refer to page 20 in Vol 1 of the waster water meta-data standard (V1.2 DRAFT A - 14 July 2016) | Sector Discussion | Completed | 2.4.6 Pump Station | Change made document updated
785 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrectly matched. EG Serial_No => Protective Material This is carried through to the Waste Water and Storm Water manuals. | Included | Resolved in current version. | 2.5.1 Equipment | Change made document updated
786 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrect matched. | Included | Resolved in current version | 2.5.1 Equipment | Change made document updated
787 | Potable water | Vol 1 | In our AMIS we are planning to utilize two fields to describe valves. Valve Type: Eg Isolation, Scour, Toby, Pressure Reducing, etc .. Valve Mechanism: Eg Gate, Knife, Ball, Air Release, etc.. Rather than combine function and mechanism into one attribute field. | Sector Discussion | to be discussed with the TWG refer to 630, 631 | 2.5.3 Valve | More information required for a decision
788 | Potable water | Vol 1 | Where are readings recorded? Should there not be an attribute for the latest meter reading and date it was recorded. | Noted: no action required | As Constructed' data not operational data. | 2.7.1 Instruments | No action
789 | Potable water | Vol 1 | Incorrect reference: Should be 1.8 | Included | Resolved in current version. | 2.8.2 Matching to Existing Infrastructure | Change made document updated
790 | Potable water | Vol 2 | Terminology Constancy: In Vol 1, Section 1.8, a lot of the elements below are referred to as "Asset Classes" They are also referred to "Asset Classes" in the attribute and validation file format. Suggest change "Categories" to "Classes" | Noted: no action required | Standards updated to a consistent approach | Table 3: Asset Hierarchy Framework | No action
791 | Potable water | Vol 2 | I am unsure what this means. Can there be more explanation of the content in the Rules column. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
792 | Potable water | Vol 2 | What is Rule 2? Ensure on what this means. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
793 | Potable water | Vol 2 | How are these levels recorded in the date table 7? (ie Network, facility) Table 7 only links back to an individual asset level (Unique_ID) There does seem to be merit to applying Risk to a network level, sub-network level or at a facility level? Could also apply this thinking to Criticality definition? | Sector Discussion | Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance or criticality | No Specific Reference | More information required for a decision
794 | Potable water | Vol 1 | All three standards use this sentence correct for all 3 waters | Sector Discussion | Please provide further information. | Executive Summary | More information required for a decision
795 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.7 Heirarchy | Change made document updated
796 | Potable water | Vol 1 | Believe there should be a level between asset group and asset type (see my hierarchy tree). Also Asset Class & Asset Category is not specified in the hierarchy. | Sector Discussion | Please provide further information relating to your hierachy. | 1.7 Heirarchy | More information required for a decision
797 | Potable water | Vol 1 | Defined as Asset Type on previous page | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
798 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
799 | Potable water | Vol 1 | What information is required to determine if a tank/reservoir is a civil structure or not. i.e. How to determine if a tank/reservoir is a containment structure or a retaining structure. | Noted: no action required | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | 1.8 Theme Structure | No action
800 | Potable water | Vol 1 | Will there be reference documents for treatment plant assets? | Noted: no action required | Not at this point in time | 1.8.1 Other Asset Classes in the precinct of a Water Network | No action
801 | Potable water | Vol 1 | How would an asset that could be represented as more than one of these be represented. e.g. would a scour be a single asset (pipe) or two (pipe and fitting) or would that be up to the Client to determine | Sector Discussion | More information is required to inform a way forward | 1.9 Data Principles | More information required for a decision
802 | Potable water | Vol 1 | water | Included | changed to Water. | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
803 | Potable water | Vol 1 | water code lists | Included | Section under review. | 2.1.5 Attribute Data Fields | Change made document updated
804 | Potable water | Vol 1 | Definition etc missing | Included | Section under review. | 2.1.6 Attribute Data Type Definitions | Change made document updated
805 | Potable water | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils/contractors to use an ESRI based product, or something else? if not suggest removing ESRI from this sentence. | Noted: no action required | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for | 2.1.7 Metadata Definitions | No action
806 | Potable water | Vol 1 | Section 2.1.4 | Included | Section under review. | 2.1.7 Metadata Definitions | Change made document updated
807 | Potable water | Vol 1 | Does this code list include options for multiple networks? or is each network to be recorded as an individual project? | Included | ProjectID already included Yes it does - added multiples in Project Table | 2.1.9 Project Attributes | Change made document updated
808 | Potable water | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
809 | Potable water | Vol 1 | See note regarding Design Company above. | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
810 | Potable water | Vol 1 | Should this not be a code list? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
811 | Potable water | Vol 1 | What is the definition of cost for contractors? What is the value of capturing this when there are no controls around application of defining cost? | Included | Reviewed and Noted for Inclusion Financial code lists for ODRC, ORC and OC are included | 2.1.10 Common Attributes | haydn
812 | Potable water | Vol 1 | What exactly are the photographic references? This appears to be a 250 Char field so completely useless for using this data. Is this intended to be used in a similar way to 'Unique ID' as a reference number for the photo? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
813 | Potable water | Vol 1 | Again using a 250 character field means the data could be all over the place. Example uses this field to record specific instructions to access the asset. To me that should be a separately labelled field. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
814 | Potable water | Vol 1 | See note regarding this field on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
815 | Potable water | Vol 1 | See not for Design Company on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
816 | Potable water | Vol 1 | Would a T not be a fitting instead of a node? | Noted: no action required | T is a fitting but also an intersection so therefore a node. | 2.4.4 Node | No action
817 | Potable water | Vol 1 | Is there a particular reason that Valves etc do not 'break' pipes? When works are undertaken (renewals in particular) actual physical assets provide useful 'real world' demarcation points. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | 2.4.5 Pipe | No action
818 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram
819 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram
820 | Potable water | Vol 1 | What are the reasons for Internal Diameter, Nominal Diameter and Nominal Bore all being required? Are these all not essentially the same thing? | Sector Discussion | The range of diameter types are an analytical requirement for interogating assets through a range of lenses | 2.4.5 Pipe | More information required for a decision
821 | Potable water | Vol 1 | Would this class also cover assets that provide access but are not part of a dam or weir wall? Suggest that this be added to the wastewater specification as well. | Included | Agreed 9/3/2017 | 2.3.6 Tunnel | Comment clarifed in potable water document and tunnel asset class added to wastewater document
822 | Potable water | Vol 1 | Should purchase date be included? Do some warranties apply from date of purchase? | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision
823 | Potable water | Vol 2 | a' instead of 'the' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
824 | Potable water | Vol 2 | Why is infrastructure for collection and treatment not covered? These assets are integral to potable water supply and asset managers need quality information that they can use to make asset management decisions. Sentence also contradicts itself. "does not cover infrastructure...treatment of water, except in the case of..infrastructure to treat water". | Noted: no action required | There is a desire to create anoter standard which includes these assets, as there is in th ebuilding environment for Large Commercial Buildings and Industrial Buildings | No Specific Reference | No action
825 | Potable water | Vol 2 | Pressure is more of a Quality provision. Suggest moving this into Quality. | Noted: no action required | Pressure is a Design Attribute How it performs against that design is a Design Performance attribute | No Specific Reference | No action
826 | Potable water | Vol 2 | Delete extra "that" | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
827 | Potable water | Vol 2 | outlines' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
828 | Potable water | Vol 2 | investment' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
829 | Potable water | Vol 2 | replace' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
830 | Potable water | Vol 2 | Influences | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
831 | Potable water | Vol 2 | Replication | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
832 | Potable water | Vol 2 | General comment - risk and criticality are closely linked. Are they really different things? Just use one term and get rid of the other. | Noted: no action required | No action required. Decision to separate two schemas taken at project management level | No Specific Reference | No action
833 | Potable water | Vol 2 | Table is missing a 'comments' field | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
834 | Potable water | Vol 2 | Inconsistent with the wastewater and stormwater measure headings (Rating). Suggest same terminology is used across all three waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
835 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
836 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would" more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
837 | Potable water | Vol 2 | Is this a different manual than the 3rd Edition New Zealand Pipe Inspection Manual? If not use full document name as used in the wastewater and stormwater documents. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
838 | Potable water | Vol 2 | Should this not be in line with the wastewater and stormwater measures? (IIMM 2015) | Noted: no action required | No action required. This is the same document | No Specific Reference | No action
839 | Potable water | Vol 2 | If this information is to be completed by field (maintenance and operations) staff they are unlikely to know if works have been deferred or will be deferred. | Noted: no action required | Not an attribute of these standards | No Specific Reference | No action
840 | Potable water | Vol 2 | Replace "data" with "cost" | Included | Documents have undergone a full publishing edit | Haydn | No action
841 | Potable water | Vol 2 | Stormwater document includes complete code lists for these items. Water and wastewater do not. | Noted: no action required | Code lists updated | List of Code Lists | No action
842 | Potable water | Vol 2 | Not convinced that this is a useful or practical schema, at least for potable water assets. Perhaps don't bother with this and just use demand schema instead? They are similar. | Noted: no action required | Utilisation and Demand are different decision elements as explained in the standards. | 3.2 Utilisation Schema 3.3 Demand Schema | No action
843 | Potable water | Vol 2 | Missing sentence from WW and SW Volume two further explaining the utilisation schema. " Utilisation is measured using time or other base unit measured against a known availability." | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
844 | Potable water | Vol 2 | "Current Utilisation" at an asset by asset level would require an impractical amount of monitoring. i.e. are we really going to know average and peak flows through each and every length of water pipe? | Included | This is an analytical construct, and easily monitored in an analytical sense at whatever frequency required for intervention circumstances | 3.2 Utilisation Schema | An explanation of Data Science will be provided for at the Technical Working Groups
845 | Potable water | Vol 2 | Partly a function of the pressure in the pipe. Are we really going to know potential utilisation for each and every length of water pipe? | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
846 | Potable water | Vol 2 | Don't think it's possible to determine this for each and every asset. At least for potable water assets. | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
847 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets without extensive modelling. Alternatively would require data from modelling software. | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
848 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
849 | Potable water | Vol 2 | This does not seem to be an relevant measure for water demand in a metropolitan situation. | Included | Completed - see Demand section | 3.3 Demand Schema | No action
850 | Potable water | Vol 2 | Criticality varies across all three waters. While a data centre may have a higher water criticality than a hospital, the opposite would be true of wastewater. | Included | Correct, which is why each asst class is treated differently when an analysis of things like criticality are conducted across a network | No Specific Reference | No action
851 | Potable water | Vol 2 | Of risk & criticality, which are both similar schema, criticality is much quicker and easier to measure and much less subjective. I would be tempted to exclude risk or use it with caution in decision-making compared the use of other schema. | Noted: no action required | It will be required n some circumstances, and here it is defined when you do | No Specific Reference | No action
852 | Potable water | Vol 2 | Ln only needs to be 1 due to 1,5 rule | Included | Completed | No Specific Reference | No action
853 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
854 | Potable water | Vol 2 | Even at a score of 3 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
855 | Potable water | Vol 2 | Even at a score of 3 is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
856 | Potable water | Vol 2 | Even at a score of 4 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
857 | Potable water | Vol 2 | Not convinced there is much use in this table, at least for water assets. Most revenue is derived from consumption so would be associated with a meter and the usage of water. | Noted: no action required | No action required. Organisation can choose how revenue is recorded against an asset | No Specific Reference | No action
858 | Potable water | Vol 2 | So this is theoretical revenue? Not actual revenue? | Included | Actual, Forecast and Budget included in financial code lists | Code List 6: Bases of Cost | No action
859 | Potable water | Vol 2 | Delete this text. Captured in the field below. | Included | Completd | No Specific Reference | No action
860 | Potable water | Vol 2 | This whole section is confusing. It's trying to do two things at once. Individual asset attributes and whole of network attributes should be separated out. | Included | Network analytics are completed on individual asset analytical interogations | No Specific Reference | No action
861 | Potable water | Vol 2 | So its not intended to be used for decisions at an individual asset level? If not, strip out all the individual asset measures and move somewhere else. | Included | It is in some circumstances to be used on an individual assetID | No Specific Reference | No action
862 | Potable water | Vol 2 | This table seems to be a jumble of attributes for individual assets and DIA measures which are taken for the network / organisation as a whole. I'm not really sure the whole of network / organisation attributes are metadata. Delete DIA whole of network / organisation attributes or move to a separate table. dlane: Some data items are network wide while others are asset specific. If data capture is required these should be split into separate network and asset tables. | Included | Volume 2 is completed in these draft standards. Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance | No Specific Reference | No action
863 | Potable water | Vol 2 | How does this field work? Is it the duration of the most recent unplanned interruption, the the total duration of all unplanned interruptions (from field below) or the average unplanned interruption duration? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
864 | Potable water | Vol 2 | How does this field work? Is it the connections affected in the most recent unplanned interruption, the total connections affected in all unplanned interruptions (from field below) or the average number of connections affected in unplanned an unplanned interruption? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
865 | Potable water | Vol 2 | Delete this field. It makes no sense and is confusing. Field Ref 11.04 does the job. | Included | Table updated | No Specific Reference | Change made document updated
866 | Potable water | Vol 2 | Need to include the units of measure. kPa,psi etc | Included | Tables updated in code lists of Vol 2 | Code List 44: Description of Design Performance – Engineering Unit of Measure | psi to be added
867 | Potable water | Vol 2 | Surely this field would only be used for a reservoir asset. Not, say, a pipe supplied from the reservoir. Please clarify the use of this field. | Included | It can be both | No Specific Reference | No action
868 | Potable water | Vol 2 | Not sure it would come from Repairs and Maintenance Schema. | Noted: no action required | This MoH included in the Service Performance Attributes | Data Table 11: Service Performance Attributes – Functional | No action
869 | Potable water | Vol 2 | Confusing to have it on this table. So this field is used at a facility level not an individual asset level? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
870 | Potable water | Vol 2 | Confusing to have it in this table. So this field is used at an organisation level? The question of whether there is an adequate backflow prevention programme doesn't relate to individual assets? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
871 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
872 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
873 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
874 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
875 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
876 | Potable water | Vol 2 | This is not a demand attribute, its abstraction/take and is source based. as you've said that this is potable water assets only I don't think it's appropriate here. | Noted: no action required | A source is an asset (e.g. a reservoir), abstraction is the process, demand is the level of abstratcion on the asset - each are different and can apply to a pipe connection no less (e.g. a school) | No Specific Reference | No action
877 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
878 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
879 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated?. | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
880 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. Move to financial schema? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
881 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
882 | Potable water | Vol 2 | Differs from tables in the stormwater and wastewater specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Tables are very similar, with the asset specific elements being applied when required. Tables have been normalised where possible | No Specific Reference | No action
883 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
884 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
885 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
886 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
887 | Stormwater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Included | Reviewed and Noted for Inclusion | 2.1.7 Metadata Definitions | Change made document updated
888 | Stormwater | Vol 1 | 2.1.4 | Included | Reviewed and Noted for Inclusion | 2.1.6 Attribute Data Types Definitions 2.1.7 Metadata Definitions | Change made document updated
889 | Stormwater | Vol 1 | Does this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Noted: no action required | Either | 2.1.9 Project Attributes | No action
890 | Stormwater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
891 | Stormwater | Vol 1 | See note regarding Design Company above. | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
892 | Stormwater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
893 | Stormwater | Vol 2 | Heading (see water and wastewater) | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
894 | Stormwater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or at code should be a single character as per the water measures. Should be consistent across all 3 waters | Included | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
895 | Stormwater | Vol 2 | Differs from table in wastewater and water specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
896 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
897 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
898 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.8 Theme Structure | Change made document updated
899 | Wastewater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Noted: no action required | Not the intention. The intention is to outline why the field is structured in this way | 2.1.7 Metadata Definitions | No action
900 | Wastewater | Vol 1 | 2.1.4 | Included | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | 2.1.7 Metadata Definitions | Change made document updated
901 | Wastewater | Vol 1 | Doe this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Sector Discussion | This is an operational question related to an organisations ability to import data into their asset management systems. For immature organisations likely to be project by project, for mature ones project agnostics | 2.1.9 Project Attributes | More information required for a decision
902 | Wastewater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
903 | Wastewater | Vol 1 | See note regarding Design Company above. | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
904 | Wastewater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
905 | Wastewater | Vol 2 | Not a valid measure for wastewater utilisation. | Included | Updated | No Specific Reference | No action
906 | Wastewater | Vol 2 | Criticality varies across all three waters. for example, for wastewater a hospital would have a higher value than a data centre. while water could score differently | Noted: no action required | No action required, based on the importance of the building as defined in the Buildings standard | Code List 13: Facility Importance Rating
907 | Wastewater | Vol 2 | Heading is different from that used in water and stormwater documents. Suggest standardising for simplicity. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
908 | Wastewater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or code should be a single character as per the water measures. should be consistent across all 3 waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
909 | Wastewater | Vol 2 | Differs from tables in the stormwater and wastewater spec. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
910 | 3-Waters & Buildings | Vol 1 & Vol 2 | An obvious mistake in the Potable Water Metadata Std is that someone has put the Residential Executive Summary in it????. | Included | Included in the draft Standards | Executive Summary | Change made document updated
911 | 3-Waters & Buildings | Vol 1 & Vol 2 | You are asking for public to comment on missing attributes within meta data tables. Considering you have spent 12500 hours on this, could you please comment if all the attributes defined by Australian standard ADAC have been included? http://engicom.com.au/adac/government-organisations I appreciate your list of assets may be more comprehensive. If any of the asset attributes defined in ADAC are missing there are like to be areas where assets will miss vital information for future analysis. If you have used IPWEA in your decision making process it would be useful to include this information on your website so it doesn’t look like you are reinventing the wheel. Well done on sorting out the asset management data through the lifecycle of each asset. Local councils desperately need national standard for asset capture, storage and access to information. | Included | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. | General | No action
912 | 3-Waters & Buildings | Vol 1 & Vol 2 | I’d like to provide feedback on the proposed standard. However I caveat this as coming from a hands on GIS Practitioner View, which may be different to my colleagues here at LINZ. I think it will be incredibly important to incorporate good practice guidance at some stage on how these standards are practically implemented. Ideally providing an empty or working dataset that a person can take, open with their system and populate. Generally when you go to create the schema in a system you’ll follow it and interpret changing the types, field lengths, column names etc. My request is based on recent experience. Often this step is left out, and implementation of the standard fails. This was my experience with the ANZLIC geospatial metadata standard, 10 years after its release 95% of GIS practitioners in New Zealand could still not easily implement the standard within the most common desktop GIS software. The Australian based tool provided did not support NZ requirements. We ended up shoving the required text into a single desc field in an inappropriate manner, ending up with a total mess. This may require getting software providers onboard with adding these into their pre-defined templates for users of the most common software providers. If you could imagine in the same way we create a LINZ letterhead letter in MS Word. My 2 cents from a GIS data capture perspective and I am happy to discuss this further if appropriate, otherwise happy to leave it as this. | Noted: no action required | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | N/A | No action
913 | 3-Waters & Buildings | Vol 1 & Vol 2 | In each of these documents out for proposal, there is reference to standard codes for things like asset type and material (“the CODELIST”), but none of these are available yet – will this be available before consultation closes? | Included | Code lists are included Attributes to be discussed | General | Gauge input from next review
914 | 3-Waters & Buildings | Vol 1 & Vol 2 | This is a great initiative and will aid everybody involved in the area of Asset Management. I would ask is has there been any coordination with the Institute of Public Works Engineering Australasia as they have a system already in place called ADAC (http://www.engicom.com.au/adac). Could your framework be an extension to that so we can leverage what software companies have developed already to support that schema. It appears that a lot of the info you are capturing has already been covered, why reinvent the wheel? | Noted: no action required | IPEWA Australisia has representation around the table, and has had for 2 years | N/A | No action
915 | 3-Waters & Buildings | Vol 1 & Vol 2 | Structure of the standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes. Further to the split of water sectors there is an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group has specified that a single document that focusses on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. In terms of usability our end users are expecting a data framework that is easy to understand and use. In the proposed layout we are expecting the standards will be met with cost burdens. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
916 | 3-Waters & Buildings | Vol 1 & Vol 2 | 2. Applicability of volumes 1 and 2 The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was about creating an as-built data set for industry that can be used to collect field data, most of the workshops evolved around this input. Volume 2 for derived data has had limited industry input and we do not believe it is ready to be published. Further work on this volume is therefore required. | Noted: no action required | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. | General | No action
917 | 3-Waters & Buildings | Vol 1 & Vol 2 | 3. Data hierarchy The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. As presented at the workshops, an example of how this could be applied to the tables is outlined below: Level 0 (system/layout specific data – master data. Typically assigned by organisational systems and numbering or coding rules - contains the common data set) -Inventory identification number / -Functional location i.e. Network type (water, wastewater, stormwater) / -etc. Level 1: Data categories, in example: “Technical/physical” i.e. Containment structures (available technical core classes) (or) Operational data (or) Financial data etc. Level 2: (attributes) Minimum required attributes, in example: -Function / -Depth / -Material / -etc. Level 3: (attributes) Conditional attributes, in example: -Diameter if circular / -length and width if not circular / -Joint type (if the structure has joints) / -etc. Level 4: (attributes) Optional attributes, in example: -Manufacturer / -Model/part number / -etc. | Included | Asset Classifications have been defined in the Standards Tables are to be discussed at length | No Specific Reference | Sector discussion
918 | 3-Waters & Buildings | Vol 1 & Vol 2 | 4. Terminologies and definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need to be agreed. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
919 | 3-Waters & Buildings | Vol 1 & Vol 2 | 5. Graphical representation and its accuracy This subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. Graphical representation should be removed from the document; the purpose of this standard is collecting metadata of asset physical properties. Geospatial requirements are a standard in its own right and even providing these as guidelines does not seem appropriate. | Included | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH | General | No action
920 | 3-Waters & Buildings | Vol 1 & Vol 2 | 6. General content 1.“Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. 2. The units of measure have not been covered during the workshops. Further input may be required before the draft is ready for public release. 3. Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and the implementation may not be practical. 4. Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. In many instances data will be collected in-house. 5. Australian examples and photos should be replaced by New Zealand examples. Word choice such as “savvy” (used often) is not the best choice. Some of the language used needs to be reviewed in order to retain the standard’s professionalism. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included | General | No action
921 | 3-Waters & Buildings | Vol 1 & Vol 2 | 7. Implementation The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate has not been considered where organisations may choose not to collect certain information for low risk assets. An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard | Noted: no action required | This is not within the scope of these standards | N/A | No action
922 | 3-Waters & Buildings | Vol 1 & Vol 2 | We believe there is a reasonable amount of work that has not been completed, such as standard definitions, which may lead to inconsistencies between the water organisations. Without this work being completed the documentation that has been produced could only be used as a guideline or a code of practice. | Noted: no action required | All definitions have been standardised and normalised | No Specific Reference | No action
923 | 3-Waters | Vol 1 & Vol 2 | However, page 141 of Potable Water Volume 1 As-constructed/As-built references code lists for 3 waters assets that can be reviewed in a supplementary document called 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016 Is this document available for download or can it be emailed to me? I would like to cross-check what is in this code list against the attribute tables to assist with my review. | Included | Code lists are included | General | Change made document updated
924 | 3-Waters | Vol 1 & Vol 2 | As-constructed schema should not be a separate document, and should recognize that many assets are created though term contracts not just greenfield build. We should not separate “as-constructed” from other elements of the standard because this perpetuates last century’s practice of asset management being about the asset whereas it is about the service enabled by the asset. We should modify the “as-constructed” schema to recognise that construction happens both in new builds and in renewal term contracts and the information should support both efficiently. I am not convinced of the value of separating the standards into two parts. While as constructed data is central to an asset information system there are few transactions that use it in practice. Most construction projects will use subsets of the inventory tables, performance based construction projects will also use the condition and performance tables, term PPP or BOOT contracts will use almost the entire standard. This means there is no one to one connection between projects and elements of the entire data schemas so the split of the source documents is artificial. I think there is a serious downside to separating the two documents that drives us towards a combined view. Asset management is all about delivering services that require significant assets. Separating as-constructed from performance data perpetuates past practice that asset management was about having assets in good condition, whereas it is about having assets in sufficient condition to deliver targeted services. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
925 | 3-Waters | Vol 1 & Vol 2 | Another challenge with this proposed separation and the associated “constructor” reference fields is that for roads and 3 waters, though to a lesser extent buildings, much infrastructure is created through renewal or replacement programmes. For example for State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. This means that we need to think seriously about replacing the “constructor” record in the “as-constructed” table with a reference to an “Asset Intervention” record as described elsewhere in my comments. Unless this is done there will be not be normalisation of records relating responsibility for modification of inventory, a ridiculous amount of duplicate records created from term contracts where much inventory is created, and a mismatch between the constructor records in the “as-constructed” schema and those of the maintenance schema, when in term network management contracts these are the same constructor. The same duplication will occur when the same constructor creates many inventory records as occurs in term contracts | Noted: no action required | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | No Specific Reference | No action
926 | 3-Waters | Vol 1 & Vol 2 | The categories of data type should be simple, exhaustive and mutually exclusive so should vulnerability and resilience stand alone? The proposed “global meta data schemata” classifies data into several categories. This is a necessary and good thing because it help users appreciate the scope of the data and find the elements they may be interested in. To do this well the elements must be simple, described in commonly understood language, cover the field of interest, i.e. be exhaustive, and be mutually exclusive, i.e. not have definitions that overlap or require subtle nuancing. | Included | Included in the draft Standards | General | No action
927 | 3-Waters | Vol 1 & Vol 2 | Vulnerability - risk There is an open question in the document as to whether vulnerability should be drawn out as a standalone data category, when it influences risk. I do not think it should be standalone because this then makes “risk” become “risk other than vulnerability” and I think that is a bit silly. I certainly agree that vulnerability is important. I think it so important that we should draw it out in the risk or resilience categories. The high level approach to risk is to consider likelihood and consequence. Simplistically consequence conflates: • vulnerability of service, and • impact from reduction or loss of service and vulnerability of service conflates: • vulnerability of infrastructure (considering network effects), and • availability of alternate infrastructure or alternate services. I think we should draw out these or similar elements of risk for those elements of infrastructure type that potentially have a consequence greater than tolerable. This might mean (in the transport context) arterials and above in a transport world because of their importance to the economy and society. Effectively this creates a level of service gap around vulnerability, the very gap that rental companies advertise as being closed when they proclaim on their hoardings that a building to let is 85% EQ code compliant. | Included | Included in the draft Standards | 4.2 Vulnerability Schema | No action
928 | 3-Waters | Vol 1 & Vol 2 | Resilience - performance Resilience is a service level, or a strategic goal. As a service level it should be within the performance elements of the data standard. I know that it has prominence because it is an important element of performance, but so too are accessibility and safety for transport, or availability of supply or health for water. As a strategic goal it is a driver of service levels. | Included | Resilience is a state and requires measurement The level of service is subject to the level of service any organisation seeks to apply, and an invetment plan to meet that level | 4.5 Resilience Schema | No action
929 | 3-Waters | Vol 1 & Vol 2 | Utilisation is multifaceted and requires enhancement The definition of utilisation given in the draft standard is the proportion of an assets available capacity that is actually being used. I think that there will need to be some clever messaging to ensure that the unit of capacity chosen is understood for infrastructure in different circumstances. Using a transport example provides an illustration of this. Over 60% of New Zealand’s roads are classified as access or low volume access roads. This means that they have less than 1000 vehicles using them per day. A single lane has a capacity of about 1400 vehicles per hour, depending on its configuration, i.e. on the proposed definition of capacity most roads have a daily utilisation of about 1.5% yet these roads represent the last and/or first mile of most trips and so are critical to our economy and society. The level of utilisation will always be low simply because there are rural and urban areas with low population that are connected to market or work place. Even with planned intensification of central urban areas daily utilisation might only rise to 5%. This is analogous to the smallest element of supply or removal for potable or waste water. Also, where there is suppressed demand because demand exceeds supply, e.g. on congested transport networks (whether roads or busses), we may report 100% utilisation, but that is bad because the potential benefit of suppressed trips is being lost or costing more. In a water example we may constrain the development of business when supply is inadequate for development yet fully used by current development. Together these factors mean that we have to be careful about the utilisation measure and how we use it alongside other measures at a local and network level, a simplistic approach won’t do. I think this section of the draft standard needs work to draw out these issues. In addition we need to consider how utilisation and performance metrics are used to optimise asset investment decisions. | Noted: no action required | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | No Specific Reference | No action
930 | 3-Waters | Vol 1 & Vol 2 | Inventory Interventions At the moment there are two types of works records, those recorded as maintenance and those associated with the as-constructed fields. I think we should consider what we want from the recording of “works” or inventory interventions because I expect that will lead to an improved data structure with one form of works interventions record. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
931 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Planned, current, completed or abandoned works so we can fuel the nationwide forward and current works viewer enabling better coordination of works and reduced disruption of customers whether the works are construction, renewal or maintenance. Interventions on inventory are a process that creates or modifies inventory. Much information is required about the process as much as of the fact that it creates inventory. E.g. the forward works viewer being developed to display proposed and current works have time, duration, and place elements of information as well as descriptive information about the constructor and infrastructure being modified or created as reflected in the proposed “as-constructed” schema. | Included | Statement noted. Already done in Repairs and Maintenance schema. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
932 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Responsibility for management of infrastructure, noting that ownership may pass to a client when inventory enters service, but responsibility for maintenance may extend beyond the transfer date | Noted: no action required | Noted | No Specific Reference | No action
933 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • A hierarchy of works and tasks that distinguish a term contract (or work) from a work task within it so that the work identifies responsibility, type of work, stage of work etc, and the task the date and type of work done linked to the infrastructure impacted. I think this allows better alignment with supplier’s management systems, responsibility for work done, and supports many forms of contract from term based contracts to single task contracts. This also enables security to be built into system for data exchange. This is important because for most infrastructure networks (buildings aside) most new infrastructure arises due to renewal works and not due to greenfield construction. | Included | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
934 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
935 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
936 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Types of inventory intervention with appropriate records, including, but not limited to: o Physical works, probably the most common type o Waste or abandonment, associated with infrastructure being removed from the inventory and reflected in a valuation as a write-off o Inventory received from third parties, e.g. as a result of transfer from development of a new residential area to a council, or the transfer of responsibility of a road from a local authority to the Transport Agency as a State highway o Inventory transferred to third parties, e.g. the transfer of responsibility of a previous State highway to a local authority on completion of a State highway bypass. I acknowledge that “inventory interventions” is not the best term and that a better one should be found. | Included | Included in the draft Standards | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
937 | 3-Waters | Vol 1 & Vol 2 | Assessments There is an opportunity to introduce a concept of an intervention type of “Assessment”. This arises because there are many instances where responsibility for some parameter in many of the tables is explicitly referenced, yet is essentially the same information in each case. This information is who changed the parameter, when, why, as a result of what process…? This proposed approach will enable normalisation of data describing the assessment of condition or performance (whether current or forecast), valuation, risk or any other metric in a standard way. It will then identify the provenance and responsibility for each. This proposal is much the same as that for “inventory interventions” in that it suggests that the core information is about the process leading to the metric in the data and this should be recognised. | Noted: no action required | Assesments are (or interventions) are subject to the element being interrogated (e.g. condition). The standards have attributes which capture these. These will however be predominantly the focus of the work when develop-ing Volume 3 | Data Table 1: Condition Attributes & Code List 17: Condition Rating – Methodology | No action
938 | 3-Waters | Vol 1 & Vol 2 | Supply of as constructed data I think that we shouldn’t mandate the form for the supply of as constructed (or other data) but rather the relevant metadata describing its provenance, quality etc. If the form is mandated then it would require an absurd level of record keeping and compliance from term contractors who create many new assets. E.g. for State highways we use term contractors who create the vast majority of new surface infrastructure each year. For State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. Suitably qualified and quality assured staff from contractors enter the as-constructed data directly into our inventory system, and this isn’t shown as an acceptable method of delivery yet it patently is. One of the purported benefits of meta-data standards is that it enables business to business transfer of data. Defining the transfer of data on a disc seems to fly in the face of these benefits and the advance of B2B technology. Similarly I would think that NIU doesn’t want to be involved in contractual requirements for each form of contract, rather whether information is being managed well and is fit for purpose. I think the supply of data section starting on page 1 of volume 1 needs review. | Noted: no action required | Data format (form here) is not within the scope of these standards | General | No action
939 | 3-Waters | Vol 1 & Vol 2 | Asset management I think the sections of the standard on asset management need a revision to better reflect: 1. That customer service at least long term cost is the goal, and not maintenance of asset condition, noting that the two are related. 2. Investment decisions made in a customer service centric world. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
940 | 3-Waters | Vol 1 & Vol 2 | Customer service focus The various diagrams, for example figure 3 on page 24 of volume 2 is written in very economic language around the return for investment of public funds. This is of course critical, but loses the narrative that relates providing customer service that is economic. | Noted: no action required | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. | No Specific Reference | No action
941 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: I think the steps in the above referenced diagram, and the description on the preceding pages are missing an element and that is what is being targeted in terms of service levels and how this target is established. Or alternatively (as a poor second best) are missing the inputs describing the economic and social benefits of different service levels experienced by customers. If these were present then the analytics could do the required work. This step is required to establish the performance targets referenced in the performance elements of the standard. Eg what is the optimal economic service level for service outages considering investment to reduce the frequency, duration and impact of service outages against the social and economic impacts of these. This step is difficult and complex but needed none the less. It requires decisions about the relative weight to be given to quasi commercial models or economic models. It requires significant analytics to be undertaken to determine the relationships between costs and benefits of different levels of service for different types of customers in different circumstances. Much of these analytics are represented in the economic evaluation manual used to determine the economic value of transport proposals in New Zealand. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | No action
942 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: The service led approach enables a more informed discussion with customers about expectations of service level and the cost of these than a black box economic model. It essentially proposes a three stage approach: (See figure in word document) This recognizes that information is never perfect to enable ideal one off analytics because customers’ needs, systems and contexts change so what might be optimum now likely won’t be at another time. The aspect of service level target should be reflected in the analytics framework. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. | No Specific Reference | No action
943 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world I think that section 1.8 needs some rework though many aspects are worth keeping. There is significant reliance on the metaphor that as assets deteriorate and consequently the maintenance expense to sustain targeted service levels increases there is a sweet spot between condition and maintenance cost. I think we need to recast that metaphor in a customer centric world and recognize that the sweet spot is tautological because the definition used for condition grade 5 is that it has failed or soon will so it is no coincidence that replacement is needed there. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
944 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world The proposed standard presents a theoretical approach to stochastic analysis. This style of analysis is becoming common place. The standard might reference the UK’s Highways Efficiency Maintenance Programme website, especially this url: http://www.highwaysefficiency.org.uk/efficiency-resources/asset-management/life-cycling-planning-toolkit.html That site includes standard tools for “stochastic analysis” of renewal programmes using the “5-step condition rating”. While the text is all about roads the processes are generic. With translation, or a babel fish (as Douglass Adams might say) they are as applicable to buildings as to roads. The tools on that site are of course single factor analyses as condition based analytics generally are. There is no single or multifactor customer service optimisation (e.g. skid resistance and ride comfort for roads) that assists planning in a constrained environment or in an environment where value for money matters, but it is a straight forward approach to estimating the works required to sustain performance. That reference, or a more applicable one, or a derivative of it, would go some way to making the theoretical text in the proposed standard tangible. | Noted: no action required | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
945 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If the text were recast to be more customer service centric it might use the following approach. The two most important decisions to intervene with some form of monitoring or works when managing a network to provide customer service are: 1. When delivered service levels have or will drop below the targeted level or there is too great a risk that they will 2. When, despite the targeted service level being met, it is cheaper in the long run to intervene, or there is an unacceptable risk that costs will rise unless an intervention is made Intervention decisions can initially lead to a monitor, maintenance, renewal or improvement interventions, whichever is part of the least long term cost intervention strategy. A more colloquial way of putting this is only intervene if its broken, or cheaper in the long run. | Noted: no action required | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
946 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world Transport examples of the two decision types are: Ensuring the service is delivered to target. • Replacing the tires on your car when the tread depth has reduced and become unsafe, or ahead of winter when risk is greatest when tread depth has almost become unsafe • Continuing to monitor the change in direction of a river beside a roadway that may ultimately risk scouring of the road formation in order that preventive works can be taken when necessary and most cost effectively to preserve the transport route • Water cutting the excess bitumen off a road to restore the prominence of the chips so tyres grip these rather than “float” on the water film when the road is wet in order to restore the skid resistance of the road surface. • Resurfacing a road when the skid resistance of a road is falling and is either unsafe or will become unsafe before the next opportunity to intervene because the stones have polished Ensuring that delivery of the service is at the least possible long term cost. • Replacing the oil in your car engine even though it is performing well in order to forestall engine damage • Monitoring the condition and maintenance expenditure on deteriorating roads so that and expected renewal works can be designed and timed to be cost effective long term • Sealing cracks in an asphaltic concrete road surface to reduce water ingress to the pavement which would cause the pavement to deteriorate rapidly and require more expensive repairs • Rebuilding or replacing the structural layers in a pavement when this is the cheapest long term cost because deterioration in pavement strength is leading to the need for significant and increasingly frequent and costly repairs and resurfacing treatments to maintain service levels | Noted: no action required | And, is the intention of the analytical foundations set down for Volume 4. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
947 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If discussion of the type inferred in the above table were included then the standard would be more tangible to users and better focussed on customer service, the goal of asset management. I think it worth the discussion including reference to or guidance on the economic decision to continue to maintain infrastructure or to renew or replace it on a site specific basis. The IIMM might be suitably referenced. When funds can be used on other investments outside asset management of the infrastructure in question then we look for the sweet spot where the net present value of the renewal plus reduced subsequent maintenance stream is better than the present value of the continued and increasingly expensive maintenance stream. This should be included because it can be implemented site by site for significant investment, and needn’t rely on sophisticated network level analytics and data, though it requires some to describe the relationship between condition, time and maintenance cost. This analysis that maintenance costs typically increase as condition worsens is shown in the following indicative diagram as indicated in the draft standard metaphorical diagrams. This shows there isn’t a sweet spot from this relationship alone. Another factor is required for optimisation and that is the present value of the replacement cost option on a site specific basis, or long term budget on a network basis. (see figures in word document) | Noted: no action required | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
948 | 3-Waters | Vol 1 & Vol 2 | Global Schemata The global asset metadata schemata diagram on page 16 of volume 2 appears out of place with the prosaic listing of detailed data requirements. If it were fully developed as an idea in the text you would expect it to tell a story about why certain data elements are required. No such story is conveyed, so the inference is that whatever data is in the standard will enable such analysis, if that were true then the benefit of the advanced analytics would be small. That seems odd. Does this description add value? | Noted: no action required | The diagram provides context for the detail that follows There are some who are already applying this level of complexity to decision-making. | 1.4 Context of Asset Data and Analytics | No action
949 | 3-Waters | Vol 1 & Vol 2 | Network level performance targets The standard for service performance p101 vol 2 as proposed enables the measurement of performance against a target. This is good. However there is no reference to what good looks like so the measurements are just that. It may be useful to add records that: • Enables the categorisation of target service levels • Set service targets for each performance aspect for each category This would provide the data required to enable reporting of whether the service provided was good enough or not, in a situation where targets differ by category. The One Network Road Classification framework developed by REG for transport classifies roads into 8 categories and sets targets for each. | Noted: no action required | Levels of service are policy decisions, and are not within the scope of these standards However, where organisatoins provide these levels, these standards will attribute them and analyse them for decision-making purposes | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
950 | 3-Waters | Vol 1 & Vol 2 | Financial Performance The standard has sections on p88 vol2 and succeeding pages. It would be beneficial to review common good practice to understand what data elements should be here. The Australian Infrastructure Financial Management Guide is one such reference. Here as elsewhere the tables can be normalised by reference to an assessment record as proposed above, the type here being valuation. In addition I would have thought there would be considerable opportunity to normalise valuation approaches by assigning each asset a valuation type, and that type record containing the depreciation rates etc. applicable to it. I am not sure that the valuation section has been fully developed yet because some thought must be given to valuation components being different to asset register components. There is no need for them to be the same as they have different drivers. This sections contains data about construction cost that will be transferred to the “as constructed” tables. It asks that the cost of an asset be supplied and that supply is mandatory. However there is a challenge with this because almost all construction contacts cost elements at a higher level of aggregation than each asset. E.g.the construction of a sewage treatment plant does not lead to an estimated cost per inventory item created. Contracts with lump sum maintenance items likewise have no costs per maintenance work task. Therefore a review is required of how costs are acquired and stored and at what level. I suspect that it will be best to capture financial information at the financial/contractual transaction level and activity at the inventory affected level. The concept proposed above for having transactional records for works and tasks enables costs to be collected at that level. | Noted: no action required | There is an opportuity to reflect on the tables and code lists provided in the standards. There are some analytical assumptions being addressed here, which are for the analytics in which will be unpacked in more detail in Volume 4. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
951 | 3-Waters | Vol 1 & Vol 2 | Information required to manage well varies by criticality of network and context I expect that, as with roads, the information needs of managing a water network in a simple undemanding context differ from those of a demanding context. While the performance metrics around health and availability may be common the needs for sophisticated infrastructure and condition metrics would differ. Similarly the information needs for the critical elements in a complex network would be greater than for other elements. This would lead to a hierarchy of mandatory fields based on context. I think this should be considered. | Sector Discussion | To discuss | 5.4 Service Performance Schema | No action
952 | 3-Waters | Vol 1 | pg 3: Validating the data submission: is this to go against each asset or an organisational process requirement? | Included | Against each asset and against each attribute | General | No action
953 | 3-Waters | Vol 1 | 1.8 They are requesting that “each asset type must be delivered on a separate level/layer and the files must be clearly labelled…” If this is in a CAD format this makes perfect sense, but then the attribute information that is being requesting won’t be able to put against the individual asset (when last I tried this, it can only be done with blocks, and blocks can be tricky to convert to a shape file). But if in a shape file format, it is a bit of an overkill, it is structuring back to the way we used to have it. And we will need to combine the information in order to import into Assetfinda. it is also implying that information from contractors will be to a High enough standard that we can suck it into our GIS and all points and lines will meet perfectly. In a perfect world that would be great, but from having a draughing background. I can guarantee you are going to get hydrants, valves etc. not matching perfectly with your pipes (this comes from the skill of the person doing the as built) and greater maintenance issues later. We would be relying on the project managers to insist on high quality as built. This then brings up the issue of disposals of existing infrastructure. Or the assigning of asset id numbers that have intelligence. | Noted: no action required | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | 1.8 Theme Structure | No action
954 | 3-Waters | Vol 1 | 1.11 Projects will need to be on board with this. | Noted: no action required | Noted, but out of scope. | 1.11 Acceptance Testing | No action
955 | 3-Waters | Vol 1 | 2.1.1 Precision needs to be clarified on what is acceptable. | Included | Precision is defined in the standards | 2.1.1 Accuracy Requirements for Locating Assets | No action
956 | 3-Waters | Vol 1 | 2.1.5 In the proposed structure, the data Code list fields will be limited to 10 characters, this is not going to allow us to use unabbreviated materials e.g.: uPVC instead of PVC Unplasticised. We need to decide on this now as it affects the look up tables and associated finance. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the Full Name once the asset data is provided. | 2.1.5 Attribute Data Fields | No action
957 | 3-Waters | Vol 1 | 2.1.8 The attribute fields they are suggesting may impact on Assetfinda fields e.g.: they are the same but have different criteria. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
958 | 3-Waters | Vol 1 | 2.4.1 For Access chamber of valves they are requesting one location point, which is what we have and one polygon of the same area representing a plan view of the valve pit. We have over 2000 valves, that is a lot of additional files, and I feel a duplication of work, as the plan view can already been seen as a schematic when viewing the reticulation. - The same as above goes for Storm water | Sector Discussion | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | General for Access Chambers and Valves | More information required for a decision
959 | 3-Waters | Vol 1 | 2.4.7 Says that pump stations should be a polygon feature and all attributes are to be attached to this polygon. Then in 2.5.2 which refers to Pumps it requires pumps to be a point feature with all attribute information attached to this point. So which is it. The Pump station, the pump, or both? - The same as above goes for Storm water | Noted: no action required | The pump station refers to site specific information. The pump is the asset specific information. | General for Pump and Pump Station | No action
960 | 3-Waters | Vol 1 | 2.6.2 Cathodic Protection- I don’t know what that is. | Noted: no action required | This refers to systems installed to protect water mains from corrosion. | 2.6.2 Cathodic Protection | No action
961 | 3-Waters | Vol 1 | 2.8.2 This puts all the responsibility on the contractor to provide all the specified information in the way the document wants it, with us only needing to import it. - The same as above goes for Storm water | Noted: no action required | It also puts the responsibility on the asset owner to specify it properly | General | No action
962 | 3-Waters | Vol 1 | All the attributes that are being requested of us seems to me to be a lot more information than will ever be needed or used, but if supplied by a contractor as suggested, is achievable. | Noted: no action required | Noted, for analytical purposes | General | No action
963 | 3-Waters | Vol 1 | Waste Water seems to be a repeat of the above. | Noted: no action required | Repeat | General | No action
964 | Potable water | Vol 1 | In Summary The main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed potable water assets as defined by asset managers in New Zealand. While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant. It’s not clear who is meant by consultants here. | Included | Note added in glossary 9/3/2017 | In Summary | Change made document updated
965 | Potable water | Vol 1 | The objective of the specification in Volume 1 is to provide geospatially savvy potable water asset “As Manufactured” and “As-constructed / As-built” digital data. The objective of the specification in Volume 2 is to provide geospatially savvy potable water asset “As Managed” digital data. I don’t like the use of the word savvy | Included | Reviewed and removed | General | Change made document updated
966 | Potable water | Vol 1 | Table 1.8 doesn’t appear to include an allowed category or descriptor for “back-flow preventer” | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | 1.8 Theme Structure | New Code List Entry proposed | Back-Flow Preventer
967 | Potable water | Vol 1 | I presume in Table 1.9 that “N” stands for No. I’m sure there will be some exceptions to the rule per asset | Noted: no action required | Reviewed and Noted only | 1.9 Data Principles | No action
968 | Potable water | Vol 1 | 2.1.1 The explanations on pages 6 and 7 between absolute accuracy, relative accuracy and spatial precision are useful; however I think the sector needs to derive one preferred conceptual practice i.e. is absolute accuracy more important than relative accuracy? Whose data set has primacy? E.g. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | 2.1.1 Accuracy Requirements for Locating Assets | No action
969 | Potable water | Vol 1 | I agree with the QA Validation field being a mandatory attribute in Table 2.1.5 | Noted: no action required | Reviewed and Noted only | 2.1.5 Attribute Data Fields | No action
970 | Potable water | Vol 1 | Not all fields in the project attribute table in 2.1.7 are practical. What about a project that is geographically separated (relining different pipes) or across different asset classes? (e.g. water mains and sewers) | Noted: no action required | Reviewed and Noted only | 2.1.9 Project Attributes | No action
971 | Potable water | Vol 1 | 2.1.1 Pg 17 . Ditto for “Area of Work” extent. | Noted: no action required | Reviewed and Noted only | 2.2.1 Area of Work Extent | No action
972 | Potable water | Vol 1 | 2.3.1 How will an open civil structure be represented? E.g. a settlement pond | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | 2.3.1 Containment Structure | More information required for a decision
973 | Potable water | Vol 1 | The repetitive use of the generic term “Health & Safety Issues” in the respective attribute tables should be revised to documented Health & Safety Risks. Or similar | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure trigger there are 'special circumstances'. A code list is proposed | General | More information required for a decision | Health & Safety Type
974 | Potable water | Vol 1 | I’m unsure what the use of a “Resilience field (as an open text field?) is in these tables. Too much variability and not enough guidance around what data and format to enter. This is an AM (Vol 2) derivation anyway and not an “As-Built” attribute in my view. Whereas “Design Life” is. | Noted: no action required | Resilience Rating is a measured a6ttribute | 4.5 Resilience Schema | No action
975 | Potable water | Vol 1 | 2.3.4 The term Well should be changed to “Bore” | Sector Discussion | Commented on this previoulsy | 2.3.4 Well | More information required for a decision
976 | Potable water | Vol 1 | 2.4.3 The point feature is to be “snapped” to the pipe asset it is associated with. Does the spatial representation snapped to the polyline create a node? If not then this creates problems when modelling. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed | 2.5.3 Valve | No action
977 | Potable water | Vol 1 | 2.4.5 How is a locator cable or Intrinsic Protection (IP) cable for anti-corrosion ruining with a pipe (e.g. taped to the pipe) to be represented? Why in the table do we have to submit pipe diameter, nominal diameter, external diameter and nominal bore? This is overkill and one wrong piece of information will lead to confusion i.e. which one is the correct one? | Sector Discussion | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | 2.4.5 Pipe & 2.6.2 Cathodic Protection | More information required for a decision
978 | Potable water | Vol 1 | 2.4.7 Should the spatial representation include and ancillary works e.g. dry wells, wet wells, filters, air scrubbers or bio-filters (more applicable to wastewater PS I realise) | Noted: no action required | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. | 2.4.6 Pump Station | No action
979 | Potable water | Vol 1 | 2.5.2 Pumps, can take many types and forms. I trust the fields in the table are flexible enough to accommodate the variety to be expected. | Noted: no action required | We hope so. This will be tested during the pilot phase | 2.5.2 Pump | No action
980 | Potable water | Vol 1 | Is a backflow preventer to be considered a mechanical equipment asset or a valve? | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | 2.5.1 Equipment & 2.5.3 Valve | More information required for a decision | Back-Flow Preventer
981 | Potable water | Vol 1 | 2.6.1 Electrical asset – table doesn’t look accommodating enough for the variety of electrical fittings and assets to be expected | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | 2.6.1 Cabling | More information required for a decision
982 | Potable water | Vol 1 | 2.6.2 Good to see Cathodic Protection systems included. | Noted: no action required | Reviewed and Noted only | 2.6.2 Cathodic Protection | No action
983 | Potable water | Vol 1 | 2.8.2 reporting Mismatches could be problematic depending upon the spatial base used – see 2.1.1 above. | Noted: no action required | Reviewed and Noted only | 2.8.2 Matching to Existing Infrastructure | No action
984 | Potable water | Vol 1 | There are a heap more Definitions that could be added to the Glossary e.g. “trunk main” for starters. | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Glossary | More information required for a decision
985 | Potable water | Vol 1 | Request for code lists: On page 158 of volume 1 of the potable water standard there is mention of supplementary document 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016. Even though this document is in draft, I’d really like to take a look at it. Can it be made available for download, or am I to a copy emailed to me? | Sector Discussion | Code lists now incorporated into document | General | Change made document updated
986 | 3-Waters & Buildings | Vol 1 & Vol 2 | We appreciate the work put in by your team and the various working groups in developing these documents. The process of evaluating the standards has also been useful for Education as an agency, in promoting a review of our data collection processes and considering how these align with a potential implementation of the standards. Our comments on the standards focus at the strategic level. For our organization, with over 30,000 buildings, the cost of changing data collection are high. We therefore need to consider very carefully what information we capture, what decisions we will need to take with information, how we control the quality of information and how it is updated. For that reason it is important to us that we understand the proposed benefits and implementation uses of the standards before taking firm decisions on data collection for their use. We look forward to further discussion on implementation. Your presentation at the last governance group was a helpful insight into your team’s thinking: we want to ensure that agencies understand each other before committing to implementation or advancing a business case with Ministers. For that reason our comments are interim, subject to these further discussions. | Noted: no action required | Statement noted. | General | No action
987 | 3-Waters & Buildings | Vol 1 & Vol 2 | Overview of the Metadata Standards Education recognises the importance of asset information in protecting New Zealand’s ability to provide services in a fast-changing national economy. We also endorse a commitment to standardising and sharing information between public agencies. However, we have concerns about the detail and structure of the data proposed in the metadata standards. A challenge in commenting on the proposed metadata standards is understanding the objectives of the data collection process. It remains unclear how this information will be used, what elements of the process will be compulsory and how the comparison between agencies will work. Education is concerned that the costs of collecting the information outlined in the metadata standards will exceed the benefits. Understanding the benefits derived from these comparisons is critical to determining what data should be collected and how it should be categorised. For instance, the data that is needed to promote All-of-Government procurement is very different from the data needed to identify major network risks within New Zealand | Noted: no action required | Statement noted. Business case. | General | No action
988 | 3-Waters & Buildings | Vol 1 & Vol 2 | Education is also concerned that the focus on the physical condition of the assets may be poorly targeted. Rapid changes in demographics profiles, technology and consumer preferences will also have a major impact on the ability of the current asset networks to meet the future needs of communities. We think that the metadata project should place as much emphasis on the ‘fitness for purpose’, as it does to the physical condition. | Noted: no action required | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | General | No action
989 | 3-Waters & Buildings | Vol 1 & Vol 2 | In addition, the metadata standards assume that decisions on asset maintenance are made centrally. Where maintenance decisions are made is a policy choice that is influenced by broader factors than asset management. In the case of Education, asset maintenance decisions are largely managed at a school level. This is a fundamental premise of how the management of schools is devolved to local communities. This is more responsive to the needs of local communities, as well as meaning minor maintenance decisions can be made in the context of education delivery. However, this also means that, while we fund schools for maintenance, we do not specifically control how that funding is spent. This limits the extent to which Education is able to track maintenance expenditure. | Noted: no action required | This standard does not assume where or how decisions are made, it is a set of metadata standards that define decision elements for analytics to support those decisions - in a standard way | No Specific Reference | No action
990 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: Education’s documentation for new construction includes much of the data outlined in the Metadata standards. However, while we collect and hold this information for each project, we do not capture this data into a central database. The nature of this information is useful when looking at the details of potential redevelopment of an asset but not for evaluation at a portfolio level. As with our response to the overall project, Education believes that clearly articulating the benefits of the process will better inform how and what information needs to be collected. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
991 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: We are aware that much of the information for as-built projects will be provided by the contractor. However, we have concerns that the rigorous specification of data may limit the pool of contractors to larger firms with the resources to provide information in a metadata standard. There is a risk that this reduces competition in the industry, and creates price increases especially in provincial centres where Education operates. Education’s exposure to price increases with small building firms is more pronounced than other government agencies who may build a smaller number of more complex facilities (e.g. Courts, Corrections, Defence). | Included | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | N/A | No action
992 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
993 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | Repeat | N/A | No action
994 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education’s ability to maintain the quality of data is also limited by the devolution of maintenance and minor capital works to schools. Most of the subsequent alterations to buildings are controlled by the schools. Reconfiguring teaching spaces is a regular occurrence across the portfolio but it is unlikely that these changes will be updated in as-built records. | Noted: no action required | Implementation considerations are out of scope | General | No action
995 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The detail of components specified in the metadata standards appear to be very granular for many of Education’s buildings – for instance there are about 200 fields to describe a building ceiling. The majority of Education’s building will be a simple domestic-scale or light industrial structures, where there is little benefit in collecting this level of detailed information. | Noted: no action required | Implementation considerations are out of scope | General | No action
996 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education would recommend that different levels of information are collected for different types of assets. For instance, complex multi-storey buildings with lifts, fire protection and science laboratories, would require more extensive data to be collected than single-storey wooden-structure school buildings. | Noted: no action required | Implementation considerations are out of scope | General | No action
997 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The information Education collects on underground services varies greatly depending on the scale and nature of the development. Many of Education’s developments are additions or small schools in provincial locations, with work undertaken by local building firms. The ability of small contracting firms to record in detail where underground services are located is poor, and records are unlikely to be available in an electronic format. Detailed collection of this data may be appropriate for major assets. However, we recommend that collection of geospatial information on underground services is restricted to the larger or more complex developments. | Included | Implementation considerations are out of scope | N/A | No action
998 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The risk assessment analysis in the proposed standards is difficult to interpret and evaluate especially for the type of assets being developed by Education. The scale of Ministry buildings tends to be domestic or light industrial in scale. The risk implications for different components of the assets (such as the roof) cannot be easily separated from the risk profile of other components of the building. We recommend this aspect of the risk criteria of the Metadata standards be critically reviewed. | Sector Discussion | The standards make the separation of components and the analysis of risk at a component level of granularity possible. There will be a further discussion about this level of recording with the technial working group. | No Specific Reference | More information required for a decision |  | Leave as is - there is a need to determine, during implementaiton, if it is optional (or mandatory) to collect this level of information. Need the ability to tag against a room or a building, as well as against a component | nil | This is an output from the pilots, as agreed at the workshops |  |  |  | No further action
999 | 3-Waters & Buildings | Vol 2 | Broad comments The focus of the data collection is around the building envelope (walls, roof) with significantly less focus on the interior assets. However, building interiors represent a large component of the total cost of providing assets and are the components with the shortest life expectancy. The interior configuration has a major influence on the ability of school buildings to generate positive educational and social outcomes. For these reasons, Education believes the metadata standards should have a greater focus on the interior assets and configuration. | Noted: no action required | All components are collected, including interior components | No Specific Reference | No action
1000 | 3-Waters & Buildings | Vol 2 | Broad comments As well as the definition of the data held, the metadata schema will need to outline the data structure and hierarchy. If information is not collected at a consistent level in the asset hierarchy it makes comparisons between entities difficult. For instance, it is difficult to compare what proportion of the portfolio has fitted wall insulation, if one agency collects the information by building and another by facility. This aspect of the standards should be reviewed. | Noted: no action required | Data Classification, Heirarchy and Structure are all outlined in the Draft Standards | No Specific Reference | No action
1001 | 3-Waters & Buildings | Vol 2 | Broad comments The amount of information collected about the assessor for each data category is unnecessary. It is always useful to know who undertook the assessment but the collection of qualification and experience against each asset is excessive. This detail should be replaced with a measure of confidence around the measures, such as whether it was the result of an exhaustive analysis or a desk-top assessment. | Noted: no action required | Each organisation will decide at what level of granularity (detail) it collects tdata to manage its assets. | No Specific Reference | No action
1002 | 3-Waters & Buildings | Vol 2 | Detailed comments on categories of data The metadata standard outlines the format and categorisation of data on the assets. The following considers each of the categories individually. It discusses these in broad terms and then outlines how Education collates and reports of these asset categories. | Noted: no action required | Statement noted, no action required. | No Specific Reference | No action
1003 | 3-Waters & Buildings | Vol 2 | Condition: The metadata standards propose that condition measures categorise assets by: structure; external; interior; services; and fittings. Separating external cladding and structure is a useful differentiation for some of the housing and light commercial categories. The detail captured on the interior is overly simplistic. The proposed metadata standards focus on cosmetic issues such as the quality of the paint finish, rather than configuration and functionality which is of greater importance for Education. As noted above, interior components represent around one-third of the total building cost and have the highest depreciation rates/shortest lives. Ministry measures: The broad asset categories used by Education are: external; interior; services; and roof. More detailed condition data is held for individual schools but the revaluation and portfolio reporting for Education uses these four categories. Education is currently reviewing options to measure how different building design and fabric choices impact on the light, air quality, temperature and noise levels in teaching spaces. | Noted: no action required | Condition Elements are covered in detail in the standards They do not differentiate buildings by type, beyond the Building Code definition of Facility Importance (which is not building type) These are asset metadata standards, not portfolio form / function and mix standards | 2.2 Condition Schema Code List 13: Facility Importance Rating | No action
1004 | 3-Waters & Buildings | Vol 2 | Repairs and Maintenance The definitions of repairs and maintenance defined in the metadata standards are reasonable and workable. 1. However, collecting data on deferred maintenance items is too complex and unproductive. Part of the issue is that subsequent work may override the maintenance items, but be difficult to identify and measure. Under-maintaining an asset may be best reflected in the condition assessment process. 2. Ministry measures: Education currently identifies programme maintenance items to be undertaken on a building, including recurrence timeframes. Education also categorises the reason for maintenance according to priority (i.e. health and safety, protection of building etc). While Education has a good knowledge of the budgeting for repairs and maintenance, it does not track specific expenditure, accountability for which has been devolved to schools. This means that the explicit scope of work that has been undertaken is not available in Education’s information systems. | Included | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
1005 | 3-Waters & Buildings | Vol 2 | Utilisation: The utilisation measures by nature need to be specific to the industry in which the agency operates and would tend to be for internal reporting only. There is limited advantage in establishing utilisation standards for comparison between entities with very different objectives. This is more appropriately a component of the annual reporting to stakeholders rather than a metadata measure. Ministry measures: Currently Education has a formula for entitlement of classrooms and other space based on school enrolments. Education measures schools’ provision of space compared to entitlement with an optimal target range of 85% to 105%. | Noted: no action required | Agreed, but the standards apply across all Sectoirs (e.g. Housing Providers) | 3.2 Utilisation | No action
1006 | 3-Waters & Buildings | Vol 2 | Demand There are several problems attempting to identify demand for an asset. These are compounded for school assets, which provide free and compulsory services. Commonly residential and light commercial facilities have a variety of different demand parameters. For instance a school hall will support school assemblies, indoor sports activities and community events. Each of these demands has different physical requirements. Measures of demand are therefore difficult to establish. Ministry measures: Education regularly needs to address circumstances where the demand for a school exceeds its capacity. This would commonly be dealt with by strategies such as the application of enrolment zones. Education uses local and regional demographic trends amongst other inputs to identify demand for additional learning spaces and/or new schools. | Noted: no action required | Demand Section has been updated in Volume 2 And, there are many examples of useful demand analytics for schools | 3.3 Demand Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1007 | 3-Waters & Buildings | Vol 2 | Criticality Applying criticality to residential and light commercial buildings is more difficult than with infrastructure. The metadata approach to defining communities being serviced by public sector buildings is not viable. Communities which use public sector buildings tend to be complex and overlapping and criticality dependent on other assets within the network. The definitions of criticality should therefore be limited to explicit requirements in supporting post-disaster response or recovery i.e. identifying assets which have an explicit function defined by Ministry of Civil Defence and Emergency Management plans. Ministry measures: The criticality for the school as a civil defence centre is an agreement between Civil Defence and the Board of Trustees. This will partially be dependent on other community infrastructure in the location. Schools which are Civil Defence centres are not identified within Education’s central information systems. | Noted: no action required | Critciality will be closely linked to Faclity Importance per the Building Code | Code List 13: Facility Importance Rating | No action
1008 | 3-Waters & Buildings | Vol 2 | Risk The metadata schema for risk measurement works to associate risks with asset components. For most of the risks (e.g. earthquake, flooding) it is more appropriate to associate the risk with a building or site, rather than individual component (e.g. roof). Ministry measures: Education has risk registers at a portfolio level and each school has a risk register. Some of the risks associated with the assets relate to the use of materials (e.g. asbestos). These are also logged on the school risk register but not captured centrally. | Included | Risk can be applied at any level of granularity Analytics enable Portfolio level of risk to be established | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1009 | 3-Waters & Buildings | Vol 2 | Resilience The resilience measures have yet to be developed within the metadata standards. The focus of the resilience measures appears to be around major civil defence and emergency events, such as earthquakes. It will be useful to identify the ‘Importance Level’ as defined in building legislation. A sole focus of the civil defence component of resilience is too narrow. We believe the issues should also encompass the ability to change the use of assets or to reconfigure them for different demand or purposes such Ministry measures: When Education developed the business plan for transportable modular classrooms it aimed for these to constitute a proportion of the network to allow flexibility to respond to demographic changes. | Included | Resilience has been updated in the standards | 4.5 Resilience Schema | No action
1010 | 3-Waters & Buildings | Vol 2 | Design Performance The majority of the design performance schema appears to relate to items of equipment, such as pumps and piping. This represents a relatively small proportion of the assets within Education’s network. The majority of the network is relatively uncomplicated, one and two storey buildings, with limited HVAC or specialist facilities. Collecting design performance at the level of individual items is therefore of limited value. Ministry Measures There are some specialised assets within Education’s portfolio, such as lifts in multi-storey buildings. However, these are few in number and are managed under a national contract. Details on the design performance of smaller components, such as heat pumps are typically held by the school. | Included | There are also mant examples of building design perfomance (Earthquake Rating, Energy Rating etc.) | Table 14: Design Performance Examples | An explanation of Data Science will be provided for at the Technical Working Groups
1011 | 3-Waters & Buildings | Vol 2 | Financial Performance There has been significant effort to develop measures for financial performance within the standards. The proposed standards outline a detailed basis for the collection of valuation, depreciation, time of payment information. Rather than replicate data held elsewhere, it would be more useful to ensure that there are linkages with the agency’s broader financial system. This has the advantage of enabling association of asset measures with other agency performance measures, for instance measuring the asset cost per visitor or student. Ministry Measures Education has recently established a new asset management system (Tribal K2) which tracks budgeting for maintenance and other property costs. The system links to Ministry’s property data warehouse system. This allows analysis and development of a broad range of performance measures. The result is the ability to compare asset performance measures to aspects such as student numbers (e.g. the percentage of students learning in buildings that fall into each asset condition category). | Noted: no action required | Organisation specific financial analytics will be supported by attribution within this standard. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1012 | 3-Waters & Buildings | Vol 2 | Service Performance The service performance schema appears to be a raft of unrelated criteria, which individually may be critical to the functionality of the asset, but do not belong in the same category. The result is measures which relate to different levels of assets from components (e.g. disabled access) through to facilities (e.g. iwi interest). A number of the proximity measures, such as kilometres to communities are difficult to establish without further definitions of community. The result is a wide range of criteria which does not allow comparison between different agencies. Similarly, the raft of measures around district plan criteria, such as provision of car parks, is difficult to update. For many public service assets the land will be designated so underlying zonings will be poor indicators of the use of the site. Some aspects of the data, such as iwi values, heritage considerations or community interests, cannot be easily summarised into a data base. It would be better to include an identifier which would highlight whether more detailed analysis is available on file. Overall Education would advocate for service performance to be restructured into a number of separate themes. Ministry measures Education has a basis for evaluating the service levels called the Innovative Learning Environment (ILE) assessment tool. The information is currently collected at a building level and is a requirement of the five yearly capital and maintenance planning process. Education is evaluating ways of standardising the capture of the information. The ILE assessment tool also has facility to include a range of qualitative measures such as ‘how well the design reflects the needs of the local community’ which may be developed in future. | Noted: no action required | No action required with regards to comment son the business case. The standard is intended to system and organisation agnostic. | 5.4 Service Performance Schema | No action
1013 | 3-Waters & Buildings | Vol 1 & Vol 2 | Introduction The Auckland Council family fully supports of the intention behind this standard and has actively contributed in the working groups for roads, residential housing and light commercial buildings and the three waters. The Auckland Council family welcomes the opportunity to provide feedback at this time, and the opportunity to participate in the further development of the standard. The metadata standard is a great opportunity to gain national consensus of what minimum level of data capture is required. This initiative will enable us to ensure that data can be applied in a consistent and repeatable way to make good asset management decisions based on acceptable levels of service, replacement and growth strategies. | Noted: no action required | Statement noted. | General | No action
1014 | 3-Waters & Buildings | Vol 1 & Vol 2 | Summary Feedback is currently sought with specific regards to the three waters and the residential housing and light commercial buildings standards. We have found it difficult to provide meaningful feedback in the absence of a clear strategic message, an understanding of which is shared by all reviewers. That message needs to link the standards to the business case and to recently held discussions with the Minister of Finance. A further opportunity to work on and develop the standard from the ground up, in the way that the transport group has developed the roads standard, would also help the Auckland Council family to feel more confident about the result. To that end we suggest that it would be useful to incorporate such an opportunity into the process from here. We would like: • To present our feedback to the combined governance group • The working groups to review and address all feedback on the standards • The resulting outputs to be made available for consideration by the governance group prior to any public release of the standards | Noted: no action required | Discussions will continue across the Infrastructure Sectors (Core and Social) | No Specific Reference | No action
1015 | 3-Waters & Buildings | Vol 1 | Volume 1 – As-built metadata standard What we like: • Provides reasonable coverage of possible data fields • As a collection of possible attributes it will help to drive a culture of good practice to capture metadata • It brings attention to the need for good base data What we consider could be further developed: • In its current format the standard is not adoptable due to the constraints it will place on systems and business processes this needs to be addressed before it can be adopted. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Close, this is to be answered as part of implementation | nil | This is an output from the pilots, as agreed at the workshops |  |  |  | No further action
1016 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • The layout should be modified to clarify the distinctions between master data and metadata. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | include a note/definition as to what Master Data is | speak to haydn | Master Data (or primary data) is defined as the primary data set. It is the data which is normlly held within an Asset Management Information System and used for the systematic analysis to inform evidence-based investment decisions. Secondary data are other data sets which are used from time to time to suppliment asset data (for example planning data) in order to deepen the analytics and underastanding of an asset in certain circumstances (in a plan change) | N/A |  |  | No further action
1017 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • A number of elements have been included but are not complete, and an understanding of industry definitions, hierarchies and processes is required to complete this volume. We would welcome the opportunity to assist with this. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | GISSA to undertaken assessment | follow up by GISSA | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - this is to be discussed during implementation |  | No further action
1018 | 3-Waters & Buildings | Vol 2 | Volume 2 – Asset management performance standard What we like: • Recognition of the notion that data is only useful if it is used • An approach that recognises the value of rigorous analysis to inform decision making What we consider could be further developed: • In general, we consider that this volume is under developed with inconsistencies and cross-overs to Volume 1. We would welcome an opportunity to further input into its development, as we recognise that it can provide a useful tool, particularly for organisations with limited capability in this area. | Noted: no action required | Volume 2 is now a comprehensive document | No Specific Reference | No action
1019 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • This volume assumes generalist practices that are inadequate for non-linear assets and includes operational and derived data that is not suitable for inclusion in an AMIS system. | Noted: no action required | This volume is spatially aware, and will attribute point, line, ployline and 3D objects. It is also agnostic to any AMIS and GIS system | No Specific Reference | This will be discussed at the technical workshops
1020 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Needs to be carefully framed for the asset types that it relates to. | Noted: no action required | Asset types are specifically defined within the standards - See Volume 1 of each Group of Assets | No Specific Reference | No action
1021 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Replacement trigger points should be broadened from reliance on subjective visual condition to incorporate best practice for optimal replacement, that is, based on objective measurement and sound engineering judgement. | Included | Visual inspections are only one type of condition assessment to trigger an interventi. Capacity could be another (at Very High > 95%) | Code List 31: Demand – Capacity Unit of Measure | No action
1022 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Reference should also be made to failure mode effects analysis (FMEA/FMECA) as a means to support optimal replacement points. Our feedback does not further consider this volume due to the large disparity with practice and limited workshops to fully capture industry needs. | Included | The standards do not preclude failure mode analysis of any type. The standard captures some of the attributes for this analysis. | 2.3.5 Code Lists | This will be discussed at the technical workshops - mor ework is required here with the sector
1023 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 1. Create a separate volume that covers strategic fit and business needs across all asset categories. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1024 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 2. Focus on a business standard for assets including improving the hierarchy to cover both asset and data hierarchies and outline the relationship between them. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | No Specific Reference | No action
1025 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 3. Review publishing formats to maximise the impact of the standard. | Included | The drafts have now had a full publishing edit | General | No action
1026 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 4. Remove content that is not related to the business standard including those referring to implementation paths, delivery mechanisms and quality control rules. | Sector Discussion | To discuss - for example? | General | More information required for a decision |  |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - this is to be discussed during implementation |  | No further action
1027 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Workshops The working groups were presented with A-Spec as a straw-man and tasked to focus on the possible data that could be captured for individual asset types. The working groups started with limited traction and concern was raised early on as to the purpose of the workshops in diving into attribute detail that is quite easily obtainable from various sources. A basic data hierarchy was established that allowed the attributes to be tackled in a constructive manner. In hindsight, it would have been useful to consider other industry standards as part of the process. We feel that such consideration could still be undertaken as part of the follow on from this feedback. Despite the concerns mentioned above, the workshop groups generally worked well and came to agreement on the things that were required. It would be extremely useful for the working groups to go over the feedback and address it as appropriate. Strategic, governance and procedural feedback should also be reviewed by the governance groups. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | General | No action
1028 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Definitions of industry terminologies and attributes. | Sector Discussion | Examples required | General | More information required for a decision |  |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - this is to be discussed during implementation |  | No further action
1029 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Identification of business needs. | Noted: no action required | Business case will outline / describe benefits | N/A | No action
1030 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • An assessment of “fit for purpose” data capture. A matrix and understanding of the minimum data capture required based on organisational needs. | Noted: no action required | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | N/A | No action
1031 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Exploring the origin of the data and identifying whether it belongs to volume one (As constructed) of these standards or is better suited with other data sources, for example geotechnical data. | Noted: no action required | These data sets are what are required for asset management purposes | General | No action
1032 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Validation of the Codes list or optional pick lists. | Noted: no action required | Reviewed and implemented | General | No action
1033 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • The standard is required to be system agnostic. Identifying how the standard will be implemented has an effect on the data capture requirements. To enable this we need to understand what the systems and processes look like. The standard needs to be reconciled with these systems and processes at organisation level. | Noted: no action required | Updated | General | No action
1034 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Comparison to international practice and other complimentary standards. | Sector Discussion | Information to be provided for discussion | General | More information required for a decision |  |  |  | There has been a number of reviews against international standards. These (eg OGC) have been aligned to the standards. We will continue to review the standards throughout the pilot for application, due to the variable nature of these standards |  |  |  | No further action
1035 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • There is a logical split between roads, buildings and three waters; however there is less logic to further splitting up the three waters when the majority of the components and attributes are the same. It would be sensible to consider consolidating these. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
1036 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Rather than repeating the introductory statements in both volumes of each version of the standard a covering or base document (as seen in most other standards) should be considered, as the principles of data collection are the same. This would also have the advantage of slimming the volumes down. | Noted: no action required | Format based on technical differentiation | General | No action
1037 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Common data sets are repeated at every asset class adding unnecessary volume. | Noted: no action required | Action on data scientists. | General | No action
1038 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • The standard seems to reference the manner in which data will be collected. This is the responsibility of the various organisations and should not form part of the standard. | Noted: no action required | This is not within the scope of these standards | General | No action
1039 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The document will benefit from a better structure around the rationale, strategic drivers and added benefits, of the standard. Some of this information is scattered across the introduction section but it could be strengthened and focused on the purpose of the standard, which is about agreeing on common classifications and definitions. We think there is general agreement that data standards are needed and this doesn’t need to be emphasised. | Noted: no action required | This is not a policy report, an asset management plan, nor a 30 Year Infratsructure Plan (where you would find this requirement). This is a metadata standard for assets at an assetID level of granularity. It does however capture the context of the analytics which inform these types of documents which support organisations asset management | No Specific Reference | No action
1040 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • We believe that the key purpose of this standard should be to outline data requirements that enable organisations to compare their performance and share asset lifecycle knowledge while continuing to measure their performance in a meaningful and cost effective manner in the context of their strategic objectives. | Noted: no action required | Statement noted. | General | No action
1041 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The intention of this standard development was to produce a metadata capture culture and identify the appropriate level of capture. This intention has been somewhat obscured by the very much “field-base” information that is supplied by suppliers and contractors on the physical attributes of assets. We believe that it would be useful to reconsider the audience of this standard and review it to ensure that the audience is appropriately targeted. In that way the business strategy can direct appropriate attribute fields, which will then be common sense as long as common definitions are understood. | Noted: no action required | This observation describes on audience, this is not the only audience, for example design engineers. | General | No action
1042 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Data capture, as acknowledged in the standard is but one component of good asset management and the ways in which this initiative will support organisational challenges such as achieving ISO 55001 accreditation could be made clearer within it. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1043 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The standard strategic goal is to enable organisations and the country “to collect locally and use globally”. It is unclear how this standard compares and incorporates international best practice. There are examples of other international metadata standards however only A-Spec was examined. | Noted: no action required | A number of other standards have been investigated. (Uniclass, Cbi, Omniclass, Master Spec etc. etc.) The strategic goal is to enable organisations and the country “to collect locally and use nationally” | No Specific Reference | No action
1044 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The way in which the standard is currently written presents the data capture requirements in a set manner and format thereby requiring business needs to be moulded for the data specific needs. These limitations are likely to prevent users from taking opportunities in system and process advances that may become available. Some of these initiatives already exist such as open data sources from product suppliers. We expect these advances to become more readily available in the future. It is not clear how the static two-dimensional model presented by this standard will allow business to incorporate these changes. | Noted: no action required | The standard does exactly the opposite to what this is suggesting. The question is not so much about how it is collected but how the data is manipulated into a common format when it is (see FME) | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1045 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Existing systems have been heavily invested in and are very diverse, even in the Auckland council family, to tailor for specific needs. With the possibility of the standard purely becoming a mapping exercise; it then does not support the need to prescribe data fields to intricate detail. The level of data capture required to complete the national level analytics is not identified. Anything else is considered optional and does not support the reason for capturing data at every level. | Noted: no action required | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. But Note use of tools like FME. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1046 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • In order to address the matters referred to in the point above, the standard could be reconfigured to provide the required performance outcome and guidance on how these requirements may be met, while allowing flexibility in means and methods of demonstrating compliance. | Noted: no action required | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. And, there are many analytcal options on the same data sets depending upon he problem being solved. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1047 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • As has been mentioned previously, the document uses terminology and jargon that is not consistent with those used in NZ. This is an easy fix, and appropriate language is a great factor in the ease of adopting new things. | Included | The drafts have now had a full publishing edit | General | More information required for a decision | [7 empty] | No further action
1048 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • There are plenty of NZ examples of assets of each class and type, and we will be happy to provide some if required. Using Australian examples in a NZ standard is not appropriate where there is a suitable local example available. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - refer notes under water volume 1 |  | No further action
1049 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • It is also important that the examples used are relevant to the asset type contemplated in the standard. Building examples for the residential housing and light commercial standard will make the logic of the approach more apparent. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision | [7 empty] | No further action
1050 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • Most of the terminology used in the attribute fields is not defined. Without these definitions data cannot be accurately mapped and the data collector will be left to assumptions that will compromise data integrity. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision | [7 empty] | No further action
1051 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • At the beginning of the working group workshops we agreed that these are business standards – hence system agnostic; this is even mentioned in the document. At the same time the proposed standard – language, data formats and terminology – has been prepared for an easy input to a functional specification for a GIS application. It is evident that the asset classification and the attributes were “flattened” to fit this particular implementation. This has detrimentally affected the business value of the standard – we have a number of attributes that do not belong to the asset class they are listed against. An example: in stormwater, swale only attributes are elevated at channel level, at which level they are meaningless. | Sector Discussion | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | General | More information required for a decision |  | GISSA/Haydn to work with Nick to complete mappings | follow up by LINZ | ON HOLD UNTIL FURTHER DETAILS PROVIDED TO BE FINALISED BY JUNE 30 |  | Closed: - duplicate |  | No further action
1052 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The current format of data requirements as a mix of business standard and specification is of particular concern. On one hand it makes the business part of the standard logic hard to follow, while on the other hand the document is not sufficiently detailed to be effective as a functional specification. As a consequence standard does not show the business what it needs to collect and the application vendors will not understand what they need to build. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Volume 3/4 conversataion | nil | OUT OF SCOPE - VOLUME 3&4 |  | Closed: - Implementation |  | No further action
1053 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The asset data hierarchy needs to be completed. Most importantly the way assets have been grouped for data capture needs to be reconsidered in order to represent the business asset hierarchy. Business hierarchy is of great importance for FMEA, operation and maintenance of complex assets, for example. The exclusion of business hierarchies from the standard will require every organisation to create another set of rules outside of the standard in order to maintain these relationships. | Sector Discussion | The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers that in turn will provide consistency to the asset owners. As each organisation has their own hierachy it is expected that they will categorise the data being provided according to their needs | General | More information required for a decision |  | Volume 3/4 conversataion | nil | OUT OF SCOPE - VOLUME 3&4 |  | Closed: - Implementation |  | No further action
1054 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • We strongly recommend that all implementation related fields be removed from the document, as outlined below: o Attribute abbreviations – these are in many cases system related setup and for instance instrumentation may be adopted by numbering systems such as ISA55 that is international practice. The purpose of these abbreviations is not clear. o Character length – This serves no purpose and is not supportive of being system agnostic. By providing full and proper definitions to the attribute field data may be mapped correctly, regardless of character lengths. o Comments – This filed has no purpose that cannot be fulfilled by either the unit filed or description fields o QA validation – These are rules set by business and specific software systems. It also does not serve any purpose to identify minimum capture level. This could be done in a better way through a developed hierarchy that identifies, master data from metadata and compulsory fields from conditional or optional fields | Included | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | General | No action
1055 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • To date geometrical and topology rules have not been discussed. Currently there are different requirements governing the way geospatial data is captured. As with the asset management systems, investment has been made in maintaining systems to these rules. From an analytics point this does not seem to have any impact on the analytic output. Development of such a standard is considered to be a separate endeavour in its own right and has the potential for having great cost impacts to organisations. In the same way one could argue other data sets must then be prescribed – such as geotechnical information, drawings and so on. Flexibility is key, as planning for known technology, given the pace of technological change, will mean that the standard is out of date before it is published. | Included | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | General | No action
1056 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • Attribute sets are not normalised across the asset classes. An example of this is the repetitive material types in the codes lists. (Note. Watercare, Wellington Water and Christchurch City Council were the only parties to receive the codes lists later on request. This was never published. | Included | It is acknowledged that codelists will need to be dynamic in nature and will be open to continued contribution from the sector. The code lists are now incorporated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | General | No action
1057 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • As-built data versus operational data versus derived data is crossed over between the volumes. Separation is required through the data hierarchy. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | a level of clarity around primary keys to be added to the documentation by GISSA | speak to haydn | An addition of explanation has been added to standards - completed | page 1 |  |  | No further action
1058 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 1. Create a separate volume for strategic fit and business needs | Noted: no action required | To discuss | No Specific Reference | More information required for a decision | [7 empty] | No further action
1059 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Improve the Asset Hierarchy section to cover both asset and data hierarchy and to outline the relationship between them. | Included | Asset Classifications have been defined in the Standards | General | No action
1060 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and simplify attributes specifications; all attributes that do not belong to the As Built standard, such as demand, repair and maintenance, health and safety issues, service and financial performance should be removed. These are time related measures and events that are covered by other parts of the standard. Connecting these events and measures to assets is the subject of asset analytics, not the as built standard. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
1061 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and clean the attribute tables – remove all values that are included as they are not relevant. | Sector Discussion | The standards have harmonised and standardised data and hierarchies across the standards | General | More information required for a decision |  |  |  | COMPLETED PRIOR TO MAY 1-3 WORKSHOPS |  | Closed: - completed |  | No further action
1062 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Clean the relationship between asset classes, attributes and values. One asset class has to belong to one asset category. | Included | Asset Classifications have been defined in the Standards | General | More information required for a decision | [7 empty] | No further action
1063 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Outline a list of core asset characteristics – the whole concept of the standard as vehicle for comparability becomes meaningless if we don’t agree on a few critically important attributes that must be collected. | Noted: no action required | Mandatory, Optimal, Optional will be discussed with the sectors | No Specific Reference | More information required for a decision | [7 empty] | No further action
1064 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Our recommendation is to add a section on asset geometry and topology for water networks – but not one that could be mistaken for a specification for GIS applications. This section needs to address the core rules for creating geometric networks and outline the participation of all assets in these networks. | Included | Included in the draft Standards | General | No action
1065 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Since all standards are related and are part of the same suite of documents it would make sense for them to be published as related volumes (chapters?) rather than independent books. | Included | This has been reviewed, and a decision to keep as separate documents made - at this time (the documents would be 300+ pages if combined | No Specific Reference | No action
1066 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Another approach to publishing standards which would be effective is by using links to look up the list of attribute values. | Included | Other access toolss will be reviewed before release in July 2017 | No Specific Reference | No action
1067 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Think about publishing the data tables in a data view in addition to the document | Included | Included in the draft Standards | General | More information required for a decision | [7 empty] | No further action
1068 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 4. Remove content that is not related to the business asset data standard: • We strongly recommend that all references to implementation paths, delivery mechanisms and quality control rules be removed from this document. This should be a subject to a separate project/ research due to the variety of business models that can be applied. Unless there is a directive for a centralised implementation of these standards, they remain the responsibility of each organisation and have to be adapted to the particular technology platform. | Noted: no action required | Unclear of where there are examples of this | No Specific Reference | No action
1069 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1070 | 3-Waters | Vol 1 | Asset class definitions needed: Need clear definition of asset classes. Channels are particularly bad examples; they cover a range of assets with various function and purpose - and badly. Under current structure there is no way to describe sw treatment devices. | Sector Discussion | Classifications and types defined in the standards Refer to code lists | General | More information required for a decision
1071 | 3-Waters | Vol 1 | Attribute definitions needed: Many definitions are unclear or missing. Some appear to be database oriented - need to be business meaningful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1072 | 3-Waters | Vol 1 | Standard is about structured data, not any information about assets: This standard should cover the data that needs to be captured in as structured way for further analytical and reporting use. Hence all data that has no such value needs to be removed. In complex assets most of the asset specific data is kept in operation manuals and other operation related documentation. | Noted: no action required | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | General | No action
1073 | 3-Waters | Vol 1 | This is volume one - as constructed assets. Remove all data that is not relevant to as constructed - there are other volumes that this data is described | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1074 | 3-Waters | Vol 1 | Huge number of attributes that are not relevant and not agreed. Need to go back to the workshop discussions and agree how feedback following working sessions will be captured - cannot afford to continue like that. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1075 | 3-Waters | Vol 1 | Renewal material in pipes. This should be relabeled to say lining material. | Included | Attributes included, lining material included in standards see code lists | General for Pipes | No action
1076 | 3-Waters | Vol 1 | Missing attributes. Lining material installation data is critical | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
1077 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Noted: no action required | Information to be provided for discussion refer to ID1069 | General | More information required for a decision
NEW001 | 3-Waters | Vol 2 | Code List 9 - people with a spade won't understand the difference between these codes, as they are all the same thing to the person on the ground | Codelist 21 on page 45 |  |  |  |  | Sector Discussion |  |  | Action: - Graeme to provide a new table to Haydn, who will copy and replace the existing table | Graeme provide the codelist | Christchurch | DUPLICATE see NEW005
NEW002 | 3-Waters & Buildings | Vol 1 & Vol 2 | In volume 2 there is a space to define mandatory - but there isn't the same in volume 1. what's going on? |  | General |  |  |  | Sector Discussion |  | understanding the importance of data, and what is essential v optional, will be determined during initial implementation | understanding the importance of data, and what is essential v optional, will be determined during initial implementation | Action: - Haydn Remove the mandatory field from volume 1 | Haydn | Completed
NEW003 | 3-Waters & Buildings | Vol 2 | Need to include an attribute where something hasn't been assessed yet |  | General |  |  |  | Sector Discussion |  | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty |  | Action: - George to add 'not assessed' as an attribute where needed | GISSA | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty
NEW004 | 3-Waters & Buildings | Vol 1 & Vol 2 | There are potentially occurances where the standards include code lists, where not enough information is known to make the code lists finite - suggestion that these code lists are flagged as being examples etc |  | General |  |  |  | Sector Discussion |  | Completed Added to standard |  | Action: All required additions/changes to code lists to be provided to GISSA by COB 2nd June 2016 | GISSA | Completed Added to standard
NEW005 | 3-Waters & Buildings | Vol 2 | Table 2 - looks more transactional than elemental, why connected to an 'event' rather than directly to the 'table'? |  | General |  |  |  | Sector Discussion |  | Multivariate analysis | multivariate analysis | Action: Nick and Haydn to discuss and determine if changes are needed to the standards pre relase | Haydn | No further action required

## Workshop 2 Buildings Vol 2
NZAMS - Sector Feedback - Final Version (Workshop 2 Buildings Vol 2)
ID | Standard | Volume | Feedback | Status Included, Excluded, Sector discussion, Noted: no action required | Final Comments for Publication | Section Reference in Final Version - per Contents page | Additional Work | Proposed Codelists / Attributes | outcome from workshop May1-3 LINZ notes | Notes / Updates | Ref | outcome from workshop May 24-25 LINZ notes | GISSA/Other | Actions taken by whom and when | ACTION TAKEN
1 | Potable water | Vol 2 | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Completed with Metaconnect | No Specific Reference | No action
2 | Potable water | Vol 2 | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Included | Completed with Metaconnect | No Specific Reference | No action
3 | Potable water | Vol 2 | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Included | Completed with Metaconnect | No Specific Reference | No action
4 | Buildings | Vol 2 | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Included | Completed with Metaconnect | No Specific Reference | No action
5 | Stormwater | Vol 2 | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | Completed with Metaconnect | No Specific Reference | No action
6 | Stormwater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
7 | Wastewater | Vol 2 | Should be "coordinate reference system" as in ISO 19111 | Included | Standards are OGC spatial attribution compliant | Use of the Specification | No action
8 | Wastewater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
9 | Potable water | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | not required in this section, covered in later sections | Use of the Specification | No action
10 | Potable water | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
11 | Potable water | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
12 | Potable water | Vol 1 | or vertical datum | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
13 | Potable water | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | changed precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | Change made document updated
14 | Buildings | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
15 | Buildings | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
16 | Stormwater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
17 | Stormwater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
18 | Stormwater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
19 | Stormwater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
20 | Wastewater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Updated in draft standards | Use of the Specification | No action
21 | Wastewater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
22 | Wastewater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
23 | Wastewater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Updated in draft standards | 2.1.2 Projections and Datums | Change made document updated
24 | Wastewater | Vol 1 | Update to NZVD2016 | Included | Updated in draft standards | Glossary | Change made document updated
25 | 3-Waters | Vol 1 & Vol 2 | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General | No action
26 | 3-Waters | Vol 1 & Vol 2 | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Noted: no action required | Reviewed and Noted only | General | No action
27 | 3-Waters | Vol 1 & Vol 2 | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference | No action
28 | 3-Waters | Vol 1 & Vol 2 | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | Included | The drafts have now had a full publishing edit | General | Change made document updated
29 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Noted: no action required | The adoption of extents of fields is determined ny each organisation | General | No action
30 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General | No action
31 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General | No action
32 | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | Noted: no action required | Future work is yet to be determined | General | No action
33 | 3-Waters | Vol 1 & Vol 2 | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | Included | The classification has been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
34 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | Included | The classification has been defined in the Standards Code Lists included | General | No action
35 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | Included | The classification has been defined in the Standards | General | No action
36 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | Included | Asset Classifications have been defined in the Standards Code Lists included | General | No action
37 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy | No action
38 | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Noted: no action required | The adoption of extents of fields is determined by each organisation | General for Hierarchy | No action
39 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference | No action
40 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference | No action
41 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics | No action
42 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums | No action
44 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Included | Adjustment will be made to standards | General | Change made document updated
45 | 3-Waters | Vol 1 & Vol 2 | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Noted: no action required | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. | General | No action
46 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Noted: no action required | Reviewed and Noted only | General | No action
47 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Included | Photographic Evidence is an optional attribute | General | change made document updated
48 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Noted: no action required | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General | New Code List proposed | Health & Safety Type
49 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Included | Adjustment will be made to standards | General | Change made document updated
50 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | No action
51 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | No action
52 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | Included | Code lists included in standards | 2.3.3 Retaining Structure | No action
53 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Sector Discussion | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | No action
54 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves | More information required for a decision
55 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Noted: no action required | These standards are not about Treatment Plants | General | No action
56 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | Included | Code lists included in standards | General Equipment | Gauge input from next review
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail.
58 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments | No action
59 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | Gauge input from next review
60 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General | No action
61 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | Change made document updated
62 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | Change made document updated
63 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA)
64 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | Noted: no action required | resolved in updated version | 2.5.1 Equipment | Change made document updated
65 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
66 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision
67 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision
68 | Stormwater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | AddCCTV & Laser Profiling testing to code list testing type | General | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
69 | Stormwater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Sector Discussion | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | New attribute proposed | Installer of Asset
70 | Stormwater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Sector Discussion | Reviewed and Noted for Inclusion | 2.3.4 Pipe | More information required for a decision
71 | Stormwater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | General | New Code List entry for Condition Assessment Type proposed | Deflection Test
72 | Stormwater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
73 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
74 | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
75 | Stormwater | Vol 1 | Deflection Test result | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | New Code List entry for Condition Assessment Type proposed | Compaction Test
76 | Stormwater | Vol 1 | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not)
77 | Stormwater | Vol 1 | Seal Access Safety | Sector Discussion | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber | New Code List & entries proposed | Health & Safety Type
78 | Stormwater | Vol 1 | Manufacturer Manufacturing Standard Third Party QA Accreditation | Sector Discussion | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
79 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.4.4 Pipe | New attribute proposed | Rigid or Flexible as option
80 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling
81 | Stormwater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | Additional entries included in Code list Condition Assessment Type
82 | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling
83 | Stormwater | Vol 1 | Rigid material standard and QA Separate Flexible material standard and it's QA | Sector Discussion | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA
84 | Stormwater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test
85 | Stormwater | Vol 1 | Compaction strength per NZS4566.2 | Sector Discussion | More information required for a way forward | 2.4.4 Pipe | More information required for a decision
86 | Stormwater | Vol 1 | Third Party QA for pipe material manufacturer | Sector Discussion | Third Party QA Accreditation to code lists | 2.4.4 Pipe | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list
87 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
88 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing
89 | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing
90 | Wastewater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
91 | Wastewater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments | New attribute proposed | Installer of Asset
92 | Wastewater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
93 | Wastewater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | 1.7 Heirarchy | Create entries Desktop Visual cctv laser etc
94 | Wastewater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
95 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
96 | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
97 | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option
98 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling
99 | Wastewater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | More information is required to inform a way forward | 2.3.4 Pipe | More information required for a decision
100 | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling
101 | Wastewater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Compaction Test per NZ4566.2 Foundation strength pre-install
102 | Wastewater | Vol 1 | Compaction strength per NZS4566.2 or NZS3725 | Sector Discussion | More information required for a way forward | 2.3.4 Pipe | More information required for a decision
103 | Wastewater | Vol 1 | Third Party QA for pipe material manufacturer | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
104 | Stormwater | Vol 1 | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure | More information required for a decision
105 | Stormwater | Vol 1 | Spillway should be its own Asset Class | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure | More information required for a decision
106 | Stormwater | Vol 1 | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles | More information required for a decision
107 | Stormwater | Vol 1 | Source for what? This should have more detail. | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | Change made document updated
108 | Stormwater | Vol 1 | Does this include forebay bunds and pond banks associated with ponds? | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks
109 | Stormwater | Vol 1 | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure | More information required for a decision
110 | Stormwater | Vol 1 | Bathymetry Attribute? | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | Haydn suggest this is excluded as I think it can be sourced from LINZ
111 | Buildings | Vol 1 | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable | Noted: no action required | Reviewed and Noted only | General | No action
112 | Buildings | Vol 1 | The Hierarchy table works well | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy | No action
113 | Buildings | Vol 1 | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. | Sector Discussion | Reviewed and Noted only for discussion | General | No action
114 | Buildings | Vol 1 | Complex requirement for such a large property portfolio | Noted: no action required | Reviewed and Noted only | General | No action
115 | Buildings | Vol 1 | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles | No action
116 | Buildings | Vol 1 | This is a huge task for as constructed / as built for a large portfolio | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
117 | Buildings | Vol 1 | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | Reviewed and Noted only | General | No action
118 | Buildings | Vol 1 | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General | No action
119 | Buildings | Vol 1 | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | No action
120 | Buildings | Vol 1 | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes | More information required for a decision
121 | Buildings | Vol 1 | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) | Noted: no action required | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General | No action
122 | Buildings | Vol 1 | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
123 | Buildings | Vol 1 | V_Proc  what is this and what is it to relate to? | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
124 | Buildings | Vol 1 | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? | Included | Tables will be referenced in Final Versions | General | No action
125 | Buildings | Vol 1 | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 | More information required for a decision
126 | Buildings | Vol 1 | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof | More information required for a decision
127 | Buildings | Vol 1 | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision
128 | Buildings | Vol 1 | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision
129 | Buildings | Vol 1 | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone | Noted: no action required | This detail is to be provided at the time it was built not at time of capture This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint | No action
130 | Buildings | Vol 1 | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
131 | Buildings | Vol 1 | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint | Change made document updated
132 | Buildings | Vol 1 | Graffiti  irrelevant | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint | No action
133 | Buildings | Vol 1 | Flood  applicable only in related areas, and this information is on local council records | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint | No action
134 | Buildings | Vol 1 | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint | No action
135 | Buildings | Vol 1 | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint | No action
136 | Buildings | Vol 1 | Design life how is this applied to existing property | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
137 | Buildings | Vol 1 | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling | No action
138 | Buildings | Vol 1 |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
139 | Buildings | Vol 1 | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling | No action
140 | Buildings | Vol 1 | Finish  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
141 | Buildings | Vol 1 | Finish condition assessment, condition and repairs  ✓ The rest is superfluous | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
142 | Buildings | Vol 1 | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satisfy both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling | No action
143 | Buildings | Vol 1 | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
144 | Buildings | Vol 1 | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
145 | Buildings | Vol 1 | Design life  If new = Ok | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
146 | Buildings | Vol 1 | Cost  Not needed? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
147 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
148 | Buildings | Vol 1 | Too much detail required for ceilings. Condition, material, surface finish = Yes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
149 | Buildings | Vol 1 | Risk, Resilience, and Financial performance  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
150 | Buildings | Vol 1 | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
151 | Buildings | Vol 1 | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling | More information required for a decision
152 | Buildings | Vol 1 | Smoke_Barr  Smoke relevant to multiunit development only. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
153 | Buildings | Vol 1 | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling | Change made document updated
154 | Buildings | Vol 1 | Des_Life - ? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
155 | Buildings | Vol 1 | Cost ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
156 | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
157 | Buildings | Vol 1 | Whole page  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
158 | Buildings | Vol 1 | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor | No action
159 | Buildings | Vol 1 | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
160 | Buildings | Vol 1 | Live load rating of floor à too difficult to define | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
161 | Buildings | Vol 1 | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
162 | Buildings | Vol 1 | Repairs and Maintenance à what’s the need for this? | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema | No action
163 | Buildings | Vol 1 | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference | No action
164 | Buildings | Vol 1 | First 5 rows à Very detailed for residential use. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
165 | Buildings | Vol 1 | Bracing is as per ceiling notes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
166 | Buildings | Vol 1 | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision
167 | Buildings | Vol 1 | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision
168 | Buildings | Vol 1 | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
169 | Buildings | Vol 1 | Third row à Maybe | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
170 | Buildings | Vol 1 | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
171 | Buildings | Vol 1 | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
172 | Buildings | Vol 1 | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
173 | Buildings | Vol 1 | Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
174 | Buildings | Vol 1 | - Multi storey application only. Too much detail required. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
175 | Buildings | Vol 1 | Last 5 yellow rows à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
176 | Buildings | Vol 1 | - 2nd row à ? Building Code complaint for new works. Unknown for much existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
177 | Buildings | Vol 1 | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
178 | Buildings | Vol 1 | Thermal barrier à ? Floor insulation is all that is relevant in residential. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
179 | Buildings | Vol 1 | All pages à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
180 | Buildings | Vol 1 | Whole page à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
181 | Buildings | Vol 1 | Acoustic row, content  maybe Cost  X Rest of page  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
182 | Buildings | Vol 1 | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
183 | Buildings | Vol 1 | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
184 | Buildings | Vol 1 | Whole page  undefinable in existing housing. | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
185 | Buildings | Vol 1 | Vents  ✓ Membrane rows  Define what membrane? | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation | No action
186 | Buildings | Vol 1 | Foundation area, content à ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation | No action
187 | Buildings | Vol 1 | à See previous foundation notes | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision
188 | Buildings | Vol 1 | All pages à ✕ | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision
189 | Buildings | Vol 1 | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof | No action
190 | Buildings | Vol 1 | Load wind/fix  Not known in existing stock | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof | No action
191 | Buildings | Vol 1 | Frame_Tr  not always identifiable Frame_ Sp  why? | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
192 | Buildings | Vol 1 | Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
193 | Buildings | Vol 1 | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
194 | Buildings | Vol 1 | Last 3 rows  Is this needed and how is it defined? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
195 | Buildings | Vol 1 | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
196 | Buildings | Vol 1 | First row, QA Validation  N/A needs to be applied here | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof | No action
197 | Buildings | Vol 1 | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
198 | Buildings | Vol 1 | Last 5 rows  as per previous notes | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
199 | Buildings | Vol 1 | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
200 | Buildings | Vol 1 | Whole page  ✓ apart from: Cost row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
201 | Buildings | Vol 1 | First 3 rows  ? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision
202 | Buildings | Vol 1 | Last row, QA validation à Critical | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof | More information required for a decision
203 | Buildings | Vol 1 | Risk  ✓ Resil, Des_Perf  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
204 | Buildings | Vol 1 | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
205 | Buildings | Vol 1 | Whole page à ✓ Apart from Cost row à ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
206 | Buildings | Vol 1 | First 3 rows à? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
207 | Buildings | Vol 1 | critically, QA Validation à Critical | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
208 | Buildings | Vol 1 | All 3 rows  ? Row 3  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
209 | Buildings | Vol 1 | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
210 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
211 | Buildings | Vol 1 | All 4 rows  ✕, ?, ?, ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
212 | Buildings | Vol 1 | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
213 | Buildings | Vol 1 | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | No action
214 | Buildings | Vol 1 | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
215 | Buildings | Vol 1 | Whole page à✕. Risk – could relate to a water risks | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
216 | Buildings | Vol 1 | Whole page à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
217 | Buildings | Vol 1 | Classifications, Masterpec, Enclosure à not sure what this is representing? | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof | No action
218 | Buildings | Vol 1 | Ins-Type, R_Value à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
219 | Buildings | Vol 1 | Whole page  ✓ Insulation installer and warranty  maybe | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
220 | Buildings | Vol 1 | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
221 | Buildings | Vol 1 | Whole pink pages/part  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
222 | Buildings | Vol 1 | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls | No action
223 | Buildings | Vol 1 | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
224 | Buildings | Vol 1 | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
225 | Buildings | Vol 1 | Grout and Wall Structure Joint  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
226 | Buildings | Vol 1 | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
227 | Buildings | Vol 1 | Condition  ✓ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
228 | Buildings | Vol 1 | Structure, Bracing à As per floor and roof bracing | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
229 | Buildings | Vol 1 | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
230 | Buildings | Vol 1 | Wall, Design Life à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
231 | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
232 | Buildings | Vol 1 | Fire barrier à Multiunit. May not be known on existing stock | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
233 | Buildings | Vol 1 | Orange à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
234 | Buildings | Vol 1 | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
235 | Buildings | Vol 1 |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor | No action
236 | Buildings | Vol 1 | Whole page à why would we use this information? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
237 | Buildings | Vol 1 | Acoustic and Thermal rating à Not used. Where applicable? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
238 | Buildings | Vol 1 | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor | No action
239 | Buildings | Vol 1 | à Why / how would we use this? Too much information required. | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs | No action
240 | Buildings | Vol 1 | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs | No action
241 | Buildings | Vol 1 | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
242 | Buildings | Vol 1 | Pages  ✕ | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
243 | Buildings | Vol 1 | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision
244 | Buildings | Vol 1 | Framed and Frame material à not defined in window anatomy page 149 | Sector Discussion | Update diagram on p149 | 2.5.3 Windows | Modify Diagram
245 | Buildings | Vol 1 | Height of windows in mm à what value? | Noted: no action required | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | No action
246 | Buildings | Vol 1 | Condition  ✓ Width  why needed? | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision
247 | Buildings | Vol 1 | Manufacturer, warranty, installation date, installer àUnknown on existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
248 | Buildings | Vol 1 | Design life à How to define? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
249 | Buildings | Vol 1 | Repairs à ? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
250 | Buildings | Vol 1 | Page à✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
251 | Buildings | Vol 1 | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
252 | Buildings | Vol 1 | Hardware à Locks, Yes. Lever/knobs maybe. | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
253 | Buildings | Vol 1 | Whole Column Name – Full is circled à Not always known on existing. Why needed? | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows | No action
254 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
255 | Buildings | Vol 1 | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | No action
256 | Buildings | Vol 1 | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
257 | Buildings | Vol 1 | Services, pink section àmore commercial application. | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
258 | Buildings | Vol 1 | à No! How is this captured realistically and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components | No action
259 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
260 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
261 | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
262 | Buildings | Vol 1 | à Would we use this at a per item attribute? | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
263 | Buildings | Vol 1 | Type à ✓ Last row, content à NA | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
264 | Buildings | Vol 1 | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
265 | Buildings | Vol 1 | àToo difficult and unnecessary info | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
266 | Buildings | Vol 1 | à Stove have heater fans | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment | No action
267 | Buildings | Vol 1 | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment | No action
268 | Buildings | Vol 1 | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment | No action
269 | Buildings | Vol 1 | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) | No action
270 | Buildings | Vol 1 | Pink section  Not sure how much of this is required/useful | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) | No action
271 | Buildings | Vol 1 | Blue section - ✓ | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings | No action
272 | Buildings | Vol 1 | Asset type à ✓ Kitchen Vanities in contents | Included | Add to codelist | 2.7.4 Fixtures & Fittings | New Code List entry for Fittings Type proposed | Kitchen Vanities
273 | Buildings | Vol 1 | Length, Height, Width à Why? | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings | More information required for a decision
274 | Buildings | Vol 1 | Whole page à Doubt this would be known | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings | No action
275 | Buildings | Vol 1 | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) | No action
276 | Buildings | Vol 1 | à Covered in Building WOF. *Specialist area = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components | No action
277 | Buildings | Vol 1 | àSpecialists information and only applicable to multi-unit/storey complexes. | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts | No action
278 | Buildings | Vol 1 | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. | Noted: no action required | Reviewed and Noted only | 2.7.9 Security | No action
279 | Buildings | Vol 1 | à Not so useful in residential and difficult to maintain/update. | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage | No action
280 | Buildings | Vol 1 | à Not really applicable to existing housing. Maybe some use in multi-unit development. | Noted: no action required | Reviewed and Noted only | 2.8.1 Space | No action
281 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
282 | Buildings | Vol 1 | à ✕ | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | No action
283 | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
284 | Buildings | Vol 1 | Material à ✓ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
285 | Buildings | Vol 1 | Pipe type à ✕ | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data | No action
286 | Buildings | Vol 1 | Water type à ? | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data | No action
287 | Buildings | Vol 2 | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference | No action
288 | Buildings | Vol 2 | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Included | Edited to make clearer | No Specific Reference | Change made document updated
289 | Buildings | Vol 2 | This document excludes industrial buildings and Ancillary building’s  provide examples | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
290 | Buildings | Vol 2 | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
291 | Buildings | Vol 2 | Added Laundry to Outbuildings, included in the Residential standard | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
292 | Buildings | Vol 2 | The bullet points à are they attributes or measures? | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | Haydn
293 | Buildings | Vol 2 | What is Boolean data type? | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type | No action |  | closed
294 | Buildings | Vol 2 | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | Change made document updated
295 | Buildings | Vol 2 | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | no action
296 | Buildings | Vol 2 | The third and fourth suite of analytics à seems very granular? | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
297 | Buildings | Vol 2 | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | References are being considerd | No Specific Reference | No action
298 | Buildings | Vol 2 | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | Haydn
299 | Buildings | Vol 2 | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference | No action
300 | Buildings | Vol 2 | Table 4. à unclear what this actually shows? | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas | No action
301 | Buildings | Vol 2 | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | No action
302 | Buildings | Vol 2 | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Included | Updated in draft Standards | Code List 16: Condition Rating | No action
303 | Buildings | Vol 2 | Operations definition à What does this mean? Is this routine/preventative maintenance? | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
304 | Buildings | Vol 2 | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
305 | Buildings | Vol 2 | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
306 | Buildings | Vol 2 | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Sector Discussion | Mandatory / Optimal and Optional will be discussed | No Specific Reference | No action |  | maturity conversation | This is an output from the pilots, as agreed at the workshops | N/A | Close: -
307 | Buildings | Vol 2 | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) | No action
308 | Buildings | Vol 2 | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
309 | Buildings | Vol 2 | 1st bullet point à E.g. roof? Fire alarms? | Noted: no action required | Can be as granular as needed. | No Specific Reference | No action
310 | Buildings | Vol 2 | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Included | Updated in Draft Standards | No Specific Reference | Haydn
311 | Buildings | Vol 2 | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference | No action
312 | Buildings | Vol 2 | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
313 | Buildings | Vol 2 | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | No action
314 | Buildings | Vol 2 | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
315 | Buildings | Vol 2 |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
316 | Buildings | Vol 2 | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes | No action
317 | Buildings | Vol 2 | Code G, Malicious damage à Does this include tenant damage? | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
318 | Buildings | Vol 2 | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating | No action
319 | Buildings | Vol 2 |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating | No action
320 | Buildings | Vol 2 |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference | No action
321 | Buildings | Vol 2 |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
322 | Buildings | Vol 2 |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema | No action
323 | Buildings | Vol 2 | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference | No action
324 | Buildings | Vol 2 | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Noted: no action required | No action required. Understood. | No Specific Reference | No action
325 | Buildings | Vol 2 | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | Haydn
326 | Buildings | Vol 2 | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element | To discuss with technical Working Groups
327 | Buildings | Vol 2 | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Noted: no action required | The attribute is optional. | No Specific Reference | No action
328 | Buildings | Vol 2 | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference | No action
329 | Buildings | Vol 2 | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference | No action
330 | Buildings | Vol 2 | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Noted: no action required | These are at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists | No action
331 | Potable water | Vol 1 | Add USB memory sticks/hard drives to this list. | Included | Changed in all documents | 1.5 Deliverables | Change made document updated
332 | Potable water | Vol 1 | Question: Are there requirements for developers to retain information after transmission? | Noted: no action required | We see this as something for the developer to make the call if they retain a copy or not. | 1.5 Deliverables | No action
333 | Potable water | Vol 1 | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. | Excluded | keep current practice. | 2.1.5 Attribute Data Fields | No action
334 | Potable water | Vol 1 | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. | 2.1.10 Common Attributes | No action
335 | Potable water | Vol 1 | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters | 2.2.1 Area of Work Extent | More information required for a decision
336 | Potable water | Vol 1 | For circular assets, should length and width both be populated and be the same (diameter)? | Included | For circular assets, length is not required and will be made conditional | 2.3.1 Containment Structure | Change made document updated
337 | Potable water | Vol 1 | Rename to Length Metres for consistency | Included | Changed all instances to length metres and length millimetres as appropriate | 2.3.1 Containment Structure | Change made document updated
338 | Potable water | Vol 1 | Overflow = OS? What does OS stand for? Should this be OF? | Noted: no action required | This term was agreed to by the TWG, retained | 2.3.1 Containment Structure | No action
339 | Potable water | Vol 1 | Earlier wells were requested to be polygon type. Is the point supplementary? | Included | Typo corrected, is to be polygon. | 2.3.4 Well | Change made document updated
340 | Potable water | Vol 1 | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station | More information required for a decision
341 | Potable water | Vol 1 | I believe this table and its attribute names have become mis-aligned. | Sector Discussion | Looks OK, need more information | 2.5.1 Equipment | More information required for a decision
342 | Wastewater | Vol 1 | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe | No action
343 | Wastewater | Vol 1 | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. | Noted: no action required | The standards are recording as-constructed | 1.8 Theme Structure | No action
344 | Wastewater | Vol 1 | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? | Noted: no action required | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure | No action
345 | Wastewater | Vol 1 | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
346 | Wastewater | Vol 1 | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets | No action
347 | Wastewater | Vol 1 | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent | More information required for a decision
348 | Wastewater | Vol 1 | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent | No action
349 | Wastewater | Vol 1 | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | Change made document updated
350 | Wastewater | Vol 1 | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
351 | Wastewater | Vol 1 | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
352 | Wastewater | Vol 1 | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber | No action
353 | Wastewater | Vol 1 | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. | 2.3.3 Fitting | No action
354 | Wastewater | Vol 1 | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting | No action
355 | Wastewater | Vol 1 | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting | More information required for a decision
356 | Wastewater | Vol 1 | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. | Sector Discussion | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe | More information required for a decision
357 | Wastewater | Vol 1 | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe | More information required for a decision
358 | Wastewater | Vol 1 | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. | Included | Precision is defined in the standards | 2.3.4 Pipe | No action
359 | Wastewater | Vol 1 | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision
360 | Wastewater | Vol 1 | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe | No action
361 | Wastewater | Vol 1 | These changes should be coded into the pipe geometry, not as separate notes about the pipe. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision
362 | Wastewater | Vol 1 | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | Change made document updated
363 | Wastewater | Vol 1 | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe | More information required for a decision
364 | Wastewater | Vol 1 | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe | No action
365 | Wastewater | Vol 1 | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. | Noted: no action required | Reviewed and Noted only | General | No action
366 | Wastewater | Vol 1 | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | No action
367 | Wastewater | Vol 1 | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe | More information required for a decision
368 | Wastewater | Vol 1 | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? | Included | The intent of the schema is to record what has been contructed at practical completion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | No action
369 | Wastewater | Vol 1 | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe | More information required for a decision
370 | Wastewater | Vol 1 | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General | More information required for a decision
371 | Stormwater | Vol 1 & Vol 2 | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General | More information required for a decision
372 | 3-Waters & Buildings | Vol 1 & Vol 2 | What are the timeframes for this being adopted as mandatory? | Noted: no action required | Business Case. | General | No action
373 | 3-Waters & Buildings | Vol 1 & Vol 2 | Will there be a further round of submissions / comments? | Noted: no action required | Yes. Seminars in November. | N/A | No action
374 | 3-Waters & Buildings | Vol 1 & Vol 2 | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Included | Mandatory, Optimal, Optional will be discussed with the sectors and addressed during the pilot implementation phase | General | More information required for a decision
375 | 3-Waters & Buildings | Vol 1 & Vol 2 | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General | No action
376 | 3-Waters & Buildings | Vol 1 & Vol 2 | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference | Sector discussion
377 | 3-Waters & Buildings | Vol 1 & Vol 2 | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Noted: no action required | Treatment is not included | No Specific Reference | No action
378 | 3-Waters & Buildings | Vol 1 & Vol 2 | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | Included | Asset Classifications have been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
379 | 3-Waters & Buildings | Vol 1 & Vol 2 | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | Noted: no action required | Included in Instruments | Instruments | No action
380 | 3-Waters & Buildings | Vol 1 & Vol 2 | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | Noted: no action required | Separate sections of data cohorts | General | No action
381 | 3-Waters & Buildings | Vol 1 & Vol 2 | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | Sector Discussion | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments | More information required for a decision |  | volume 1 | Refer to Volume 1 tab |  | Close: -
382 | 3-Waters & Buildings | Vol 1 & Vol 2 | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | Included | Statement noted. To be actioned. | General | Change made document updated
383 | 3-Waters & Buildings | Vol 1 & Vol 2 | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well | No action |  | volume 1 | Refer to Volume 1 tab |  | Close: -
384 | 3-Waters & Buildings | Vol 1 & Vol 2 | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | Included | Suggestion adopted Standards will be updated | 1.5 Deliverables | Change made document updated
385 | 3-Waters & Buildings | Vol 1 & Vol 2 | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Sector Discussion | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | More information required for a decision |  | further conversation needed around how important each data element is (ie core data, mandatory etc) might not be possible to answer this until we get learnings from the Pilots | This is a output from the pilots, as agreed at the workshops | N/A | Close: - to be resolved/understood more during implementation
386 | Wastewater | Vol 1 | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. | Noted: no action required | Reviewed and Noted only | General | No action
387 | Wastewater | Vol 1 | a standardised approach to the collation of data relating to As Built (As Constructed) asset information | Noted: no action required | Reviewed and Noted only | Abstract | No action
388 | Wastewater | Vol 1 | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. | Included | Will consdider for final edit - happy to add in. | Executive Summary | Haydn
389 | Potable water | Vol 1 | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. | Sector Discussion | Need recommended maximum attachment size | 1.5 Deliverables | More information required for a decision
390 | Potable water | Vol 1 | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. | 2.1.1 Accuracy Requirements for Locating Assets | No action
391 | Potable water | Vol 1 | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. | Included | picked up previously | 2.1.2 Projections and Datums | Change made document updated
392 | Potable water | Vol 1 | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. | Noted: no action required | agreed, but per pipe section, there is a from-node and a to-node, one of each. | 2.4.4 Node | No action
393 | Potable water | Vol 1 | We split pipes when there is a valve or hydrant on them. While other councils may not | Noted: no action required | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. | 2.4.5 Pipe | No action
394 | Potable water | Vol 1 | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. | Sector Discussion | need examples | 2.4.5 Pipe | More information required for a decision
395 | Potable water | Vol 1 | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | No action
396 | Potable water | Vol 1 | A lot of the attributes seem to be duplicated | Noted: no action required | attributes are all different | 2.5.2 Pump | No action
397 | Potable water | Vol 1 | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. | Included | agreed, diagram will be corrected | 2.7.1 Instruments | No action
398 | 3-Waters | Vol 1 & Vol 2 | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | Included | Updated | General | Change made document updated
399 | 3-Waters | Vol 1 & Vol 2 | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | Included | Updated | General | Change made document updated
400 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General | No action
401 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Noted: no action required | This is a metadata standard not asset management standards. | General | No action
402 | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Included | Updated | General | Change made document updated
403 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | Noted: no action required | These are differentr in some cases / in others they are not, not the same definitions across sectors | General | No action
404 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | Noted: no action required | Updated and acknowledge that this will be upto the individual organisation to address | 1.5 Deliverables | No action
405 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | No action
406 | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | Noted: no action required | References to be removed. | No Specific Reference | No action
407 | 3-Waters | Vol 1 & Vol 2 | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Noted: no action required | Treatment facilities are not included as part of these standards | No Specific Reference | No action
408 | 3-Waters | Vol 1 & Vol 2 | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Noted: no action required | Out of scope. However resourse consents maybe recorded against the specifc works for each project. | No Specific Reference | No action
409 | 3-Waters | Vol 1 & Vol 2 | Content: • Land – no parameters are set for the recoding of land information. | Excluded | Out of scope. | No Specific Reference | No action
410 | 3-Waters | Vol 1 & Vol 2 | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | No action
411 | 3-Waters | Vol 1 & Vol 2 | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | No action
412 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Noted: no action required | Detailed in business case only | No Specific Reference | No action
413 | 3-Waters | Vol 1 & Vol 2 | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Noted: no action required | Applies to all assets. Mandatory and optional fields to be determined during implementation. The benefits to costs covered in business case. | General | No action
414 | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Noted: no action required | Covered in business case. | General | No action
415 | 3-Waters | Vol 1 & Vol 2 | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Noted: no action required | Covered in business case. | General | No action
416 | 3-Waters | Vol 1 & Vol 2 | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General | No action
417 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | Noted: no action required | Noted Will be further addressed during the pilot implementation phase | General | No action
418 | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | Noted: no action required | This is not within the scope of these standards | General | No action
419 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | Noted: no action required | This is not within the scope of these standards | General | No action
420 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | No action
421 | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
422 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Noted: no action required | Included in the draft Standards | General | No action
424 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums | No action
425 | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Included | Included in the draft Standards | 2.1.2 Projections and Datums | Change made document updated
426 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Included | Included in the draft Standards Asset categories included as guidance for each organisation | General | No action
427 | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure | No action
428 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | Included | Included in the draft Standards | General | No action
429 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Included | Included in the draft standards | General | No action
430 | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General | No action
431 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference | No action
432 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Included | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General | No action
433 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes | No action
434 | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) |  | More information required for a decision |  |  | These are other data sets (layers) applied to any analytic and out of scope - per earlier discussions | N/A
435 | 3-Waters | Vol 1 & Vol 2 | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings | No action
436 | 3-Waters | Vol 1 & Vol 2 | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General | No action
437 | 3-Waters | Vol 1 & Vol 2 | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes | No action
438 | 3-Waters | Vol 1 & Vol 2 | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | Sector Discussion | More information is required to inform a way forward | General for Nodes | More information required for a decision
439 | 3-Waters | Vol 1 & Vol 2 | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure | No action
440 | 3-Waters | Vol 1 & Vol 2 | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General | No action
441 | 3-Waters | Vol 1 & Vol 2 | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General | No action
442 | 3-Waters | Vol 1 & Vol 2 | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure | No action
443 | 3-Waters | Vol 1 & Vol 2 | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles | No action
444 | 3-Waters | Vol 1 & Vol 2 | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW | No action
445 | 3-Waters | Vol 1 & Vol 2 | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | Noted: no action required | Data collection is out of scope from these standards | General | No action
446 | 3-Waters | Vol 1 & Vol 2 | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference
447 | 3-Waters | Vol 1 & Vol 2 | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node | No action
448 | 3-Waters | Vol 1 & Vol 2 | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Excluded | Junctions / end points are not assets. | General | No action
449 | 3-Waters | Vol 1 & Vol 2 | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Noted: no action required | Junctions / end points are not assets. | No Specific Reference | No action |  |  | This is covered in the standards ODRC, ORC, RC | Code List 47: Financial Performance Metrics
450 | 3-Waters | Vol 1 & Vol 2 | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
451 | 3-Waters | Vol 1 & Vol 2 | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | Noted: no action required | The ID proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes | No action
452 | 3-Waters | Vol 1 & Vol 2 | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | Included | Included in the draft standards Code lists have been supplied | General | Change made document updated
453 | 3-Waters | Vol 1 & Vol 2 | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Noted: no action required | Action on volume 1 and business case. The definition of a node has been reviewed and clarified | General | No action
454 | 3-Waters | Vol 1 & Vol 2 | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Noted: no action required | Statement noted. | General | No action
455 | 3-Waters | Vol 1 & Vol 2 | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Noted: no action required | Statement noted. Data transfer is not in scope. | No Specific Reference | No action
456 | 3-Waters | Vol 1 & Vol 2 | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference | No action
457 | 3-Waters | Vol 1 & Vol 2 | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | Noted: no action required | 1. Completed 2. Further information required from respondent. Codelists are now included 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General | No action
458 | 3-Waters & Buildings | Vol 1 & Vol 2 | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | Noted: no action required | Statement noted. Consideration for Volume 1. | General | No action
459 | 3-Waters & Buildings | Vol 1 & Vol 2 | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | Noted: no action required | Statement noted. No action required. | General | No action
460 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | Noted: no action required | Statement noted. No action required. | General | No action
461 | 3-Waters & Buildings | Vol 1 & Vol 2 | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | Noted: no action required | Statement noted. No action required. | General | No action
462 | 3-Waters & Buildings | Vol 1 & Vol 2 | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | Noted: no action required | Business case. | General | No action
463 | 3-Waters | Vol 1 & Vol 2 | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | Noted: no action required | Statement noted. | General | No action
464 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
465 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Included | These inconsistencies have been actioned in the draft standards | General | No action
466 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | These inconsistencies have been actioned in the draft standards | General | No action
467 | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | Sector Discussion | To discuss | No Specific Reference | More information required for a decision
468 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | Noted: no action required | Action for volume 1. Codelists have been included defining the types of assets covered in each asset class. These codelists are dynamic in nature and over time will be added to as new materials, products etc enter the market | 1.7 Heirarchy | No action
469 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Sector Discussion | Tables to be discussed in Final Version Vol 1 | No Specific Reference | More information required for a decision Tunnels have been included
470 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy | No action
471 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
472 | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
473 | 3-Waters | Vol 1 & Vol 2 | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Included | Tables will be referenced in Final Versions | General | No action
474 | 3-Waters | Vol 1 & Vol 2 | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | No action
475 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Noted: no action required | Statement Noted. Business case. | No Specific Reference | No action
476 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Noted: no action required | Statement noted. | No Specific Reference | No action
477 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Noted: no action required | Business case. | No Specific Reference | No action
478 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference | No action
479 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Noted: no action required | Implenmentation is not within scope | No Specific Reference | No action
480 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Noted: no action required | Business Case | No Specific Reference | No action
481 | 3-Waters | Vol 1 & Vol 2 | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Noted: no action required | Business Case. | No Specific Reference | No action
482 | 3-Waters | Vol 1 & Vol 2 | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
483 | 3-Waters | Vol 1 & Vol 2 | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
484 | 3-Waters | Vol 1 & Vol 2 | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | Included | Included in the draft Standards | General | No action
485 | 3-Waters | Vol 1 & Vol 2 | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | No action
486 | 3-Waters | Vol 1 & Vol 2 | The current drafts need additional work at the hierarchy level and better definition / guidance. | Sector Discussion | Asset Classifications have been defined in the Standards | General | More information required for a decision
487 | 3-Waters | Vol 1 & Vol 2 | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Included | This is about context for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | Further discussion with Sector
488 | 3-Waters | Vol 1 & Vol 2 | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | Included | Included in the draft Standards | General | change made document updated
489 | Potable water | Vol 1 | savvy - edit out slang words like this | Included | removed in current version | Executive Summary | Change made document updated
490 | Potable water | Vol 1 | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? | Included | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. | In Summary | Change made document updated
491 | Potable water | Vol 1 | Consultants - Replace by organisations? | Included | Term consultants now included in glossary. | 1.1 Register | Change made document updated
492 | Potable water | Vol 1 | Again, misuse of term 'consultants. edit through the document to correct this. | Included | Term consultants now included in glossary. | 1.4 Disclaimer | Change made document updated
493 | Potable water | Vol 1 | Is this still used? | Noted: no action required | optional supply | 1.5 Deliverables | No action
494 | Potable water | Vol 1 | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? | Noted: no action required | both schemata and schemas are both acceptible words for the plural of schema. | 1.6 Global Schemas | No action
495 | Potable water | Vol 1 | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? | Noted: no action required | This is not within the remit of the standards | No Specific Reference | No action
496 | Potable water | Vol 1 | how can the analytics standardise the data that has already been standardised? | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | No action
497 | Potable water | Vol 1 | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference | No action
498 | Potable water | Vol 1 | i.e. not fixed and topics can be added? | Included | Agree, asset classes can be added as agreed to | 1.8 Theme Structure | No action
499 | Potable water | Vol 1 | what does this mean? No? but no Y for yes? | Included | N changed to N/A | 1.9 Data Principles | Change made document updated
500 | Potable water | Vol 1 | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.1.1 Accuracy Requirements for Locating Assets | No action
501 | Potable water | Vol 1 | precisely? 'well' is a subjective term | Included | changed | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
502 | Potable water | Vol 1 | no 's' | Sector Discussion | cannot identify | 2.1.1 Accuracy Requirements for Locating Assets | More information required for a decision
503 | Potable water | Vol 1 | change 'issues' to 'risks' throughout document | Noted: no action required | not a risk but an issue | 2.1.10 Common Attributes | No action
504 | Potable water | Vol 1 | Well - change to 'bore' | Noted: no action required | term agreed to by TWG | 2.3.4 Well | No action
505 | Potable water | Vol 1 | does this create a 'node'/ if not then it is a problem for modelling. | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | More information required for a decision
506 | Potable water | Vol 1 | how is a locator or IP cable taped to the pipe represented? | Sector Discussion | Need more information and example | 2.4.5 Pipe | More information required for a decision
507 | Potable water | Vol 1 | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | No action
508 | Potable water | Vol 1 | Is a backflow preventer a mechanical equipment asset or a valve/ | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment | More information required for a decision
509 | Potable water | Vol 1 | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure | No action
510 | Potable water | Vol 1 | this could be much larger with additional definitions e.g.. 'trunk main' | Noted: no action required | Codelists are dynamic and wil expand over time | Glossary | No action
511 | 3-Waters | Vol 1 & Vol 2 | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
512 | 3-Waters | Vol 1 & Vol 2 | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
513 | 3-Waters | Vol 1 & Vol 2 | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
514 | 3-Waters | Vol 1 & Vol 2 | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | Noted: no action required | Volume 2 is now complete | No Specific Reference | No action
515 | 3-Waters | Vol 1 & Vol 2 | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General | No action
516 | 3-Waters | Vol 1 & Vol 2 | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Sector Discussion | Included in the draft Standards Asset Classes included that are relevant to each network. These can be added to over time. The pilot implementation phase will be used as a guide | 1.7 Heirarchy | More information required for a decision
517 | 3-Waters | Vol 1 & Vol 2 | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | No action
518 | 3-Waters | Vol 1 & Vol 2 | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Included | Tables will be referenced in Final Versions However it is upto each organisation to determine the most approapriate way to create these links based on their systems | General | No action
519 | 3-Waters | Vol 1 & Vol 2 | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
520 | 3-Waters | Vol 1 & Vol 2 | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
521 | 3-Waters | Vol 1 | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General | No action
522 | 3-Waters | Vol 1 | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. | Noted: no action required | Service level performance is included in Volume 2 | General | No action
523 | 3-Waters | Vol 1 | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes | More information required for a decision
524 | 3-Waters | Vol 1 | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
525 | 3-Waters | Vol 1 | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. | Noted: no action required | Please refer to Project and common data | General | No action
526 | 3-Waters | Vol 1 | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset owners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
527 | 3-Waters | Vol 1 | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes | No action
528 | 3-Waters | Vol 1 | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
529 | 3-Waters | Vol 1 | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. | Sector Discussion | More information is required to inform a way forward | General for Pump Station | More information required for a decision
530 | Stormwater | Vol 1 | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. | Noted: no action required | This will be catered for through recording the "Source" | General | No action
531 | Stormwater | Vol 1 | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. | Included | This is a derivation for Volume 3, including precision of survey data | General | No action
532 | Stormwater | Vol 1 | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. | Included | Now normalised and standardsed with Metaconnect | General | No action
533 | Stormwater | Vol 1 | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General | No action
534 | Stormwater | Vol 1 | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General | More information required for a decision
535 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure | No action
536 | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). | Included | Already incorporated into the table | 2.3.1 Containment Structure | No action
537 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure | No action
538 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure | No action
539 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure | No action
540 | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure | More information required for a decision
541 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall | More information required for a decision
542 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | No action
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment | More information required for a decision
544 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber | No action
545 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | Change made document updated
546 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber | More information required for a decision
547 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | No action
548 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision
549 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber | More information required for a decision
550 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision
551 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. | Sector Discussion | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | More information required for a decision
552 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). | Noted: no action required | Please refer to comment above | 2.4.2 Channels | No action
553 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. | Sector Discussion | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | More information required for a decision
554 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | No action
555 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe | No action
556 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | Haydn
557 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | Change made document updated
558 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe | More information required for a decision
559 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | No action
560 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | No action
561 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? | Included | yes in Volume 2 | 2.4.4 Pipe | No action
562 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | Change made document updated
563 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe | More information required for a decision
564 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). | Noted: no action required | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station | No action
565 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station | No action
566 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. | Included | Attribute fields are included in the Pump asset class for motors. Please review and provide details of additional | 2.5.2 Pump | No action
567 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | No action
568 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. | Sector Discussion | Will include for ratification by the reviewers. | 2.5.2 Pump | New attribute proposed | Trigger level
569 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve | More information required for a decision
570 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | No action
571 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve | No action
572 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment | No action
573 | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | Change made document updated
574 | Potable water | Vol 1 | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date | Noted: no action required | Reviewed and Noted only | General | No action
575 | Potable water | Vol 1 | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General | New Code List proposed | Health & Safety Type
576 | Potable water | Vol 1 | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General | More information required for a decision
577 | Potable water | Vol 1 | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) | Noted: no action required | 10 character fields have been adopted to allow for expansion | General | No action
578 | Potable water | Vol 1 | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General | More information required for a decision
579 | Potable water | Vol 1 | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. | Sector Discussion | Need more information and example | General | More information required for a decision
580 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). | Sector Discussion | Need more information and example | 2.3.1 Containment Structure | More information required for a decision
581 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
582 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | No action
583 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | New Code List proposed | Burial Status Above ground Below ground Partially buried
584 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure | No action
585 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure | No action
586 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
587 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
588 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
589 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision
590 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision
591 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | No action
592 | Potable water | Vol 1 | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment | No action
593 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL a. Include Ground Water Level | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well | No action
594 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL b. Resource Consent number | Included | Included in Project Attributes | 2.3.4 Well | No action
595 | Potable water | Vol 1 | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading | Sector Discussion | Code lists for NZDWS could be included - for discussion | 2.3.4 Well | More information required for a decision
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | More information required for a decision
597 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed | Manufacturer
598 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | No action
599 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. | Included | Agreed | 2.4.3 Fitting | Change made document updated
600 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting | More information required for a decision
601 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe | New Asset Class proposed Detail of data requirements needed | Support Structures
602 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. | 2.4.5 Pipe | No action
603 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | No action
604 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. | Included | Already catered for | 2.4.5 Pipe | No action
605 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe | No action
606 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe | No action
607 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | No action
608 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. | Included | change in all documents | 2.4.5 Pipe | Change made document updated
609 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter | Included | removed nom_Bore | 2.4.5 Pipe | Removal of attribute proposed Have marked for removal in documents
610 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe | More information required for a decision
611 | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe | More information required for a decision
612 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision
613 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision
614 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision
615 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber | More information required for a decision
616 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | More information required for a decision
617 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | New attribute proposed | Portable generator (Y/N)
618 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | New attribute proposed | Calculation
619 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve | More information required for a decision
620 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve | New Code List proposed | Valve Control & Automatic Control
621 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. | Sector Discussion | see 00620 | 2.5.3 Valve | New Code List proposed | Valve Power
622 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
623 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve | More information required for a decision
624 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | No action
625 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection
626 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
627 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Incoming Pressure
628 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Outgoing Pressure
629 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Headloss
630 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE l. Valve mechanism code list should be similar to: BFL Butterfly DIA Diaphragm SLC Sluice GAT Gate BAL Ball KNF Knifegate DAV Double air FLP Flap gate NED Needle SAV Single air SND Solenoid WSC Check PRV Pressure reducing RLV Pressure relief | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Mechanism Butterfly Diaphragm Sluice Gate Ball Knifegate Double air Flap gate Needle Single air Solenoid Check Pressure reducing Pressure relief
631 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow
632 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Include attribute fields describing how the pump is powered - electrical, diesel, petrol. | Sector Discussion | Does this relate to the motor or the pump? To be compared to the attributes of the motor | 2.5.2 Pump | More information required for a decision
633 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump | New attribute proposed | Pump oreintation
634 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP c. “Actual pump rate” will at times be meaningless because of Variable Speed Drive (VSD) pumps, that can run at different speeds. This field is therefore either irrelevant for VSD, although it may be an eventual ‘input’ of actual data from control systems. | Noted: no action required | Reviewed and Noted only | 2.5.2 Pump | No action
635 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty end date, Purchase date to be reviewed. | 2.5.1 Equipment | More information required for a decision
636 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. Include Capitalized cost as well as purchase cost | Included | ODRC / ORC / RC are included | 2.5.1 Equipment | No action
637 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT c. The abbreviated and full attribute names contained in this table are not related to each other (this is possible a typographical error). | Noted: no action required | Resolved in updated version | 2.5.1 Equipment | No action
638 | Potable water | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. An attribute field with an ability to include a SCADA reference should be included. | Noted: no action required | Refer to Telemetry | 2.5.1 Equipment | No action
639 | Potable water | Vol 1 | Asset Class: Electrical Asset - CABLING a. Ductwork poses a tricky question because it is separate from cabling. Ductwork can be a part of the structure, and can carry many cables. If it is going to be recorded, Ductwork needs to be an asset class in its own right. | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision
640 | Potable water | Vol 1 | Asset Class: Instrumentation - INSTRUMENTS a. SCADA and RTU (controllers) are not instruments, because they do not measure variables. Include them under electrical equipment. | Included | Reviewed and Noted for Inclusion | 2.7.1 Instruments | Change made document updated
641 | Wastewater | Vol 1 | All Asset Classes a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Will ensure that they are applied. | General | Change made document updated
642 | Wastewater | Vol 1 | All Asset Classes b. Missing asset classes: There are a number of missing asset classes in the Wastewater Standard – including “Containment Structures” and “Tunnels”. Wellington Water has 23 containment structures for Wastewater, which is material in terms of asset renewal. | Sector Discussion | Additional Assets and attributes will be added to final version | General | More information required for a decision
643 | Wastewater | Vol 1 | All Asset Classes c. It was uncertain how the ‘crossover’ between the Wastewater and Stormwater network is managed within the Standard (including weirs). | Noted: no action required | Otherwise please be specific about the uncertainty. | General | No action
644 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. A definition may be required in relation to “relative level”. Relationship of ladders to access chamber; H&S attributes may be required, as ladders need to be certified. Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. This should be considered for inclusion in Volume 2. | Included | Include H&S Attributes | 2.3.1 Access Chamber | Haydn
645 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. Vegetation should not form part of this asset class data attribute for the Wastewater network! | Sector Discussion | to be discussed with the TWG | 2.3.2 Channel | More information required for a decision
646 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b. Is this really an ‘asset class’ for Wastewater (open sewers?) | Noted: no action required | If they do not exist then this asset class will not be used | 2.3.2 Channel | No action
647 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. Generally felt to be a ‘solid’ set of data attributes related to pipes. | Noted: no action required | Reviewed and Noted only | 2.3.4 Pipe | No action
648 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. Is there scope for a new field called “expected remaining life” based on observations? | Included | Remaining life is 'expected', observed or otherwise (e.g. calculated) - related to intervention type | 2.3.4 Pipe | Haydn
649 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. How are ‘pipe supports’ treated within the Standard? | Sector Discussion | Please provide examples of the types of supports that are used | 2.3.4 Pipe | More information required for a decision
650 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. The “Material Description “ field contents need to be set at the correct level – a significant impact on design life results between different materials such as uPVC, mPVC and oPVC, MDPE, HDPE and HPPE | Included | Material is a mandatory attribute | 2.3.4 Pipe | No action
651 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Soil Type should also be captured as part of this Standard (impacts design life) and used to inform a wider geospatial dataset. We need to remember that a pipe may cross several soil types. | Sector Discussion | Was previously discussed and rejected by the TWG | 2.3.4 Pipe | Change made document updated
652 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Surface Material should be recorded as part of this Standard – impacts structural composition. We need to remember that this field must be an updatable attribute based on non-3W observations. Pipes will also cross several different surface material | Included | Add Surface Material | 2.3.4 Pipe | New attribute & associated Code List proposed | Surface Material Surface Material Type
653 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Included | This is a geospatial layer and can attribute accordingly | 2.3.4 Pipe | No action
654 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. In general, the focus group thought this was a well thought out set of attributes associated with Pump Stations. | Noted: no action required | Reviewed and Noted only | 2.3.5 Pump Station | No action
655 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Attributes related to power supply are important; elements of the “electrical” asset class are related to the pump station (see comments in section 2.9 related to the parent-child relationship inherent in pump stations). Attributes include (at least) an ICP number. | Included | Already included. | 2.3.5 Pump Station | No action
656 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION c. The Standard is silent on elements related to “Access” and/or “Easements” for this asset class. | Noted: no action required | Correct. Volume 1 focusses on recording asset data at practical completion | 2.3.5 Pump Station | No action
657 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station | More information required for a decision
658 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION e. The cost attribute is associated with a particular construction date – ie, the pump station is assumed to be ‘static’. This is not likely. (again – may relate to parent-child relationship of pump station to assets it contains). | Included | ODRC / ORC / RC are included | 2.3.5 Pump Station | No action
659 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION f. Safe working limits are a legal requirement  does this form part of the building standard? | Included | Depth is recorded | 2.3.5 Pump Station | No action
660 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION g. “Building Owner” could be split between multiple owners | Included | Owner vs manager fields available in the draft standard Catenate multiple owners in field Buildings are separate assets, see buildings | 2.3.5 Pump Station | More information required for a decision
661 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Elements of a pump may be regarded as a distinct asset – such as motors, impellors, control system, cabling. The attributes of a pump relate to the pump type – this field may need further expansion and/or definition. | Excluded | Detailed drawing and component information is provided in manuals on handover - a reference attribute is included | 2.4.2 Pump | No action
662 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. The line between a pump asset and maintenance is not discussed within the Standard – even though this could change the asset function. | Sector Discussion | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | 2.4.2 Pump | Change made document updated
663 | Wastewater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. The data attributes within this section seem to relate entirely to Electrical Equipment; this does not make sense for this asset class. For example, the “Serial #” field has a description related to “protective material”. | Included | To be resolved in all 3W tables. | 2.4.1 Equipment | More information required for a decision
664 | Wastewater | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. “Risk” should be a key field – with a strong relationship to a relevant Volume 2 table. Safety in Design elements (and residual risk) should form part of this also. | Noted: no action required | Links are not within the remit of these standards - this is an analytical element | 2.4.1 Equipment | No action
665 | 3-Waters | Vol 2 | Data Relationships: Linkages shown in charts between Schema are inconsistent. For example, the “Repairs & Maintenance” schema is shown as interfacing to “As-constructed” and “Condition” schemas. But other Schemas have “Repairs & Maintenance” as an interface. For example, “Financial Performance” and “Demand” both have “Repairs & Maintenance” as an interface. If interlinkages are not shown to be consistent then the validity of the Standard can be questioned. This aligns with the overall statement made in section 1.9 of this document. | Sector Discussion | Relationships are explained in depth in Vol 2 | No Specific Reference | No action
666 | 3-Waters | Vol 2 | 2. Project Area: The project area artefact could apply to any business project over the 3 waters and not simply a new subdivision reticulation e.g. new facility or augmentation of WW or WS plant, refurbishment of upgrading of network etc. Understanding how projects/investments are delivered and perform is an important AM capability. The metadata schema should not constrain how assets are managed to meet desired outcomes. | Noted: no action required | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | No Specific Reference | No action
667 | 3-Waters | Vol 2 | 3. Delivery Risk: In order to generate valid information and outcomes the recording of data in a schema for national reporting will require consistency both within an organisation and between organisations over time. This should be recognised as a risk to the successful delivery of benefits by the Data Standard. | Noted: no action required | Delivery risk is a risk for Volume 3 - Methodology | 1.4.2 Intervention Methodologies (Volume 3) | No action
668 | 3-Waters | Vol 2 | 4. Units of measure in asset management would include flow, pressure, time - these are not in the Code list 1, but these and other units are referenced throughout the schemas. Note that different flow and pressure measurement units will apply to different assets or uses. | Included | Amended Code list | Table 2: Water Supply Service Attributes | No action
669 | 3-Waters | Vol 2 | 5. Date Range & Traceability: Similar to the comments made in section 2.1 related to Volume 1, key fields in Volume 2 should be auditable, giving the ability to track when changes are made, why and by whom. While a function of an information system, the requirement for such should be included in a metadata standard. | Sector Discussion | More information is required tofully iundertstand this feedback, but systems business rules (e.g. date ranges) are the place for defining extents, not these standards Assessors are included Data Table 1: Condition Attributes Assessor_N Assessor Name text | No Specific Reference | More information required for a decision |  |  | This is a systems requirement - not an element for the NZAMS as per our discussions in the workshops | N/A
670 | 3-Waters | Vol 2 | 6. Code lists provided for Volume 2 generally require more work to develop consistent, full and meaningful references for use. We note that code lists have not been provided for Volume 1. | Included | Code lists have been updated for comment. | List of Code Lists | No action
671 | 3-Waters | Vol 2 | 7. Depreciation Data: Depreciation is an indicator of loss of service potential. Replacement value must reflect the true value of replacement in the current environment – which may be different to the environment at original installation. Changes to value and the rate of deterioration may be due to specific changes to asset attributes and environment over time. There must be fields to link changes to time and place. | Noted: no action required | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Code List 47: Financial Performance Metrics | No action
672 | 3-Waters | Vol 2 | 8. Lack of observation schema: As noted in section 4.4(a), the lack of an “Observations” schema hampers the ability for observation to inform multiple data schemas – such as condition or updates of asset attributes in the as-built schema. | Noted: no action required | Statement noted. Observations will feed into the attributes. | Data Table 1: Condition Attributes | No action
673 | 3-Waters | Vol 2 | 9. H&S Data: Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. | Included | Now included in Risk attributes Con_Rat_HS Consequence Rating Health and Safety | Table 7: Risk Attributes | More information required for a decision
674 | 3-Waters | Vol 2 | Condition a. Condition data is relevant for a range of decisions and processes in the asset lifecycle, most particularly around renewals, risk and valuations. The following comments consider these aspects but also apply to many of the other processes in some degree. | Included | Statement noted. | 2.2 Condition Schema
675 | 3-Waters | Vol 2 | Condition b. The inclusion of a calculated remaining useful life within the condition schema is fundamentally flawed because it does not account for other relevant asset life determining factors. Examples of such include criticality, demand, performance, optimisation and the asset’s operating environment. By linking condition grade directly to remaining useful life, the schema pre-supposes an end of life or replacement date decision. These conclusions should only be made while considering the wider factors as above. Noting this, Code List 6 linking condition grade to remaining useful life should be removed. | Sector Discussion | Let's discuss - these standards are not about decision-making - they are elements for decisionmaking - these standards define each of these elements. We are not suggesting you should make a decision on condition alone. But if your note is about definition of remaining useful life then let’s chat. | 2.2 Condition Schema | More information required for a decision |  |  | Condition is only one decision element. The standards expect critical assets have an influence on the timing of replacement. Interoperability analytics allows you to consider criticality alongside condition (in the example). Unfortunately, currently there is no quantitative analysis between these elements. If the pipe up to the hospital is condition 4 (still has a reasonable expected life, maintenance is within normal levels), then you still might chose to replace it because it's the pipe up to the hospital and do not want to take the risk. | N/A
676 | 3-Waters | Vol 2 | Condition c. It is recommended that the schema be modified to take into account the level of confidence in condition grades. There is little or no recognition of the probabilistic nature of condition assessments and hence the confidence limits which apply to the grades. Any condition grade is made within a band of confidence at a point in time. The confidence level is relative to whether it is being applied to a subject asset or extrapolated to an asset group, and whether it is applied at the time of assessment or projected forward. | Noted: no action required | This is a calculable field, for example, stochasticity | No Specific Reference | No action
677 | 3-Waters | Vol 2 | Condition d. The basis of the interfaces with other schema (Table 5) is unclear and the linkages shown do not acknowledge the relationships between condition data and all other schema. Eg: i. Criticality determines priorities for condition data collection ii. Repairs and maintenance activities are a key potential source of condition data iii. Condition is indicative of likelihood of failure and hence helps determine risk iv. Service and financial performance are impacted by condition v. Demand and utilisation inform the criticality of an asset and hence priority for condition data collection. | Noted: no action required | These are analytical outputs of specific problems being solved. We can discuss | No Specific Reference | No action
678 | 3-Waters | Vol 2 | Condition e. Items included in the condition data attributes (Table 2) appear to be a mix of data at different levels of detail; some being at the assessment level and others at the observation level. Any hierarchy or relationship between these is not implied or explained however. The potential one-to-many linkages from asset to assessments and further to observations are not apparent. Any data required must be clarified in terms of how it relates to other data to enable practical processes for capture and storage. | Sector Discussion | Action: To be discussed with Wellington Water. | Data Table 1: Condition Attributes | More information required for a decision |  |  | Condition can be determined a number of ways, the standards reflect this fact. | N/A
679 | 3-Waters | Vol 2 | Condition f. The description of condition grades against physical deterioration (Code List 2) is a good approach however the terminology is inconsistent. Most descriptors but not all relate to asset failure. All should be described on the same basis to allow for consistent interpretation. “Asset failure” in this sense also requires definition and is unclear in the schema. | Included | Uniform terminology now applies | Code List 16: Condition Rating | No action
680 | 3-Waters | Vol 2 | Condition g. The condition grade types (Code List 3) are unclear and do not give any sense of the distinctions or relationships between structural, service, mean, peak and overall grades. | Included | Condition code lists (e.g. structural, exterior, interior) are now included in Vol 2 | Code List 16: Condition Rating | No action
681 | 3-Waters | Vol 2 | Condition h. The condition grade assessment methodologies (Code List 4) and assessment types (Code List 5) are extremely limited and do not capture many methodologies that are currently available and in use. Terminology is not consistent with the purpose of the list, ie; “Cut out” is a sampling methodology rather than an assessment type as listed. A cut out may be assessed visually, by destructive and/or non-destructive testing, or other means. Code lists 7 – 10 are similarly limited and the purpose and usage of which are unclear. | Sector Discussion | See code list | Code List 17: Condition Rating – Methodology | More information required for a decision |  |  | This is an issue for volume 3 | N/A
682 | 3-Waters | Vol 2 | Repairs and Maintenance a. The Proactive and Reactive Activity Type descriptions need additional clarification to minimise ambiguity. How should “impairment” be interpreted - breakdown, significant performance issue or just incipient failure only detectible with monitoring equipment (e.g. bearing vibration, thermographic image, etc)? Also “Scheduled” needs to exclude non-routine or one-off activities that are set to occur in the future. | Noted: no action required | See code list | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
683 | 3-Waters | Vol 2 | Repairs and Maintenance b. The schema does not support optimisation of maintenance tasks through RCM analyses or other FMECA based approaches. An example would be the need for a clear and unambiguous definition of asset function. This is not well covered in Part 1 attributes. Comment should be requested from an RCM practitioner. | Noted: no action required | Statement noted. This is not a maintenance management system. | No Specific Reference | No action
684 | 3-Waters | Vol 2 | Repairs and Maintenance c. Recording the “Image_ID” against activities does not cater for referencing other types of digital files. Suggest this optional attribute is made generic and capable of accepting hyperlinks to reference files in other systems. | Noted: no action required | This is an analytical requirement | No Specific Reference | No action
685 | 3-Waters | Vol 2 | Repairs and Maintenance d. Fail_Mode and Cause_Iss is important but must be specific to each asset type rather than generic across all assets. It’s not clear if this is the intention. | Noted: no action required | This is an analytical requirement and is matched to other elements (e.g. AssetID) to determine response | No Specific Reference | No action
686 | 3-Waters | Vol 2 | Repairs and Maintenance e. A key decision for every asset is to either run to failure or apply a scheduled maintenance/inspection plan. | Noted: no action required | This is an analytical requirement (i.e. both) | No Specific Reference | No action
687 | 3-Waters | Vol 2 | Repairs and Maintenance f. In Part 1 Condition Assessment Type is an asset attribute, but Condition is part of a different schema. Shouldn’t these go together to reflect the fact that the condition assessment approach may change over time? | Included | Yes, but in the analytical phase. | No Specific Reference | No action
688 | 3-Waters | Vol 2 | Repairs and Maintenance g. It isn’t clear how maintenance strategies are to be handled (i.e. managing maintenance work that has weekly/monthly/annual/ etc activities). AMIS functional requirements should be considered before fields like Recur and Recur_Cyc are established. | Noted: no action required | Standard is not intended to populate a maintenance plan. Code Lists are included to handle this requirement e.g. Recurrence Cycle | Code List 5: Recurrence Cycle Unit | No action
689 | 3-Waters | Vol 2 | Repairs and Maintenance h. Need quantity as well as cost information to be able to analyse trends and predict future costs. Need to record all resources – not restricted. | Noted: no action required | Code lists for quanitifying repairs included | Code List 6: Bases of Cost | New Code List from Working Group
690 | 3-Waters | Vol 2 | Repairs and Maintenance i. The combination of Activity Type, start date/time, end date/time does not appear to meet the requirements for DIA non-financial reporting for urgent/non-urgent callouts (i.e. need to separately record time to reach site and time to resolve issue). | Noted: no action required | Type of maintenance activity is included | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
691 | 3-Waters | Vol 2 | Repairs and Maintenance j. There needs to be a new Event Type similar to “Upgrade/Improvement”. Irrespective of the funding source (capital vs operational) assets need to have a full history of events recorded against them. If we exclude upgrades and rely solely on project registers to capture this information we make lifecycle management significantly more difficult. | Noted: no action required | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Code List 49: Description of Financial Performance Element | No action
692 | 3-Waters | Vol 2 | Repairs and Maintenance k. Why record overflows etc. in repairs and maintenance schema and not in the level of service? Overflows are recorded per financial year, different organisations have different financial years, is history recorded i.e. over time. Should other compliance activities i.e. RON and CDEM should also be coded. | Included | One is a record of the type event One is a record a service level e.g. overflows per year and an analytic | Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | No action
693 | 3-Waters | Vol 2 | Repairs and Maintenance l. Asset versus component issue can give rise to different design criteria and system performance i.e. a pump has a l/s design while a filer has (say) minimum pressure drop, but it is performing of the pumping station that is the issue. | Noted: no action required | Statement noted | No Specific Reference | No action
694 | 3-Waters | Vol 2 | Repairs and Maintenance m. Does not appear to allow for other investigation methods e.g. vibration analysis, DCVG results, thermal imaging, usage data analytics for identifying if an intervention is required. | Included | Code lists to be discussed against current code lists e.g. Condition (This is really a Volume 3 question) | Code List 17: Condition Rating – Methodology | No action
695 | 3-Waters | Vol 2 | Repairs and Maintenance n. As found and as left condition or status is useful for items like valves, could also apply to depth of cover, locks etc. | Included | Statement Noted: No action required. | No Specific Reference | No action
696 | 3-Waters | Vol 2 | Repairs and Maintenance o. Asset performance does not clearly link to key result areas or key performance indications set by organisations in the management of assets or demanded by consumers. | Sector Discussion | This is an anlytical question - discuss with sector | No Specific Reference | More information required for a decision
697 | 3-Waters | Vol 2 | Repairs and Maintenance p. Asset or service performance - it is not clear what is referred to or if this is consistent. | Sector Discussion | Section updated in Volume 2 | 5.4 Service Performance Schema | More information required for a decision
698 | 3-Waters | Vol 2 | Repairs and Maintenance q. How are components and soft parts etc linked to assets, is the lifecycle of O&M supported by this? | Noted: no action required | Component type is an attribute in the repair schema and captured under each asset. | 2.3.4 Components of Repairs, Maintenance and Operations | No action
699 | 3-Waters | Vol 2 | Repairs and Maintenance r. Benchmarking - same as identified in service levels schema, consistency is required for valid and useful outputs to be obtained. | Noted: no action required | Statement noted and agreed. | No Specific Reference | No action
700 | 3-Waters | Vol 2 | Repairs and Maintenance s. Outage duration - mandatory for all actions but what if no outage? Also what if the customers are reinstated over time ie 95% connected in 1 hour while the rest are out for days? Outage is linked to ' number of people' - this can be impossible to measure depending on each connection (as in an apartment block), would customer or property be a better measure. | Noted: no action required | Agreed. Then outage duration = 0. | No Specific Reference | No action
701 | 3-Waters | Vol 2 | Repairs and Maintenance t. Third party damage excluded from outage definition but included in repair schema as cause. | Included | Third Party attribute included | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
702 | 3-Waters | Vol 2 | Repairs and Maintenance u. Maintenance planning - focused on time based maintenance (elapsed), but could encompass operating hours or CBRM. A MMS would do a better job, would it be better not to specify these matters in the schema and just have an objective for an outcome based system in place. This could be applied throughout the data standard noting the issues with consistently in benchmarking. | Sector Discussion | Analytical elements included in standards to schieve this analytic | No Specific Reference | More information required for a decision
703 | 3-Waters | Vol 2 | Repairs and Maintenance v. It would be desirable to have costs for maintenance collected on an area/project basis for performance analysis. | Included | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | No Specific Reference | No action
704 | 3-Waters | Vol 2 | Repairs and Maintenance w. Should complaints be linked to an issue or root cause rather than an address or asset - this would enable better linking and development of appropriate solutions and priority setting than a collection of disparate reports. Also need to know the outcome of the assessment of a compliant ie internal plumbing, no issue found etc before an organisation make decisions on number of complaints. Option of an outcome based CRM system rather than data standard? | Included | Linking CRM information to asset information is not in scope These root cause examples in the code list are asset related interrogations for asset management purposes. | No Specific Reference | No action
705 | 3-Waters | Vol 2 | Utilisation a. Asset utilisation needs to consider the level of redundancy in the network or asset system required to achieve the desired overall level of risk. The proposed calculation of utilisation could work for an individual pump, but would be of little/no value for a trunk main network. It could easily be misinterpreted. | Included | Redundancy is include in the codelists in Vol 2 as an analytical attribute (see vulnerability). | Code List 43: Global Resilience Rating Elements | No action
706 | 3-Waters | Vol 2 | Utilisation b. Until the intervention methodologies are proposed for each of the 3 waters we find it difficult to understand what fields may or may not be wanted for this schema. | Noted: no action required | Statement noted. | 3.2.5 Code Lists
707 | 3-Waters | Vol 2 | Demand a. Demand applies to collections of assets. Why would you want to record demand against an individual asset such as a pipe or valve? | Included | This is an analytics requirement, but may no be required agaist all asset components. | No Specific Reference
708 | 3-Waters | Vol 2 | Demand b. The fields offered are very limiting in this schema and the use of demand needs to be thought through in more depth. | Noted: no action required | Demand Section has been updated in Volume 2 | 3.3 Demand Schema
709 | 3-Waters | Vol 2 | Demand c. Peak demand at a system level is not the sum of zone demands due to the diversity/averaging effect as the study area increases in size. Average demand at a system level is the sum of the zone demands. The schema does not seem to recognise this. | Noted: no action required | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler | Data Table 4: Demand Attributes | No action
710 | 3-Waters | Vol 2 | Demand d. What analytics would this schema (as is) be used to support? | Noted: no action required | Future connections on flow (population demand) | Code List 33: Demand – Measure | No action
711 | 3-Waters | Vol 2 | Demand e. Should this schema exist in an AMIS? | Noted: no action required | Yes | 3.3 Demand Schema | No action
712 | 3-Waters | Vol 2 | Criticality a. Criticality is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | No change | 4.3 Criticality Schema | No action
713 | 3-Waters | Vol 2 | Criticality b. The current approach to criticality from Wellington Water uses criticality as an equivalent to consequence in the evaluation of risk. To this effect the criteria for criticality that we have developed uses cumulative weighted impacts in combination with importance (exposure) factors to derive risk. My view is that the criticality descriptors offered in the standards are only one component of the consequence variable in the risk equation ie the exposure factor. To this extent it is puzzling to identify how criticality as described could be used in the evaluation of risk – given the subsequent content of the risk schema. | Noted: no action required | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | 4.3 Criticality Schema | No action
714 | 3-Waters | Vol 2 | Criticality c. For example if the renewal of a pipe was being considered wrt risk of failure – condition is an indicator of probability, the potential impacts could be social, environmental or financial loss and the exposure is measured by the number of people or the importance of the facility affected by the loss of service. | Noted: no action required | These are analytical inferences which are attributed in code in algorithms by attributes these standards define | No Specific Reference | No action
715 | 3-Waters | Vol 2 | Criticality d. Until worked examples are provided as to how the consultants perceive criticality being used for different decisions we struggle to see how the schema as offered would be useful or at best would have limited value. | Noted: no action required | Explanation found in criticality schema | 4.3 Criticality Schema | No action
716 | 3-Waters | Vol 2 | Criticality e. The code list 27,28,29 tables have some potential flaws in our view. i. Special facilities is too vague as a term for Code 5. Few utilities would have munition storage or critical data centres and in most cases data centres would have back up. How is this derived for example if it was potential damage from blowing up a munitions store, how would compare to an LPG centre or holding tanks containing solvents ii. For a water utility is a hospital really less critical than a data centre? iii. What happens when an asset services 3 or 4 hospitals iv. Where is economic loss factored into these tables – they seem to be very “government” centric v. We struggle to think that decision making using criticality for small towns of less than 5000 people would only ever have code 3 assets as their most important asset. Risk is about context and the context must consider the community and the economic scale of their investment. We do not believe one size fits all. | Noted: no action required | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. | No Specific Reference | No action
717 | 3-Waters | Vol 2 | Risk a. Risk is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | Statement noted. | No Specific Reference | No action
718 | 3-Waters | Vol 2 | Risk b. We assume that the risk schema is intended to facilitate risk management within water utilities. | Noted: no action required | Yes, and for buildings per the Biulding Standard | 4.4 Risk Schema | No action
719 | 3-Waters | Vol 2 | Risk c. We have reviewed this schema with respect to the principles of risk management as outlined in Section 3 of the guideline document for AS/NZS 31000:2009 | Noted: no action required | Noted | 4.4 Risk Schema | No action
720 | 3-Waters | Vol 2 | Risk d. In particular the schema as drafted inhibits the following principles: | Noted: no action required | Noted | 4.4 Risk Schema | No action
721 | 3-Waters | Vol 2 | Risk e. 3(g) Risk management is aligned with the organisations external and internal context and risk profile | Sector Discussion | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
722 | 3-Waters | Vol 2 | Risk f. 3(h) Risk management recognises the capabilities, perceptions, and intentions of external and internal people that can facilitate or hinder the achievement of the organisations objectives | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
723 | 3-Waters | Vol 2 | Risk g. 3(j) Risk management continually senses and responds to change. As external and internal events occur, context and knowledge change, monitoring and review of risks takes place, new risks emerge, some change, others disappear | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
724 | 3-Waters | Vol 2 | Risk h. To propose a specific risk matrix into a national standard seems to conflict with these basic principles | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct And any organisation can taylor the analysis to the local context | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
725 | 3-Waters | Vol 2 | Risk i. Although interdependencies between other schemas are stated it is difficult to extract how they would be used together. Risk, criticality and condition must be interconnected but there is no indication as to how the application of these schemas would allow this | Noted: no action required | This would depend on the problem being solved and the analytical approach in doing so | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
726 | 3-Waters | Vol 2 | Risk j. The suggestion that probability scales for different events and water types are the same is unhelpful in the absence of worked examples. Are there examples to demonstrate a sensible cross relationship for the use of probability scales in water supply and stormwater? | Noted: no action required | Unclear of what this means, but the scales are adaptive to event type, but specifiuc to asset type | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests'
727 | 3-Waters | Vol 2 | Risk k. Other than flood risk, how do you assess time based probabilities? The use of the word “time to time” or “in your career” will lead to subjective assessments that will simply promote inconsistent investment decisions rather than secure them. | Noted: no action required | Code list updated | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
728 | 3-Waters | Vol 2 | Risk l. We believe the contents of the fields that describe 1- 5 consequences should be omitted. A decision to occupy these fields for a national risk schema to derive nationally consistent approaches to risk will do exactly the opposite – it promotes subjective assessment and also directly contravenes the principles of risk management as described in AS/NZS 31000. | Noted: no action required | To discuss, see code lists | Code List 41: Consequence Rating | More information required for a decision
729 | 3-Waters | Vol 2 | Resilience NO schema offered However, we urge you to consider a fundamental question when addressing resilience for water utilities. Is the assessment of an assets’ resilience important or is it more important to assess the resilience of the service provided to customers on a national scale? We would suggest the latter, and therefore question the merits of offering a schema for asset resilience. If it is the latter, we also suggest that resilience is better attributed to customers rather than assets. | Included | Schema updated | 4.5 Resilience Schema | No action
730 | 3-Waters | Vol 2 | Design Performance This schema is not required. We don’t need evaluative criteria here. Attributes should be in the as built schema and actual performance should be in service performance. Table 12 in all volume 2 documents (sections 9.3) refer to the linkages with the resilience schema not the design performance | Noted: no action required | Let's discuss this is important. Design performance is different than Service Performance | 5.2 Design Performance Schema | More information required for a decision
731 | 3-Waters | Vol 2 | Financial Performance a. General comment – It would be interesting to know what is determined to be core data requirements with regards to the attributes. There is a large set of attributes to collect a large number would only be relevant to a small number of organisations. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | 5.3 Financial Performance Schema | No action
732 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
733 | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
734 | 3-Waters | Vol 2 | Financial Performance c. Valuation date doesn’t seem to appear anywhere. | Noted: no action required | Included in standards | Data Table 10c: Valuation Attributes Details (Collected Level Indicated) | No action
735 | 3-Waters | Vol 2 | Financial Performance d. Linking the financial information e.g. revised asset lives with condition data. | Noted: no action required | Attributes included in standards, this is an analytical exercise | No Specific Reference | No action
736 | 3-Waters | Vol 2 | Financial Performance e. Terminology is not consistent with the Repairs and Maintenance schema e.g. reactive/planned/etc. | Noted: no action required | Now consistently applied | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
737 | 3-Waters | Vol 2 | Service Performance Level of service is recorded against individual assets, this may cause issues where service level is required from a network, facility, project, contract or organisational levels. These levels of service may not directly relate to asset parameters or the level of service at an asset may relate to another asset upstream (e.g. minimum pressure at a downstream point relates to the upstream network and pumps/regulators etc). Also levels of service are not static and these may change (this change may be the result of internal or external drivers). | Noted: no action required | These are analytical constructs from an individual assetID dataset. How consolidated into geographic units os for the specific analysis, e.g. network, zone, catchement etc. | No Specific Reference | No action
738 | 3-Waters | Vol 2 | Service Performance a. Benchmarking relies on the consistency of inputs. In order to generate valid information and outcomes the recording of data in a scheme for national reporting will require consistency in an organisation, between organisations and over time. Other national standards have shown there are issues with this approach, will the benefits of a metadata standard be realised (what are the risks and assumptions to the achievement of this benefit)? | Noted: no action required | This is a reference to standardised analytical approaches | No Specific Reference | No action
739 | 3-Waters | Vol 2 | Service Performance b. Residential demand figure, valid for industrial or commercial areas, how updated and how is history against assets recorded? | Noted: no action required | This is a reference to an analytical approach. E.g. ParcelID District Plan Zone type and connection demand (or Level of Service). | No Specific Reference | No action
740 | 3-Waters | Vol 2 | Service Performance c. Is it feasible that the same assessor (individual) is used for all items in each asset i.e. cultural significance and technical design and financial measures? | Noted: no action required | The same or multiple | No Specific Reference | No action
741 | 3-Waters | Vol 2 | Service Performance d. Consents compliance is linked to an asset when consents are typically given on an activity/facility - correct linkages and business processes will need to be established and implemented to ensure that compliance is achieved in light of asset changes. | Noted: no action required | Consent attributes are captured at property level which is not inconsistent with reporting at network/zone level - i.e. it is a spatial query between the two data sets. The attributes are specified for capturing asset detail in the standards | No Specific Reference | No action
742 | 3-Waters | Vol 2 | Service Performance e. Third party damage is excluded from service measures (interruptions) for water supply. This is a valid facet of AM, and the scheme has this included in repair and maintenance for WW assets. | Noted: no action required | Included in the Standards | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
743 | 3-Waters | Vol 2 | Service Performance f. MoH grading should be linked to a time the grade was awarded, and possibly should be greater than just a single field i.e. who assessed etc. We question the merit of this as a valid asset performance measure as it is always system based. | Noted: no action required | Included in the Standards | Data Table 11: Service Performance Attributes – Functional | No action
744 | 3-Waters | Vol 2 | Service Performance g. The fact a health and safety assessment has been carried out is interesting, but it is the results that are important (have the risks been addressed or are there outstanding issues etc) and there is no mention of this. | Noted: no action required | Included in the Standards | Table 2: Water Supply Service Attributes & Code List 41: Consequence Rating | No action
745 | 3-Waters | Vol 2 | Maintenance Planning i. Will the scheme provide an effective (and efficient) link to maintenance management systems that are in use currently? | Included | Yes that is the intention for the future. | No Specific Reference | No action
746 | 3-Waters | Vol 2 | Maintenance Planning ii. Are all costs collected at an asset level, won't different treatments give rise to different outcomes, ie, where are staff or contractor costs added to a facility, item or asset. Is maintenance carried out on assets as they exist or on notional assets? | Included | Application of costs will be at the discretion of the rganisation, but likely to be applied to a cohort of assets when being maintained | No Specific Reference | No action
747 | 3-Waters | Vol 2 | Operational Performance i. Actual performance should also be recorded as well as consent compliance - is water quality improving over time or always just inside the limit? | Included | Action: add in to schema (design performance? Service performance) | Data Table 9: Design Performance Attributes | No action
748 | 3-Waters | Vol 2 | Operational Performance ii. There is reference to LAWA framework – is this commonly used throughout the country? Would it be better to refer to the National Policy Statement or specific Regional rules as applicable for the authority? | Noted: no action required | All regional councils use LAWA | No Specific Reference | No action
749 | 3-Waters | Vol 2 | Valuation and depreciation Asset life versus economic/accounting life, does asset structure match the chart of accounts used by all organisations and applied in all business models i.e. contracted services? | Noted: no action required | Yes - there are appropriate fields for ODRC, ORC, RC and Forecast, Actual and Budget financial information in Finance Performance sections | Code List 47: Financial Performance Metrics | No action
750 | 3-Waters | Vol 2 | Planning for growth or decline i. Assets will need lifecycle stages not just in service ie proposed (linked to project), out of service, in store, abandoned, leased for F/O etc (assets can provide other services, not just those implicit in the standard) | Included | Discuss with Sector - to consider schema | No Specific Reference | Create a code list of service types as suggested here?
751 | 3-Waters | Vol 2 | Planning for growth or decline ii. Levels of service can change over time on different assets, this will need to be understood/recorded | Noted: no action required | Atributes to do this are included in the standards | No Specific Reference | No action
752 | Wastewater | Vol 1 | In talking about As Managed, I assume this is for how the councils handle data rather than how the data supplied by survey from the field, as these are two different worlds? | Sector Discussion | This is a discussion in the development of Volume 3 | No Specific Reference | No action
753 | Wastewater | Vol 1 | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this | Included | Reviewed and Noted for Inclusion Included as part of the Project Attributes table Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | More information required for a decision
754 | Wastewater | Vol 1 | There is increased risk to data accuracy in companies that are not working all the time with software projection transformations. As the client, I would always want to receive the data in it original projection and transfer it myself | Included | The requirement is for each company to deliver the data in the final projection and datum | 1.5 Deliverables | No action
755 | Wastewater | Vol 1 | Why is this BIM Enabled? Should this not be BIM Enabled/Geospatial Representation as these still hold and display 3d information. | Noted: no action required | Update, asset management and facility management systems do…. | 1.9 Data Principles | No action
756 | Wastewater | Vol 1 | This surely should be "current parcel" boundaries. Not sure as to what a title/property boundary is, as what is the definition of property (residence, address, rating unit, parcel(s))? Also, is this relevant?You want the assets to be shown in true survey location even if this shows them being constructed illegally through private property. | Sector Discussion | For analytical purposes Have added 'geographical units' code list | 2.1 Technical Reference Information | More information required for a decision
757 | Wastewater | Vol 1 | I believe this is how data should be stored, but supply of data should be as captured. By forcing this to the supplier you are increasing the risk of error, with groups that will only project data occasionally more likely to make mistakes | Noted: no action required | The intent of this is to educate the indutsry in what capability it will need | 2.1.2 Projections and Datums | No action
758 | Wastewater | Vol 1 | Why would you develop a new specification and then allow for it to be supplied in a historic format such as shapefile. This also means that the defined "text" geometry type cannot be supplied and instead would need to be changed to a point | Noted: no action required | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF | 2.1.7 Metadata Definitions | No action
759 | Wastewater | Vol 1 | Is this cost of the asset or cost of the asset plus installation? Is this standard cost of the recommended price of the asset, rather than any discounts were achieved? | Noted: no action required | All replacement costs include installation | 2.1.10 Common Attributes | No action
760 | Wastewater | Vol 1 | Is the central location the centre of access (i.e. manhole lid)or the centre of the structure? | Included | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. | 2.3.1 Access Chamber | Change made document updated
761 | Wastewater | Vol 1 | Pipe length shown here is neither the length of the digital pipe feature or the length of the real world feature, as you are not taking into account the "faux" pipe connectors angle. The middle pipe length here is very confusing! | Sector Discussion | Need more information for a way forward | 2.3.1 Access Chamber | More information required for a decision
762 | Wastewater | Vol 1 | Does this mean covered by dirt and not readily accessible or below ground level? | Noted: no action required | Below ground level | 2.3.3 Fitting | No action
763 | Wastewater | Vol 1 | What happens when two separate pipes are installed between access points (e.g. different material etc). Also there are examples were pipes may not have access chambers (as defined by this document). While that may be not best practice, it does occur. | Noted: no action required | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists | 2.3.4 Pipe | No action
764 | Wastewater | Vol 1 | Is this the digital length or the real world length? | Included | This is the real world length as described in the QA validation field. | 2.3.4 Pipe | No action
765 | Wastewater | Vol 1 | What does this mean? What level of accuracy is defined as a discrepancy? | Included | Changes made to wording to reflect tolerances used in practice ('field') | 2.7.2 Matching to Existing Infrastructure | Change made document updated
766 | Potable water | Vol 1 | Asset Group: To be consistent with Section 1.8 Should this heading be changed to "Asset Category" ? (Or in section 1.8 change "Asset Category" to "Asset Group" | Included | Changed to Asset Group for consistency. | 1.7 Heirarchy | Change made document updated
767 | Potable water | Vol 1 | Asset Type: To be consistent with Section 1.8, should this be changed to "Asset Class" | Included | Changed to Asset Class. | 1.7 Heirarchy | Change made document updated
768 | Potable water | Vol 1 | The paragraph refers to "Asset Types", yet table 1.8 does not reference "Asset Types", only "Asset Class". If these are not interchange in relation to meaning, then I suggest a explanation of "Asset Type" and "Asset Class" be documented within the document somewhere. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
769 | Potable water | Vol 1 | My personal preference is to utilize "Asset Class" as standard terminology, and replace any instances of "Asset Type" within the document if they are inferring the same meaning. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
770 | Potable water | Vol 1 | My personal preference is to utilize "Asset Category" as standard terminology, and replace any instances of "Asset Group" within document. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
771 | Potable water | Vol 1 | Conflicts with section 2.3.4 states that a well is to be represented as a polygon | Included | Changed to Polygon | 1.8 Theme Structure | Change made document updated
772 | Potable water | Vol 1 | Listed here as a guide, but each definition of the asset class states the required spatial representation. ie 2.3.1 states polygon feature. Therefore for clarity, should this table also list the requirement of the standard for each asset class? | Sector Discussion | More information is needed for a way forward | 1.9 Data Principles | More information required for a decision
773 | Potable water | Vol 1 | I am assuming this only for Geo-spatial attributes? (As there may be different sources utilized across multiple attributes.) If this is correct, can this be added for clarity in the contents column. | Included | Defined by organisation | 2.1.10 Common Attributes | No action
774 | Potable water | Vol 1 | If the data source changes, is there a need to keep a date history of the changes. | Noted: no action required | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. | 2.1.10 Common Attributes | No action
775 | Potable water | Vol 1 | Common Attributes for your consideration: (We currently have the following 3 attributes fields across all our assets) - Manufacturer (of asset) - Supplier (of asset) - Installed By (Contractor who installed asset) Fields to be utilized to identify failing assets due to manufacturer/supplier and potential faulty installation by a contractor. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
776 | Potable water | Vol 1 | This field should be allowed to be empty. What if there is no photographic references available. Flows through to Asset Class definitions | Sector Discussion | consider N/A as an appropriate response. | 2.1.10 Common Attributes | More information required for a decision
777 | Potable water | Vol 1 | Define "Asset Classes" and "Asset Types" | Included | Asset Classifications have been defined in the Standards | 2.2 Asset Categories | No action
778 | Potable water | Vol 1 | RL: Add a definition of RL in the "Glossary of Terms and Definitions" in the document (Reduced Level) "RL" acronym used in multiple places in the document. | Included | Included in Glossary | 2.3.2 Embankment, Glossary | Change made document updated
779 | Potable water | Vol 1 | No Type field for Wells. ie Type_Well Is this an oversight or genuinely not needed? | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision
780 | Potable water | Vol 1 | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision
781 | Potable water | Vol 1 | Seem to be missing Chamber Diameter, for circular access chambers. (As it states that AC_Length and AC_width only to be used if chamber is non circular) | Sector Discussion | Needs some rework and clarifiation. | 2.4.1 Access Chamber | More information required for a decision
782 | Potable water | Vol 1 | Potential Attribute: Manufacturer of Fitting | Included | Already identified and will be refered to TWG. | 2.4.3 Fitting | New attribute proposed | Manufacturer
783 | Potable water | Vol 1 | Water flow direction is not absolute. I am assuming this is for a network operating under "normal" conditions. | Included | Correct. For a network operating under 'normal' conditions. | 2.4.5 Pipe | No action
784 | Potable water | Vol 1 | For clarity, perhaps include a diagram showing an irregular access chamber. Refer to page 20 in Vol 1 of the waster water meta-data standard (V1.2 DRAFT A - 14 July 2016) | Sector Discussion | Completed | 2.4.6 Pump Station | Change made document updated
785 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrectly matched. EG Serial_No => Protective Material This is carried through to the Waste Water and Storm Water manuals. | Included | Resolved in current version. | 2.5.1 Equipment | Change made document updated
786 | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrect matched. | Included | Resolved in current version | 2.5.1 Equipment | Change made document updated
787 | Potable water | Vol 1 | In our AMIS we are planning to utilize two fields to describe valves. Valve Type: Eg Isolation, Scour, Toby, Pressure Reducing, etc .. Valve Mechanism: Eg Gate, Knife, Ball, Air Release, etc.. Rather than combine function and mechanism into one attribute field. | Sector Discussion | to be discussed with the TWG refer to 630, 631 | 2.5.3 Valve | More information required for a decision
788 | Potable water | Vol 1 | Where are readings recorded? Should there not be an attribute for the latest meter reading and date it was recorded. | Noted: no action required | As Constructed' data not operational data. | 2.7.1 Instruments | No action
789 | Potable water | Vol 1 | Incorrect reference: Should be 1.8 | Included | Resolved in current version. | 2.8.2 Matching to Existing Infrastructure | Change made document updated
790 | Potable water | Vol 2 | Terminology Constancy: In Vol 1, Section 1.8, a lot of the elements below are referred to as "Asset Classes" They are also referred to "Asset Classes" in the attribute and validation file format. Suggest change "Categories" to "Classes" | Noted: no action required | Standards updated to a consistent approach | Table 3: Asset Hierarchy Framework | No action
791 | Potable water | Vol 2 | I am unsure what this means. Can there be more explanation of the content in the Rules column. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
792 | Potable water | Vol 2 | What is Rule 2? Ensure on what this means. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
793 | Potable water | Vol 2 | How are these levels recorded in the date table 7? (ie Network, facility) Table 7 only links back to an individual asset level (Unique_ID) There does seem to be merit to applying Risk to a network level, sub-network level or at a facility level? Could also apply this thinking to Criticality definition? | Sector Discussion | Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance or criticality | No Specific Reference | More information required for a decision
794 | Potable water | Vol 1 | All three standards use this sentence correct for all 3 waters | Sector Discussion | Please provide further information. | Executive Summary | More information required for a decision
795 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.7 Heirarchy | Change made document updated
796 | Potable water | Vol 1 | Believe there should be a level between asset group and asset type (see my hierarchy tree). Also Asset Class & Asset Category is not specified in the hierarchy. | Sector Discussion | Please provide further information relating to your hierachy. | 1.7 Heirarchy | More information required for a decision
797 | Potable water | Vol 1 | Defined as Asset Type on previous page | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
798 | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
799 | Potable water | Vol 1 | What information is required to determine if a tank/reservoir is a civil structure or not. i.e. How to determine if a tank/reservoir is a containment structure or a retaining structure. | Noted: no action required | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | 1.8 Theme Structure | No action
800 | Potable water | Vol 1 | Will there be reference documents for treatment plant assets? | Noted: no action required | Not at this point in time | 1.8.1 Other Asset Classes in the precinct of a Water Network | No action
801 | Potable water | Vol 1 | How would an asset that could be represented as more than one of these be represented. e.g. would a scour be a single asset (pipe) or two (pipe and fitting) or would that be up to the Client to determine | Sector Discussion | More information is required to inform a way forward | 1.9 Data Principles | More information required for a decision
802 | Potable water | Vol 1 | water | Included | changed to Water. | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
803 | Potable water | Vol 1 | water code lists | Included | Section under review. | 2.1.5 Attribute Data Fields | Change made document updated
804 | Potable water | Vol 1 | Definition etc missing | Included | Section under review. | 2.1.6 Attribute Data Type Definitions | Change made document updated
805 | Potable water | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils/contractors to use an ESRI based product, or something else? if not suggest removing ESRI from this sentence. | Noted: no action required | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for | 2.1.7 Metadata Definitions | No action
806 | Potable water | Vol 1 | Section 2.1.4 | Included | Section under review. | 2.1.7 Metadata Definitions | Change made document updated
807 | Potable water | Vol 1 | Does this code list include options for multiple networks? or is each network to be recorded as an individual project? | Included | ProjectID already included Yes it does - added multiples in Project Table | 2.1.9 Project Attributes | Change made document updated
808 | Potable water | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
809 | Potable water | Vol 1 | See note regarding Design Company above. | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
810 | Potable water | Vol 1 | Should this not be a code list? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
811 | Potable water | Vol 1 | What is the definition of cost for contractors? What is the value of capturing this when there are no controls around application of defining cost? | Included | Reviewed and Noted for Inclusion Financial code lists for ODRC, ORC and OC are included | 2.1.10 Common Attributes | haydn
812 | Potable water | Vol 1 | What exactly are the photographic references? This appears to be a 250 Char field so completely useless for using this data. Is this intended to be used in a similar way to 'Unique ID' as a reference number for the photo? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
813 | Potable water | Vol 1 | Again using a 250 character field means the data could be all over the place. Example uses this field to record specific instructions to access the asset. To me that should be a separately labelled field. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision
814 | Potable water | Vol 1 | See note regarding this field on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
815 | Potable water | Vol 1 | See not for Design Company on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
816 | Potable water | Vol 1 | Would a T not be a fitting instead of a node? | Noted: no action required | T is a fitting but also an intersection so therefore a node. | 2.4.4 Node | No action
817 | Potable water | Vol 1 | Is there a particular reason that Valves etc do not 'break' pipes? When works are undertaken (renewals in particular) actual physical assets provide useful 'real world' demarcation points. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | 2.4.5 Pipe | No action
818 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram
819 | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram
820 | Potable water | Vol 1 | What are the reasons for Internal Diameter, Nominal Diameter and Nominal Bore all being required? Are these all not essentially the same thing? | Sector Discussion | The range of diameter types are an analytical requirement for interogating assets through a range of lenses | 2.4.5 Pipe | More information required for a decision
821 | Potable water | Vol 1 | Would this class also cover assets that provide access but are not part of a dam or weir wall? Suggest that this be added to the wastewater specification as well. | Included | Agreed 9/3/2017 | 2.3.6 Tunnel | Comment clarifed in potable water document and tunnel asset class added to wastewater document
822 | Potable water | Vol 1 | Should purchase date be included? Do some warranties apply from date of purchase? | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision
823 | Potable water | Vol 2 | a' instead of 'the' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
824 | Potable water | Vol 2 | Why is infrastructure for collection and treatment not covered? These assets are integral to potable water supply and asset managers need quality information that they can use to make asset management decisions. Sentence also contradicts itself. "does not cover infrastructure...treatment of water, except in the case of..infrastructure to treat water". | Noted: no action required | There is a desire to create anoter standard which includes these assets, as there is in th ebuilding environment for Large Commercial Buildings and Industrial Buildings | No Specific Reference | No action
825 | Potable water | Vol 2 | Pressure is more of a Quality provision. Suggest moving this into Quality. | Noted: no action required | Pressure is a Design Attribute How it performs against that design is a Design Performance attribute | No Specific Reference | No action
826 | Potable water | Vol 2 | Delete extra "that" | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
827 | Potable water | Vol 2 | outlines' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
828 | Potable water | Vol 2 | investment' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
829 | Potable water | Vol 2 | replace' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
830 | Potable water | Vol 2 | Influences | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
831 | Potable water | Vol 2 | Replication | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
832 | Potable water | Vol 2 | General comment - risk and criticality are closely linked. Are they really different things? Just use one term and get rid of the other. | Noted: no action required | No action required. Decision to separate two schemas taken at project management level | No Specific Reference | No action
833 | Potable water | Vol 2 | Table is missing a 'comments' field | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
834 | Potable water | Vol 2 | Inconsistent with the wastewater and stormwater measure headings (Rating). Suggest same terminology is used across all three waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
835 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
836 | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would" more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
837 | Potable water | Vol 2 | Is this a different manual than the 3rd Edition New Zealand Pipe Inspection Manual? If not use full document name as used in the wastewater and stormwater documents. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
838 | Potable water | Vol 2 | Should this not be in line with the wastewater and stormwater measures? (IIMM 2015) | Noted: no action required | No action required. This is the same document | No Specific Reference | No action
839 | Potable water | Vol 2 | If this information is to be completed by field (maintenance and operations) staff they are unlikely to know if works have been deferred or will be deferred. | Noted: no action required | Not an attribute of these standards | No Specific Reference | No action
840 | Potable water | Vol 2 | Replace "data" with "cost" | Included | Documents have undergone a full publishing edit | Haydn | No action
841 | Potable water | Vol 2 | Stormwater document includes complete code lists for these items. Water and wastewater do not. | Noted: no action required | Code lists updated | List of Code Lists | No action
842 | Potable water | Vol 2 | Not convinced that this is a useful or practical schema, at least for potable water assets. Perhaps don't bother with this and just use demand schema instead? They are similar. | Noted: no action required | Utilisation and Demand are different decision elements as explained in the standards. | 3.2 Utilisation Schema 3.3 Demand Schema | No action
843 | Potable water | Vol 2 | Missing sentence from WW and SW Volume two further explaining the utilisation schema. " Utilisation is measured using time or other base unit measured against a known availability." | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
844 | Potable water | Vol 2 | "Current Utilisation" at an asset by asset level would require an impractical amount of monitoring. i.e. are we really going to know average and peak flows through each and every length of water pipe? | Included | This is an analytical construct, and easily monitored in an analytical sense at whatever frequency required for intervention circumstances | 3.2 Utilisation Schema | An explanation of Data Science will be provided for at the Technical Working Groups
845 | Potable water | Vol 2 | Partly a function of the pressure in the pipe. Are we really going to know potential utilisation for each and every length of water pipe? | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
846 | Potable water | Vol 2 | Don't think it's possible to determine this for each and every asset. At least for potable water assets. | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
847 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets without extensive modelling. Alternatively would require data from modelling software. | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
848 | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
849 | Potable water | Vol 2 | This does not seem to be an relevant measure for water demand in a metropolitan situation. | Included | Completed - see Demand section | 3.3 Demand Schema | No action
850 | Potable water | Vol 2 | Criticality varies across all three waters. While a data centre may have a higher water criticality than a hospital, the opposite would be true of wastewater. | Included | Correct, which is why each asst class is treated differently when an analysis of things like criticality are conducted across a network | No Specific Reference | No action
851 | Potable water | Vol 2 | Of risk & criticality, which are both similar schema, criticality is much quicker and easier to measure and much less subjective. I would be tempted to exclude risk or use it with caution in decision-making compared the use of other schema. | Noted: no action required | It will be required n some circumstances, and here it is defined when you do | No Specific Reference | No action
852 | Potable water | Vol 2 | Ln only needs to be 1 due to 1,5 rule | Included | Completed | No Specific Reference | No action
853 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
854 | Potable water | Vol 2 | Even at a score of 3 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
855 | Potable water | Vol 2 | Even at a score of 3 is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
856 | Potable water | Vol 2 | Even at a score of 4 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
857 | Potable water | Vol 2 | Not convinced there is much use in this table, at least for water assets. Most revenue is derived from consumption so would be associated with a meter and the usage of water. | Noted: no action required | No action required. Organisation can choose how revenue is recorded against an asset | No Specific Reference | No action
858 | Potable water | Vol 2 | So this is theoretical revenue? Not actual revenue? | Included | Actual, Forecast and Budget included in financial code lists | Code List 6: Bases of Cost | No action
859 | Potable water | Vol 2 | Delete this text. Captured in the field below. | Included | Completd | No Specific Reference | No action
860 | Potable water | Vol 2 | This whole section is confusing. It's trying to do two things at once. Individual asset attributes and whole of network attributes should be separated out. | Included | Network analytics are completed on individual asset analytical interogations | No Specific Reference | No action
861 | Potable water | Vol 2 | So its not intended to be used for decisions at an individual asset level? If not, strip out all the individual asset measures and move somewhere else. | Included | It is in some circumstances to be used on an individual assetID | No Specific Reference | No action
862 | Potable water | Vol 2 | This table seems to be a jumble of attributes for individual assets and DIA measures which are taken for the network / organisation as a whole. I'm not really sure the whole of network / organisation attributes are metadata. Delete DIA whole of network / organisation attributes or move to a separate table. dlane: Some data items are network wide while others are asset specific. If data capture is required these should be split into separate network and asset tables. | Included | Volume 2 is completed in these draft standards. Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance | No Specific Reference | No action
863 | Potable water | Vol 2 | How does this field work? Is it the duration of the most recent unplanned interruption, the the total duration of all unplanned interruptions (from field below) or the average unplanned interruption duration? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
864 | Potable water | Vol 2 | How does this field work? Is it the connections affected in the most recent unplanned interruption, the total connections affected in all unplanned interruptions (from field below) or the average number of connections affected in unplanned an unplanned interruption? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
865 | Potable water | Vol 2 | Delete this field. It makes no sense and is confusing. Field Ref 11.04 does the job. | Included | Table updated | No Specific Reference | Change made document updated
866 | Potable water | Vol 2 | Need to include the units of measure. kPa,psi etc | Included | Tables updated in code lists of Vol 2 | Code List 44: Description of Design Performance – Engineering Unit of Measure | psi to be added
867 | Potable water | Vol 2 | Surely this field would only be used for a reservoir asset. Not, say, a pipe supplied from the reservoir. Please clarify the use of this field. | Included | It can be both | No Specific Reference | No action
868 | Potable water | Vol 2 | Not sure it would come from Repairs and Maintenance Schema. | Noted: no action required | This MoH included in the Service Performance Attributes | Data Table 11: Service Performance Attributes – Functional | No action
869 | Potable water | Vol 2 | Confusing to have it on this table. So this field is used at a facility level not an individual asset level? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
870 | Potable water | Vol 2 | Confusing to have it in this table. So this field is used at an organisation level? The question of whether there is an adequate backflow prevention programme doesn't relate to individual assets? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
871 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
872 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
873 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
874 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
875 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
876 | Potable water | Vol 2 | This is not a demand attribute, its abstraction/take and is source based. as you've said that this is potable water assets only I don't think it's appropriate here. | Noted: no action required | A source is an asset (e.g. a reservoir), abstraction is the process, demand is the level of abstratcion on the asset - each are different and can apply to a pipe connection no less (e.g. a school) | No Specific Reference | No action
877 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
878 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
879 | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated?. | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments'
880 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. Move to financial schema? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
881 | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
882 | Potable water | Vol 2 | Differs from tables in the stormwater and wastewater specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Tables are very similar, with the asset specific elements being applied when required. Tables have been normalised where possible | No Specific Reference | No action
883 | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
884 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
885 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
886 | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
887 | Stormwater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Included | Reviewed and Noted for Inclusion | 2.1.7 Metadata Definitions | Change made document updated
888 | Stormwater | Vol 1 | 2.1.4 | Included | Reviewed and Noted for Inclusion | 2.1.6 Attribute Data Types Definitions 2.1.7 Metadata Definitions | Change made document updated
889 | Stormwater | Vol 1 | Does this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Noted: no action required | Either | 2.1.9 Project Attributes | No action
890 | Stormwater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
891 | Stormwater | Vol 1 | See note regarding Design Company above. | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
892 | Stormwater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
893 | Stormwater | Vol 2 | Heading (see water and wastewater) | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
894 | Stormwater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or at code should be a single character as per the water measures. Should be consistent across all 3 waters | Included | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
895 | Stormwater | Vol 2 | Differs from table in wastewater and water specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
896 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
897 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
898 | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.8 Theme Structure | Change made document updated
899 | Wastewater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Noted: no action required | Not the intention. The intention is to outline why the field is structured in this way | 2.1.7 Metadata Definitions | No action
900 | Wastewater | Vol 1 | 2.1.4 | Included | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | 2.1.7 Metadata Definitions | Change made document updated
901 | Wastewater | Vol 1 | Doe this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Sector Discussion | This is an operational question related to an organisations ability to import data into their asset management systems. For immature organisations likely to be project by project, for mature ones project agnostics | 2.1.9 Project Attributes | More information required for a decision
902 | Wastewater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
903 | Wastewater | Vol 1 | See note regarding Design Company above. | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
904 | Wastewater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision
905 | Wastewater | Vol 2 | Not a valid measure for wastewater utilisation. | Included | Updated | No Specific Reference | No action
906 | Wastewater | Vol 2 | Criticality varies across all three waters. for example, for wastewater a hospital would have a higher value than a data centre. while water could score differently | Noted: no action required | No action required, based on the importance of the building as defined in the Buildings standard | Code List 13: Facility Importance Rating
907 | Wastewater | Vol 2 | Heading is different from that used in water and stormwater documents. Suggest standardising for simplicity. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
908 | Wastewater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or code should be a single character as per the water measures. should be consistent across all 3 waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
909 | Wastewater | Vol 2 | Differs from tables in the stormwater and wastewater spec. Most/all of these measures should be applicable across all three waters. | Noted: no action required | consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
910 | 3-Waters & Buildings | Vol 1 & Vol 2 | An obvious mistake in the Potable Water Metadata Std is that someone has put the Residential Executive Summary in it????. | Included | Included in the draft Standards | Executive Summary | Change made document updated
911 | 3-Waters & Buildings | Vol 1 & Vol 2 | You are asking for public to comment on missing attributes within meta data tables. Considering you have spent 12500 hours on this, could you please comment if all the attributes defined by Australian standard ADAC have been included? http://engicom.com.au/adac/government-organisations I appreciate your list of assets may be more comprehensive. If any of the asset attributes defined in ADAC are missing there are like to be areas where assets will miss vital information for future analysis. If you have used IPWEA in your decision making process it would be useful to include this information on your website so it doesn’t look like you are reinventing the wheel. Well done on sorting out the asset management data through the lifecycle of each asset. Local councils desperately need national standard for asset capture, storage and access to information. | Included | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. | General | No action
912 | 3-Waters & Buildings | Vol 1 & Vol 2 | I’d like to provide feedback on the proposed standard. However I caveat this as coming from a hands on GIS Practitioner View, which may be different to my colleagues here at LINZ. I think it will be incredibly important to incorporate good practice guidance at some stage on how these standards are practically implemented. Ideally providing an empty or working dataset that a person can take, open with their system and populate. Generally when you go to create the schema in a system you’ll follow it and interpret changing the types, field lengths, column names etc. My request is based on recent experience. Often this step is left out, and implementation of the standard fails. This was my experience with the ANZLIC geospatial metadata standard, 10 years after its release 95% of GIS practitioners in New Zealand could still not easily implement the standard within the most common desktop GIS software. The Australian based tool provided did not support NZ requirements. We ended up shoving the required text into a single desc field in an inappropriate manner, ending up with a total mess. This may require getting software providers onboard with adding these into their pre-defined templates for users of the most common software providers. If you could imagine in the same way we create a LINZ letterhead letter in MS Word. My 2 cents from a GIS data capture perspective and I am happy to discuss this further if appropriate, otherwise happy to leave it as this. | Noted: no action required | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | N/A | No action
913 | 3-Waters & Buildings | Vol 1 & Vol 2 | In each of these documents out for proposal, there is reference to standard codes for things like asset type and material (“the CODELIST”), but none of these are available yet – will this be available before consultation closes? | Included | Code lists are included Attributes to be discussed | General | Gauge input from next review | [5 empty] | No action required
914 | 3-Waters & Buildings | Vol 1 & Vol 2 | This is a great initiative and will aid everybody involved in the area of Asset Management. I would ask is has there been any coordination with the Institute of Public Works Engineering Australasia as they have a system already in place called ADAC (http://www.engicom.com.au/adac). Could your framework be an extension to that so we can leverage what software companies have developed already to support that schema. It appears that a lot of the info you are capturing has already been covered, why reinvent the wheel? | Noted: no action required | IPWEA Australasia has representation around the table, and has had for 2 years | N/A | No action
915 | 3-Waters & Buildings | Vol 1 & Vol 2 | Structure of the standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes. Further to the split of water sectors there is an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group has specified that a single document that focusses on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. In terms of usability our end users are expecting a data framework that is easy to understand and use. In the proposed layout we are expecting the standards will be met with cost burdens. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
916 | 3-Waters & Buildings | Vol 1 & Vol 2 | 2. Applicability of volumes 1 and 2 The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was about creating an as-built data set for industry that can be used to collect field data, most of the workshops evolved around this input. Volume 2 for derived data has had limited industry input and we do not believe it is ready to be published. Further work on this volume is therefore required. | Noted: no action required | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. | General | No action
917 | 3-Waters & Buildings | Vol 1 & Vol 2 | 3. Data hierarchy The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. As presented at the workshops, an example of how this could be applied to the tables is outlined below: Level 0 (system/layout specific data – master data. Typically assigned by organisational systems and numbering or coding rules - contains the common data set) -Inventory identification number / -Functional location i.e. Network type (water, wastewater, stormwater) / -etc. Level 1: Data categories, in example: “Technical/physical” i.e. Containment structures (available technical core classes) (or) Operational data (or) Financial data etc. Level 2: (attributes) Minimum required attributes, in example: -Function / -Depth / -Material / -etc. Level 3: (attributes) Conditional attributes, in example: -Diameter if circular / -length and width if not circular / -Joint type (if the structure has joints) / -etc. Level 4: (attributes) Optional attributes, in example: -Manufacturer / -Model/part number / -etc. | Included | Asset Classifications have been defined in the Standards Tables are to be discussed at length | No Specific Reference | Sector discussion | [5 empty] | Closed
918 | 3-Waters & Buildings | Vol 1 & Vol 2 | 4. Terminologies and definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need to be agreed. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
919 | 3-Waters & Buildings | Vol 1 & Vol 2 | 5. Graphical representation and its accuracy This subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. Graphical representation should be removed from the document; the purpose of this standard is collecting metadata of asset physical properties. Geospatial requirements are a standard in its own right and even providing these as guidelines does not seem appropriate. | Included | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH | General | No action
920 | 3-Waters & Buildings | Vol 1 & Vol 2 | 6. General content 1.“Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. 2. The units of measure have not been covered during the workshops. Further input may be required before the draft is ready for public release. 3. Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and the implementation may not be practical. 4. Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. In many instances data will be collected in-house. 5. Australian examples and photos should be replaced by New Zealand examples. Word choice such as “savvy” (used often) is not the best choice. Some of the language used needs to be reviewed in order to retain the standard’s professionalism. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included | General | No action
921 | 3-Waters & Buildings | Vol 1 & Vol 2 | 7. Implementation The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate has not been considered where organisations may choose not to collect certain information for low risk assets. An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard | Noted: no action required | This is not within the scope of these standards | N/A | No action
922 | 3-Waters & Buildings | Vol 1 & Vol 2 | We believe there is a reasonable amount of work that has not been completed, such as standard definitions, which may lead to inconsistencies between the water organisations. Without this work being completed the documentation that has been produced could only be used as a guideline or a code of practice. | Noted: no action required | All definitions have been standardised and normalised | No Specific Reference | No action
923 | 3-Waters | Vol 1 & Vol 2 | However, page 141 of Potable Water Volume 1 As-constructed/As-built references code lists for 3 waters assets that can be reviewed in a supplementary document called 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016 Is this document available for download or can it be emailed to me? I would like to cross-check what is in this code list against the attribute tables to assist with my review. | Included | Code lists are included | General | Change made document updated
924 | 3-Waters | Vol 1 & Vol 2 | As-constructed schema should not be a separate document, and should recognize that many assets are created though term contracts not just greenfield build. We should not separate “as-constructed” from other elements of the standard because this perpetuates last century’s practice of asset management being about the asset whereas it is about the service enabled by the asset. We should modify the “as-constructed” schema to recognise that construction happens both in new builds and in renewal term contracts and the information should support both efficiently. I am not convinced of the value of separating the standards into two parts. While as constructed data is central to an asset information system there are few transactions that use it in practice. Most construction projects will use subsets of the inventory tables, performance based construction projects will also use the condition and performance tables, term PPP or BOOT contracts will use almost the entire standard. This means there is no one to one connection between projects and elements of the entire data schemas so the split of the source documents is artificial. I think there is a serious downside to separating the two documents that drives us towards a combined view. Asset management is all about delivering services that require significant assets. Separating as-constructed from performance data perpetuates past practice that asset management was about having assets in good condition, whereas it is about having assets in sufficient condition to deliver targeted services. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
925 | 3-Waters | Vol 1 & Vol 2 | Another challenge with this proposed separation and the associated “constructor” reference fields is that for roads and 3 waters, though to a lesser extent buildings, much infrastructure is created through renewal or replacement programmes. For example for State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. This means that we need to think seriously about replacing the “constructor” record in the “as-constructed” table with a reference to an “Asset Intervention” record as described elsewhere in my comments. Unless this is done there will be not be normalisation of records relating responsibility for modification of inventory, a ridiculous amount of duplicate records created from term contracts where much inventory is created, and a mismatch between the constructor records in the “as-constructed” schema and those of the maintenance schema, when in term network management contracts these are the same constructor. The same duplication will occur when the same constructor creates many inventory records as occurs in term contracts | Noted: no action required | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | No Specific Reference | No action
926 | 3-Waters | Vol 1 & Vol 2 | The categories of data type should be simple, exhaustive and mutually exclusive so should vulnerability and resilience stand alone? The proposed “global meta data schemata” classifies data into several categories. This is a necessary and good thing because it help users appreciate the scope of the data and find the elements they may be interested in. To do this well the elements must be simple, described in commonly understood language, cover the field of interest, i.e. be exhaustive, and be mutually exclusive, i.e. not have definitions that overlap or require subtle nuancing. | Included | Included in the draft Standards | General | No action
927 | 3-Waters | Vol 1 & Vol 2 | Vulnerability - risk There is an open question in the document as to whether vulnerability should be drawn out as a standalone data category, when it influences risk. I do not think it should be standalone because this then makes “risk” become “risk other than vulnerability” and I think that is a bit silly. I certainly agree that vulnerability is important. I think it so important that we should draw it out in the risk or resilience categories. The high level approach to risk is to consider likelihood and consequence. Simplistically consequence conflates: • vulnerability of service, and • impact from reduction or loss of service and vulnerability of service conflates: • vulnerability of infrastructure (considering network effects), and • availability of alternate infrastructure or alternate services. I think we should draw out these or similar elements of risk for those elements of infrastructure type that potentially have a consequence greater than tolerable. This might mean (in the transport context) arterials and above in a transport world because of their importance to the economy and society. Effectively this creates a level of service gap around vulnerability, the very gap that rental companies advertise as being closed when they proclaim on their hoardings that a building to let is 85% EQ code compliant. | Included | Included in the draft Standards | 4.2 Vulnerability Schema | No action
928 | 3-Waters | Vol 1 & Vol 2 | Resilience - performance Resilience is a service level, or a strategic goal. As a service level it should be within the performance elements of the data standard. I know that it has prominence because it is an important element of performance, but so too are accessibility and safety for transport, or availability of supply or health for water. As a strategic goal it is a driver of service levels. | Included | Resilience is a state and requires measurement The level of service is subject to the level of service any organisation seeks to apply, and an invetment plan to meet that level | 4.5 Resilience Schema | No action
929 | 3-Waters | Vol 1 & Vol 2 | Utilisation is multifaceted and requires enhancement The definition of utilisation given in the draft standard is the proportion of an assets available capacity that is actually being used. I think that there will need to be some clever messaging to ensure that the unit of capacity chosen is understood for infrastructure in different circumstances. Using a transport example provides an illustration of this. Over 60% of New Zealand’s roads are classified as access or low volume access roads. This means that they have less than 1000 vehicles using them per day. A single lane has a capacity of about 1400 vehicles per hour, depending on its configuration, i.e. on the proposed definition of capacity most roads have a daily utilisation of about 1.5% yet these roads represent the last and/or first mile of most trips and so are critical to our economy and society. The level of utilisation will always be low simply because there are rural and urban areas with low population that are connected to market or work place. Even with planned intensification of central urban areas daily utilisation might only rise to 5%. This is analogous to the smallest element of supply or removal for potable or waste water. Also, where there is suppressed demand because demand exceeds supply, e.g. on congested transport networks (whether roads or busses), we may report 100% utilisation, but that is bad because the potential benefit of suppressed trips is being lost or costing more. In a water example we may constrain the development of business when supply is inadequate for development yet fully used by current development. Together these factors mean that we have to be careful about the utilisation measure and how we use it alongside other measures at a local and network level, a simplistic approach won’t do. I think this section of the draft standard needs work to draw out these issues. In addition we need to consider how utilisation and performance metrics are used to optimise asset investment decisions. | Noted: no action required | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | No Specific Reference | No action
930 | 3-Waters | Vol 1 & Vol 2 | Inventory Interventions At the moment there are two types of works records, those recorded as maintenance and those associated with the as-constructed fields. I think we should consider what we want from the recording of “works” or inventory interventions because I expect that will lead to an improved data structure with one form of works interventions record. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
931 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Planned, current, completed or abandoned works so we can fuel the nationwide forward and current works viewer enabling better coordination of works and reduced disruption of customers whether the works are construction, renewal or maintenance. Interventions on inventory are a process that creates or modifies inventory. Much information is required about the process as much as of the fact that it creates inventory. E.g. the forward works viewer being developed to display proposed and current works have time, duration, and place elements of information as well as descriptive information about the constructor and infrastructure being modified or created as reflected in the proposed “as-constructed” schema. | Included | Statement noted. Already done in Repairs and Maintenance schema. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
932 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Responsibility for management of infrastructure, noting that ownership may pass to a client when inventory enters service, but responsibility for maintenance may extend beyond the transfer date | Noted: no action required | Noted | No Specific Reference | No action
933 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • A hierarchy of works and tasks that distinguish a term contract (or work) from a work task within it so that the work identifies responsibility, type of work, stage of work etc, and the task the date and type of work done linked to the infrastructure impacted. I think this allows better alignment with supplier’s management systems, responsibility for work done, and supports many forms of contract from term based contracts to single task contracts. This also enables security to be built into system for data exchange. This is important because for most infrastructure networks (buildings aside) most new infrastructure arises due to renewal works and not due to greenfield construction. | Included | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
934 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
935 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
936 | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Types of inventory intervention with appropriate records, including, but not limited to: o Physical works, probably the most common type o Waste or abandonment, associated with infrastructure being removed from the inventory and reflected in a valuation as a write-off o Inventory received from third parties, e.g. as a result of transfer from development of a new residential area to a council, or the transfer of responsibility of a road from a local authority to the Transport Agency as a State highway o Inventory transferred to third parties, e.g. the transfer of responsibility of a previous State highway to a local authority on completion of a State highway bypass. I acknowledge that “inventory interventions” is not the best term and that a better one should be found. | Included | Included in the draft Standards | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
937 | 3-Waters | Vol 1 & Vol 2 | Assessments There is an opportunity to introduce a concept of an intervention type of “Assessment”. This arises because there are many instances where responsibility for some parameter in many of the tables is explicitly referenced, yet is essentially the same information in each case. This information is who changed the parameter, when, why, as a result of what process…? This proposed approach will enable normalisation of data describing the assessment of condition or performance (whether current or forecast), valuation, risk or any other metric in a standard way. It will then identify the provenance and responsibility for each. This proposal is much the same as that for “inventory interventions” in that it suggests that the core information is about the process leading to the metric in the data and this should be recognised. | Noted: no action required | Assesments are (or interventions) are subject to the element being interrogated (e.g. condition). The standards have attributes which capture these. These will however be predominantly the focus of the work when develop-ing Volume 3 | Data Table 1: Condition Attributes & Code List 17: Condition Rating – Methodology | No action
938 | 3-Waters | Vol 1 & Vol 2 | Supply of as constructed data I think that we shouldn’t mandate the form for the supply of as constructed (or other data) but rather the relevant metadata describing its provenance, quality etc. If the form is mandated then it would require an absurd level of record keeping and compliance from term contractors who create many new assets. E.g. for State highways we use term contractors who create the vast majority of new surface infrastructure each year. For State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. Suitably qualified and quality assured staff from contractors enter the as-constructed data directly into our inventory system, and this isn’t shown as an acceptable method of delivery yet it patently is. One of the purported benefits of meta-data standards is that it enables business to business transfer of data. Defining the transfer of data on a disc seems to fly in the face of these benefits and the advance of B2B technology. Similarly I would think that NIU doesn’t want to be involved in contractual requirements for each form of contract, rather whether information is being managed well and is fit for purpose. I think the supply of data section starting on page 1 of volume 1 needs review. | Noted: no action required | Data format (form here) is not within the scope of these standards | General | No action
939 | 3-Waters | Vol 1 & Vol 2 | Asset management I think the sections of the standard on asset management need a revision to better reflect: 1. That customer service at least long term cost is the goal, and not maintenance of asset condition, noting that the two are related. 2. Investment decisions made in a customer service centric world. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
940 | 3-Waters | Vol 1 & Vol 2 | Customer service focus The various diagrams, for example figure 3 on page 24 of volume 2 is written in very economic language around the return for investment of public funds. This is of course critical, but loses the narrative that relates providing customer service that is economic. | Noted: no action required | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. | No Specific Reference | No action
941 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: I think the steps in the above referenced diagram, and the description on the preceding pages are missing an element and that is what is being targeted in terms of service levels and how this target is established. Or alternatively (as a poor second best) are missing the inputs describing the economic and social benefits of different service levels experienced by customers. If these were present then the analytics could do the required work. This step is required to establish the performance targets referenced in the performance elements of the standard. Eg what is the optimal economic service level for service outages considering investment to reduce the frequency, duration and impact of service outages against the social and economic impacts of these. This step is difficult and complex but needed none the less. It requires decisions about the relative weight to be given to quasi commercial models or economic models. It requires significant analytics to be undertaken to determine the relationships between costs and benefits of different levels of service for different types of customers in different circumstances. Much of these analytics are represented in the economic evaluation manual used to determine the economic value of transport proposals in New Zealand. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | No action
942 | 3-Waters | Vol 1 & Vol 2 | Customer service focus: The service led approach enables a more informed discussion with customers about expectations of service level and the cost of these than a black box economic model. It essentially proposes a three stage approach: (See figure in word document) This recognizes that information is never perfect to enable ideal one off analytics because customers’ needs, systems and contexts change so what might be optimum now likely won’t be at another time. The aspect of service level target should be reflected in the analytics framework. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. | No Specific Reference | No action
943 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world I think that section 1.8 needs some rework though many aspects are worth keeping. There is significant reliance on the metaphor that as assets deteriorate and consequently the maintenance expense to sustain targeted service levels increases there is a sweet spot between condition and maintenance cost. I think we need to recast that metaphor in a customer centric world and recognize that the sweet spot is tautological because the definition used for condition grade 5 is that it has failed or soon will so it is no coincidence that replacement is needed there. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
944 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world The proposed standard presents a theoretical approach to stochastic analysis. This style of analysis is becoming common place. The standard might reference the UK’s Highways Efficiency Maintenance Programme website, especially this url: http://www.highwaysefficiency.org.uk/efficiency-resources/asset-management/life-cycling-planning-toolkit.html That site includes standard tools for “stochastic analysis” of renewal programmes using the “5-step condition rating”. While the text is all about roads the processes are generic. With translation, or a babel fish (as Douglass Adams might say) they are as applicable to buildings as to roads. The tools on that site are of course single factor analyses as condition based analytics generally are. There is no single or multifactor customer service optimisation (e.g. skid resistance and ride comfort for roads) that assists planning in a constrained environment or in an environment where value for money matters, but it is a straight forward approach to estimating the works required to sustain performance. That reference, or a more applicable one, or a derivative of it, would go some way to making the theoretical text in the proposed standard tangible. | Noted: no action required | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
945 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If the text were recast to be more customer service centric it might use the following approach. The two most important decisions to intervene with some form of monitoring or works when managing a network to provide customer service are: 1. When delivered service levels have or will drop below the targeted level or there is too great a risk that they will 2. When, despite the targeted service level being met, it is cheaper in the long run to intervene, or there is an unacceptable risk that costs will rise unless an intervention is made Intervention decisions can initially lead to a monitor, maintenance, renewal or improvement interventions, whichever is part of the least long term cost intervention strategy. A more colloquial way of putting this is only intervene if its broken, or cheaper in the long run. | Noted: no action required | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
946 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world Transport examples of the two decision types are: Ensuring the service is delivered to target. • Replacing the tires on your car when the tread depth has reduced and become unsafe, or ahead of winter when risk is greatest when tread depth has almost become unsafe • Continuing to monitor the change in direction of a river beside a roadway that may ultimately risk scouring of the road formation in order that preventive works can be taken when necessary and most cost effectively to preserve the transport route • Water cutting the excess bitumen off a road to restore the prominence of the chips so tyres grip these rather than “float” on the water film when the road is wet in order to restore the skid resistance of the road surface. • Resurfacing a road when the skid resistance of a road is falling and is either unsafe or will become unsafe before the next opportunity to intervene because the stones have polished Ensuring that delivery of the service is at the least possible long term cost. • Replacing the oil in your car engine even though it is performing well in order to forestall engine damage • Monitoring the condition and maintenance expenditure on deteriorating roads so that and expected renewal works can be designed and timed to be cost effective long term • Sealing cracks in an asphaltic concrete road surface to reduce water ingress to the pavement which would cause the pavement to deteriorate rapidly and require more expensive repairs • Rebuilding or replacing the structural layers in a pavement when this is the cheapest long term cost because deterioration in pavement strength is leading to the need for significant and increasingly frequent and costly repairs and resurfacing treatments to maintain service levels | Noted: no action required | And, is the intention of the analytical foundations set down for Volume 4. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
947 | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If discussion of the type inferred in the above table were included then the standard would be more tangible to users and better focussed on customer service, the goal of asset management. I think it worth the discussion including reference to or guidance on the economic decision to continue to maintain infrastructure or to renew or replace it on a site specific basis. The IIMM might be suitably referenced. When funds can be used on other investments outside asset management of the infrastructure in question then we look for the sweet spot where the net present value of the renewal plus reduced subsequent maintenance stream is better than the present value of the continued and increasingly expensive maintenance stream. This should be included because it can be implemented site by site for significant investment, and needn’t rely on sophisticated network level analytics and data, though it requires some to describe the relationship between condition, time and maintenance cost. This analysis that maintenance costs typically increase as condition worsens is shown in the following indicative diagram as indicated in the draft standard metaphorical diagrams. This shows there isn’t a sweet spot from this relationship alone. Another factor is required for optimisation and that is the present value of the replacement cost option on a site specific basis, or long term budget on a network basis. (see figures in word document) | Noted: no action required | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
948 | 3-Waters | Vol 1 & Vol 2 | Global Schemata The global asset metadata schemata diagram on page 16 of volume 2 appears out of place with the prosaic listing of detailed data requirements. If it were fully developed as an idea in the text you would expect it to tell a story about why certain data elements are required. No such story is conveyed, so the inference is that whatever data is in the standard will enable such analysis, if that were true then the benefit of the advanced analytics would be small. That seems odd. Does this description add value? | Noted: no action required | The diagram provides context for the detail that follows There are some who are already applying this level of complexity to decision-making. | 1.4 Context of Asset Data and Analytics | No action
949 | 3-Waters | Vol 1 & Vol 2 | Network level performance targets The standard for service performance p101 vol 2 as proposed enables the measurement of performance against a target. This is good. However there is no reference to what good looks like so the measurements are just that. It may be useful to add records that: • Enables the categorisation of target service levels • Set service targets for each performance aspect for each category This would provide the data required to enable reporting of whether the service provided was good enough or not, in a situation where targets differ by category. The One Network Road Classification framework developed by REG for transport classifies roads into 8 categories and sets targets for each. | Noted: no action required | Levels of service are policy decisions, and are not within the scope of these standards However, where organisatoins provide these levels, these standards will attribute them and analyse them for decision-making purposes | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
950 | 3-Waters | Vol 1 & Vol 2 | Financial Performance The standard has sections on p88 vol2 and succeeding pages. It would be beneficial to review common good practice to understand what data elements should be here. The Australian Infrastructure Financial Management Guide is one such reference. Here as elsewhere the tables can be normalised by reference to an assessment record as proposed above, the type here being valuation. In addition I would have thought there would be considerable opportunity to normalise valuation approaches by assigning each asset a valuation type, and that type record containing the depreciation rates etc. applicable to it. I am not sure that the valuation section has been fully developed yet because some thought must be given to valuation components being different to asset register components. There is no need for them to be the same as they have different drivers. This sections contains data about construction cost that will be transferred to the “as constructed” tables. It asks that the cost of an asset be supplied and that supply is mandatory. However there is a challenge with this because almost all construction contacts cost elements at a higher level of aggregation than each asset. E.g.the construction of a sewage treatment plant does not lead to an estimated cost per inventory item created. Contracts with lump sum maintenance items likewise have no costs per maintenance work task. Therefore a review is required of how costs are acquired and stored and at what level. I suspect that it will be best to capture financial information at the financial/contractual transaction level and activity at the inventory affected level. The concept proposed above for having transactional records for works and tasks enables costs to be collected at that level. | Noted: no action required | There is an opportuity to reflect on the tables and code lists provided in the standards. There are some analytical assumptions being addressed here, which are for the analytics in which will be unpacked in more detail in Volume 4. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
951 | 3-Waters | Vol 1 & Vol 2 | Information required to manage well varies by criticality of network and context I expect that, as with roads, the information needs of managing a water network in a simple undemanding context differ from those of a demanding context. While the performance metrics around health and availability may be common the needs for sophisticated infrastructure and condition metrics would differ. Similarly the information needs for the critical elements in a complex network would be greater than for other elements. This would lead to a hierarchy of mandatory fields based on context. I think this should be considered. | Sector Discussion | To discuss | 5.4 Service Performance Schema | No action
952 | 3-Waters | Vol 1 | pg 3: Validating the data submission: is this to go against each asset or an organisational process requirement? | Included | Against each asset and against each attribute | General | No action
953 | 3-Waters | Vol 1 | 1.8 They are requesting that “each asset type must be delivered on a separate level/layer and the files must be clearly labelled…” If this is in a CAD format this makes perfect sense, but then the attribute information that is being requesting won’t be able to put against the individual asset (when last I tried this, it can only be done with blocks, and blocks can be tricky to convert to a shape file). But if in a shape file format, it is a bit of an overkill, it is structuring back to the way we used to have it. And we will need to combine the information in order to import into Assetfinda. it is also implying that information from contractors will be to a High enough standard that we can suck it into our GIS and all points and lines will meet perfectly. In a perfect world that would be great, but from having a draughing background. I can guarantee you are going to get hydrants, valves etc. not matching perfectly with your pipes (this comes from the skill of the person doing the as built) and greater maintenance issues later. We would be relying on the project managers to insist on high quality as built. This then brings up the issue of disposals of existing infrastructure. Or the assigning of asset id numbers that have intelligence. | Noted: no action required | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | 1.8 Theme Structure | No action
954 | 3-Waters | Vol 1 | 1.11 Projects will need to be on board with this. | Noted: no action required | Noted, but out of scope. | 1.11 Acceptance Testing | No action
955 | 3-Waters | Vol 1 | 2.1.1 Precision needs to be clarified on what is acceptable. | Included | Precision is defined in the standards | 2.1.1 Accuracy Requirements for Locating Assets | No action
956 | 3-Waters | Vol 1 | 2.1.5 In the proposed structure, the data Code list fields will be limited to 10 characters, this is not going to allow us to use unabbreviated materials e.g.: uPVC instead of PVC Unplasticised. We need to decide on this now as it affects the look up tables and associated finance. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the Full Name once the asset data is provided. | 2.1.5 Attribute Data Fields | No action
957 | 3-Waters | Vol 1 | 2.1.8 The attribute fields they are suggesting may impact on Assetfinda fields e.g.: they are the same but have different criteria. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
958 | 3-Waters | Vol 1 | 2.4.1 For Access chamber of valves they are requesting one location point, which is what we have and one polygon of the same area representing a plan view of the valve pit. We have over 2000 valves, that is a lot of additional files, and I feel a duplication of work, as the plan view can already been seen as a schematic when viewing the reticulation. - The same as above goes for Storm water | Sector Discussion | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | General for Access Chambers and Valves | More information required for a decision
959 | 3-Waters | Vol 1 | 2.4.7 Says that pump stations should be a polygon feature and all attributes are to be attached to this polygon. Then in 2.5.2 which refers to Pumps it requires pumps to be a point feature with all attribute information attached to this point. So which is it. The Pump station, the pump, or both? - The same as above goes for Storm water | Noted: no action required | The pump station refers to site specific information. The pump is the asset specific information. | General for Pump and Pump Station | No action
960 | 3-Waters | Vol 1 | 2.6.2 Cathodic Protection- I don’t know what that is. | Noted: no action required | This refers to systems installed to protect water mains from corrosion. | 2.6.2 Cathodic Protection | No action
961 | 3-Waters | Vol 1 | 2.8.2 This puts all the responsibility on the contractor to provide all the specified information in the way the document wants it, with us only needing to import it. - The same as above goes for Storm water | Noted: no action required | It also puts the responsibility on the asset owner to specify it properly | General | No action
962 | 3-Waters | Vol 1 | All the attributes that are being requested of us seems to me to be a lot more information than will ever be needed or used, but if supplied by a contractor as suggested, is achievable. | Noted: no action required | Noted, for analytical purposes | General | No action
963 | 3-Waters | Vol 1 | Waste Water seems to be a repeat of the above. | Noted: no action required | Repeat | General | No action
964 | Potable water | Vol 1 | In Summary The main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed potable water assets as defined by asset managers in New Zealand. While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant. It’s not clear who is meant by consultants here. | Included | Note added in glossary 9/3/2017 | In Summary | Change made document updated
965 | Potable water | Vol 1 | The objective of the specification in Volume 1 is to provide geospatially savvy potable water asset “As Manufactured” and “As-constructed / As-built” digital data. The objective of the specification in Volume 2 is to provide geospatially savvy potable water asset “As Managed” digital data. I don’t like the use of the word savvy | Included | Reviewed and removed | General | Change made document updated
966 | Potable water | Vol 1 | Table 1.8 doesn’t appear to include an allowed category or descriptor for “back-flow preventer” | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | 1.8 Theme Structure | New Code List Entry proposed | Back-Flow Preventer
967 | Potable water | Vol 1 | I presume in Table 1.9 that “N” stands for No. I’m sure there will be some exceptions to the rule per asset | Noted: no action required | Reviewed and Noted only | 1.9 Data Principles | No action
968 | Potable water | Vol 1 | 2.1.1 The explanations on pages 6 and 7 between absolute accuracy, relative accuracy and spatial precision are useful; however I think the sector needs to derive one preferred conceptual practice i.e. is absolute accuracy more important than relative accuracy? Whose data set has primacy? E.g. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | 2.1.1 Accuracy Requirements for Locating Assets | No action
969 | Potable water | Vol 1 | I agree with the QA Validation field being a mandatory attribute in Table 2.1.5 | Noted: no action required | Reviewed and Noted only | 2.1.5 Attribute Data Fields | No action
970 | Potable water | Vol 1 | Not all fields in the project attribute table in 2.1.7 are practical. What about a project that is geographically separated (relining different pipes) or across different asset classes? (e.g. water mains and sewers) | Noted: no action required | Reviewed and Noted only | 2.1.9 Project Attributes | No action
971 | Potable water | Vol 1 | 2.1.1 Pg 17 . Ditto for “Area of Work” extent. | Noted: no action required | Reviewed and Noted only | 2.2.1 Area of Work Extent | No action
972 | Potable water | Vol 1 | 2.3.1 How will an open civil structure be represented? E.g. a settlement pond | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | 2.3.1 Containment Structure | More information required for a decision
973 | Potable water | Vol 1 | The repetitive use of the generic term “Health & Safety Issues” in the respective attribute tables should be revised to documented Health & Safety Risks. Or similar | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure trigger there are 'special circumstances'. A code list is proposed | General | More information required for a decision | Health & Safety Type
974 | Potable water | Vol 1 | I’m unsure what the use of a “Resilience field (as an open text field?) is in these tables. Too much variability and not enough guidance around what data and format to enter. This is an AM (Vol 2) derivation anyway and not an “As-Built” attribute in my view. Whereas “Design Life” is. | Noted: no action required | Resilience Rating is a measured a6ttribute | 4.5 Resilience Schema | No action
975 | Potable water | Vol 1 | 2.3.4 The term Well should be changed to “Bore” | Sector Discussion | Commented on this previoulsy | 2.3.4 Well | More information required for a decision
976 | Potable water | Vol 1 | 2.4.3 The point feature is to be “snapped” to the pipe asset it is associated with. Does the spatial representation snapped to the polyline create a node? If not then this creates problems when modelling. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed | 2.5.3 Valve | No action
977 | Potable water | Vol 1 | 2.4.5 How is a locator cable or Intrinsic Protection (IP) cable for anti-corrosion ruining with a pipe (e.g. taped to the pipe) to be represented? Why in the table do we have to submit pipe diameter, nominal diameter, external diameter and nominal bore? This is overkill and one wrong piece of information will lead to confusion i.e. which one is the correct one? | Sector Discussion | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | 2.4.5 Pipe & 2.6.2 Cathodic Protection | More information required for a decision
978 | Potable water | Vol 1 | 2.4.7 Should the spatial representation include and ancillary works e.g. dry wells, wet wells, filters, air scrubbers or bio-filters (more applicable to wastewater PS I realise) | Noted: no action required | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. | 2.4.6 Pump Station | No action
979 | Potable water | Vol 1 | 2.5.2 Pumps, can take many types and forms. I trust the fields in the table are flexible enough to accommodate the variety to be expected. | Noted: no action required | We hope so. This will be tested during the pilot phase | 2.5.2 Pump | No action
980 | Potable water | Vol 1 | Is a backflow preventer to be considered a mechanical equipment asset or a valve? | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | 2.5.1 Equipment & 2.5.3 Valve | More information required for a decision | Back-Flow Preventer
981 | Potable water | Vol 1 | 2.6.1 Electrical asset – table doesn’t look accommodating enough for the variety of electrical fittings and assets to be expected | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | 2.6.1 Cabling | More information required for a decision
982 | Potable water | Vol 1 | 2.6.2 Good to see Cathodic Protection systems included. | Noted: no action required | Reviewed and Noted only | 2.6.2 Cathodic Protection | No action
983 | Potable water | Vol 1 | 2.8.2 reporting Mismatches could be problematic depending upon the spatial base used – see 2.1.1 above. | Noted: no action required | Reviewed and Noted only | 2.8.2 Matching to Existing Infrastructure | No action
984 | Potable water | Vol 1 | There are a heap more Definitions that could be added to the Glossary e.g. “trunk main” for starters. | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Glossary | More information required for a decision
985 | Potable water | Vol 1 | Request for code lists: On page 158 of volume 1 of the potable water standard there is mention of supplementary document 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016. Even though this document is in draft, I’d really like to take a look at it. Can it be made available for download, or am I to a copy emailed to me? | Sector Discussion | Code lists now incorporated into document | General | Change made document updated
986 | 3-Waters & Buildings | Vol 1 & Vol 2 | We appreciate the work put in by your team and the various working groups in developing these documents. The process of evaluating the standards has also been useful for Education as an agency, in promoting a review of our data collection processes and considering how these align with a potential implementation of the standards. Our comments on the standards focus at the strategic level. For our organization, with over 30,000 buildings, the cost of changing data collection are high. We therefore need to consider very carefully what information we capture, what decisions we will need to take with information, how we control the quality of information and how it is updated. For that reason it is important to us that we understand the proposed benefits and implementation uses of the standards before taking firm decisions on data collection for their use. We look forward to further discussion on implementation. Your presentation at the last governance group was a helpful insight into your team’s thinking: we want to ensure that agencies understand each other before committing to implementation or advancing a business case with Ministers. For that reason our comments are interim, subject to these further discussions. | Noted: no action required | Statement noted. | General | No action
987 | 3-Waters & Buildings | Vol 1 & Vol 2 | Overview of the Metadata Standards Education recognises the importance of asset information in protecting New Zealand’s ability to provide services in a fast-changing national economy. We also endorse a commitment to standardising and sharing information between public agencies. However, we have concerns about the detail and structure of the data proposed in the metadata standards. A challenge in commenting on the proposed metadata standards is understanding the objectives of the data collection process. It remains unclear how this information will be used, what elements of the process will be compulsory and how the comparison between agencies will work. Education is concerned that the costs of collecting the information outlined in the metadata standards will exceed the benefits. Understanding the benefits derived from these comparisons is critical to determining what data should be collected and how it should be categorised. For instance, the data that is needed to promote All-of-Government procurement is very different from the data needed to identify major network risks within New Zealand | Noted: no action required | Statement noted. Business case. | General | No action
988 | 3-Waters & Buildings | Vol 1 & Vol 2 | Education is also concerned that the focus on the physical condition of the assets may be poorly targeted. Rapid changes in demographics profiles, technology and consumer preferences will also have a major impact on the ability of the current asset networks to meet the future needs of communities. We think that the metadata project should place as much emphasis on the ‘fitness for purpose’, as it does to the physical condition. | Noted: no action required | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | General | No action
989 | 3-Waters & Buildings | Vol 1 & Vol 2 | In addition, the metadata standards assume that decisions on asset maintenance are made centrally. Where maintenance decisions are made is a policy choice that is influenced by broader factors than asset management. In the case of Education, asset maintenance decisions are largely managed at a school level. This is a fundamental premise of how the management of schools is devolved to local communities. This is more responsive to the needs of local communities, as well as meaning minor maintenance decisions can be made in the context of education delivery. However, this also means that, while we fund schools for maintenance, we do not specifically control how that funding is spent. This limits the extent to which Education is able to track maintenance expenditure. | Noted: no action required | This standard does not assume where or how decisions are made, it is a set of metadata standards that define decision elements for analytics to support those decisions - in a standard way | No Specific Reference | No action
990 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: Education’s documentation for new construction includes much of the data outlined in the Metadata standards. However, while we collect and hold this information for each project, we do not capture this data into a central database. The nature of this information is useful when looking at the details of potential redevelopment of an asset but not for evaluation at a portfolio level. As with our response to the overall project, Education believes that clearly articulating the benefits of the process will better inform how and what information needs to be collected. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
991 | 3-Waters & Buildings | Vol 1 | Broad strategic issues: We are aware that much of the information for as-built projects will be provided by the contractor. However, we have concerns that the rigorous specification of data may limit the pool of contractors to larger firms with the resources to provide information in a metadata standard. There is a risk that this reduces competition in the industry, and creates price increases especially in provincial centres where Education operates. Education’s exposure to price increases with small building firms is more pronounced than other government agencies who may build a smaller number of more complex facilities (e.g. Courts, Corrections, Defence). | Included | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | N/A | No action
992 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
993 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | Repeat | N/A | No action
994 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education’s ability to maintain the quality of data is also limited by the devolution of maintenance and minor capital works to schools. Most of the subsequent alterations to buildings are controlled by the schools. Reconfiguring teaching spaces is a regular occurrence across the portfolio but it is unlikely that these changes will be updated in as-built records. | Noted: no action required | Implementation considerations are out of scope | General | No action
995 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The detail of components specified in the metadata standards appear to be very granular for many of Education’s buildings – for instance there are about 200 fields to describe a building ceiling. The majority of Education’s building will be a simple domestic-scale or light industrial structures, where there is little benefit in collecting this level of detailed information. | Noted: no action required | Implementation considerations are out of scope | General | No action
996 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education would recommend that different levels of information are collected for different types of assets. For instance, complex multi-storey buildings with lifts, fire protection and science laboratories, would require more extensive data to be collected than single-storey wooden-structure school buildings. | Noted: no action required | Implementation considerations are out of scope | General | No action
997 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The information Education collects on underground services varies greatly depending on the scale and nature of the development. Many of Education’s developments are additions or small schools in provincial locations, with work undertaken by local building firms. The ability of small contracting firms to record in detail where underground services are located is poor, and records are unlikely to be available in an electronic format. Detailed collection of this data may be appropriate for major assets. However, we recommend that collection of geospatial information on underground services is restricted to the larger or more complex developments. | Included | Implementation considerations are out of scope | N/A | No action
998 | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The risk assessment analysis in the proposed standards is difficult to interpret and evaluate especially for the type of assets being developed by Education. The scale of Ministry buildings tends to be domestic or light industrial in scale. The risk implications for different components of the assets (such as the roof) cannot be easily separated from the risk profile of other components of the building. We recommend this aspect of the risk criteria of the Metadata standards be critically reviewed. | Sector Discussion | The standards make the separation of components and the analysis of risk at a component level of granularity possible. There will be a further discussion about this level of recording with the technial working group. | No Specific Reference | More information required for a decision
999 | 3-Waters & Buildings | Vol 2 | Broad comments The focus of the data collection is around the building envelope (walls, roof) with significantly less focus on the interior assets. However, building interiors represent a large component of the total cost of providing assets and are the components with the shortest life expectancy. The interior configuration has a major influence on the ability of school buildings to generate positive educational and social outcomes. For these reasons, Education believes the metadata standards should have a greater focus on the interior assets and configuration. | Noted: no action required | All components are collected, including interior components | No Specific Reference | No action
1000 | 3-Waters & Buildings | Vol 2 | Broad comments As well as the definition of the data held, the metadata schema will need to outline the data structure and hierarchy. If information is not collected at a consistent level in the asset hierarchy it makes comparisons between entities difficult. For instance, it is difficult to compare what proportion of the portfolio has fitted wall insulation, if one agency collects the information by building and another by facility. This aspect of the standards should be reviewed. | Noted: no action required | Data Classification, Heirarchy and Structure are all outlined in the Draft Standards | No Specific Reference | No action
1001 | 3-Waters & Buildings | Vol 2 | Broad comments The amount of information collected about the assessor for each data category is unnecessary. It is always useful to know who undertook the assessment but the collection of qualification and experience against each asset is excessive. This detail should be replaced with a measure of confidence around the measures, such as whether it was the result of an exhaustive analysis or a desk-top assessment. | Noted: no action required | Each organisation will decide at what level of granularity (detail) it collects tdata to manage its assets. | No Specific Reference | No action
1002 | 3-Waters & Buildings | Vol 2 | Detailed comments on categories of data The metadata standard outlines the format and categorisation of data on the assets. The following considers each of the categories individually. It discusses these in broad terms and then outlines how Education collates and reports of these asset categories. | Noted: no action required | Statement noted, no action required. | No Specific Reference | No action
1003 | 3-Waters & Buildings | Vol 2 | Condition: The metadata standards propose that condition measures categorise assets by: structure; external; interior; services; and fittings. Separating external cladding and structure is a useful differentiation for some of the housing and light commercial categories. The detail captured on the interior is overly simplistic. The proposed metadata standards focus on cosmetic issues such as the quality of the paint finish, rather than configuration and functionality which is of greater importance for Education. As noted above, interior components represent around one-third of the total building cost and have the highest depreciation rates/shortest lives. Ministry measures: The broad asset categories used by Education are: external; interior; services; and roof. More detailed condition data is held for individual schools but the revaluation and portfolio reporting for Education uses these four categories. Education is currently reviewing options to measure how different building design and fabric choices impact on the light, air quality, temperature and noise levels in teaching spaces. | Noted: no action required | Condition Elements are covered in detail in the standards They do not differentiate buildings by type, beyond the Building Code definition of Facility Importance (which is not building type) These are asset metadata standards, not portfolio form / function and mix standards | 2.2 Condition Schema Code List 13: Facility Importance Rating | No action
1004 | 3-Waters & Buildings | Vol 2 | Repairs and Maintenance The definitions of repairs and maintenance defined in the metadata standards are reasonable and workable. 1. However, collecting data on deferred maintenance items is too complex and unproductive. Part of the issue is that subsequent work may override the maintenance items, but be difficult to identify and measure. Under-maintaining an asset may be best reflected in the condition assessment process. 2. Ministry measures: Education currently identifies programme maintenance items to be undertaken on a building, including recurrence timeframes. Education also categorises the reason for maintenance according to priority (i.e. health and safety, protection of building etc). While Education has a good knowledge of the budgeting for repairs and maintenance, it does not track specific expenditure, accountability for which has been devolved to schools. This means that the explicit scope of work that has been undertaken is not available in Education’s information systems. | Included | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
1005 | 3-Waters & Buildings | Vol 2 | Utilisation: The utilisation measures by nature need to be specific to the industry in which the agency operates and would tend to be for internal reporting only. There is limited advantage in establishing utilisation standards for comparison between entities with very different objectives. This is more appropriately a component of the annual reporting to stakeholders rather than a metadata measure. Ministry measures: Currently Education has a formula for entitlement of classrooms and other space based on school enrolments. Education measures schools’ provision of space compared to entitlement with an optimal target range of 85% to 105%. | Noted: no action required | Agreed, but the standards apply across all Sectoirs (e.g. Housing Providers) | 3.2 Utilisation | No action
1006 | 3-Waters & Buildings | Vol 2 | Demand There are several problems attempting to identify demand for an asset. These are compounded for school assets, which provide free and compulsory services. Commonly residential and light commercial facilities have a variety of different demand parameters. For instance a school hall will support school assemblies, indoor sports activities and community events. Each of these demands has different physical requirements. Measures of demand are therefore difficult to establish. Ministry measures: Education regularly needs to address circumstances where the demand for a school exceeds its capacity. This would commonly be dealt with by strategies such as the application of enrolment zones. Education uses local and regional demographic trends amongst other inputs to identify demand for additional learning spaces and/or new schools. | Noted: no action required | Demand Section has been updated in Volume 2 And, there are many examples of useful demand analytics for schools | 3.3 Demand Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1007 | 3-Waters & Buildings | Vol 2 | Criticality Applying criticality to residential and light commercial buildings is more difficult than with infrastructure. The metadata approach to defining communities being serviced by public sector buildings is not viable. Communities which use public sector buildings tend to be complex and overlapping and criticality dependent on other assets within the network. The definitions of criticality should therefore be limited to explicit requirements in supporting post-disaster response or recovery i.e. identifying assets which have an explicit function defined by Ministry of Civil Defence and Emergency Management plans. Ministry measures: The criticality for the school as a civil defence centre is an agreement between Civil Defence and the Board of Trustees. This will partially be dependent on other community infrastructure in the location. Schools which are Civil Defence centres are not identified within Education’s central information systems. | Noted: no action required | Critciality will be closely linked to Faclity Importance per the Building Code | Code List 13: Facility Importance Rating | No action
1008 | 3-Waters & Buildings | Vol 2 | Risk The metadata schema for risk measurement works to associate risks with asset components. For most of the risks (e.g. earthquake, flooding) it is more appropriate to associate the risk with a building or site, rather than individual component (e.g. roof). Ministry measures: Education has risk registers at a portfolio level and each school has a risk register. Some of the risks associated with the assets relate to the use of materials (e.g. asbestos). These are also logged on the school risk register but not captured centrally. | Included | Risk can be applied at any level of granularity Analytics enable Portfolio level of risk to be established | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1009 | 3-Waters & Buildings | Vol 2 | Resilience The resilience measures have yet to be developed within the metadata standards. The focus of the resilience measures appears to be around major civil defence and emergency events, such as earthquakes. It will be useful to identify the ‘Importance Level’ as defined in building legislation. A sole focus of the civil defence component of resilience is too narrow. We believe the issues should also encompass the ability to change the use of assets or to reconfigure them for different demand or purposes such Ministry measures: When Education developed the business plan for transportable modular classrooms it aimed for these to constitute a proportion of the network to allow flexibility to respond to demographic changes. | Included | Resilience has been updated in the standards | 4.5 Resilience Schema | No action
1010 | 3-Waters & Buildings | Vol 2 | Design Performance The majority of the design performance schema appears to relate to items of equipment, such as pumps and piping. This represents a relatively small proportion of the assets within Education’s network. The majority of the network is relatively uncomplicated, one and two storey buildings, with limited HVAC or specialist facilities. Collecting design performance at the level of individual items is therefore of limited value. Ministry Measures There are some specialised assets within Education’s portfolio, such as lifts in multi-storey buildings. However, these are few in number and are managed under a national contract. Details on the design performance of smaller components, such as heat pumps are typically held by the school. | Included | There are also mant examples of building design perfomance (Earthquake Rating, Energy Rating etc.) | Table 14: Design Performance Examples | An explanation of Data Science will be provided for at the Technical Working Groups
1011 | 3-Waters & Buildings | Vol 2 | Financial Performance There has been significant effort to develop measures for financial performance within the standards. The proposed standards outline a detailed basis for the collection of valuation, depreciation, time of payment information. Rather than replicate data held elsewhere, it would be more useful to ensure that there are linkages with the agency’s broader financial system. This has the advantage of enabling association of asset measures with other agency performance measures, for instance measuring the asset cost per visitor or student. Ministry Measures Education has recently established a new asset management system (Tribal K2) which tracks budgeting for maintenance and other property costs. The system links to Ministry’s property data warehouse system. This allows analysis and development of a broad range of performance measures. The result is the ability to compare asset performance measures to aspects such as student numbers (e.g. the percentage of students learning in buildings that fall into each asset condition category). | Noted: no action required | Organisation specific financial analytics will be supported by attribution within this standard. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups
1012 | 3-Waters & Buildings | Vol 2 | Service Performance The service performance schema appears to be a raft of unrelated criteria, which individually may be critical to the functionality of the asset, but do not belong in the same category. The result is measures which relate to different levels of assets from components (e.g. disabled access) through to facilities (e.g. iwi interest). A number of the proximity measures, such as kilometres to communities are difficult to establish without further definitions of community. The result is a wide range of criteria which does not allow comparison between different agencies. Similarly, the raft of measures around district plan criteria, such as provision of car parks, is difficult to update. For many public service assets the land will be designated so underlying zonings will be poor indicators of the use of the site. Some aspects of the data, such as iwi values, heritage considerations or community interests, cannot be easily summarised into a data base. It would be better to include an identifier which would highlight whether more detailed analysis is available on file. Overall Education would advocate for service performance to be restructured into a number of separate themes. Ministry measures Education has a basis for evaluating the service levels called the Innovative Learning Environment (ILE) assessment tool. The information is currently collected at a building level and is a requirement of the five yearly capital and maintenance planning process. Education is evaluating ways of standardising the capture of the information. The ILE assessment tool also has facility to include a range of qualitative measures such as ‘how well the design reflects the needs of the local community’ which may be developed in future. | Noted: no action required | No action required with regards to comment son the business case. The standard is intended to system and organisation agnostic. | 5.4 Service Performance Schema | No action
1013 | 3-Waters & Buildings | Vol 1 & Vol 2 | Introduction The Auckland Council family fully supports of the intention behind this standard and has actively contributed in the working groups for roads, residential housing and light commercial buildings and the three waters. The Auckland Council family welcomes the opportunity to provide feedback at this time, and the opportunity to participate in the further development of the standard. The metadata standard is a great opportunity to gain national consensus of what minimum level of data capture is required. This initiative will enable us to ensure that data can be applied in a consistent and repeatable way to make good asset management decisions based on acceptable levels of service, replacement and growth strategies. | Noted: no action required | Statement noted. | General | No action
1014 | 3-Waters & Buildings | Vol 1 & Vol 2 | Summary Feedback is currently sought with specific regards to the three waters and the residential housing and light commercial buildings standards. We have found it difficult to provide meaningful feedback in the absence of a clear strategic message, an understanding of which is shared by all reviewers. That message needs to link the standards to the business case and to recently held discussions with the Minister of Finance. A further opportunity to work on and develop the standard from the ground up, in the way that the transport group has developed the roads standard, would also help the Auckland Council family to feel more confident about the result. To that end we suggest that it would be useful to incorporate such an opportunity into the process from here. We would like: • To present our feedback to the combined governance group • The working groups to review and address all feedback on the standards • The resulting outputs to be made available for consideration by the governance group prior to any public release of the standards | Noted: no action required | Discussions will continue across the Infrastructure Sectors (Core and Social) | No Specific Reference | No action
1015 | 3-Waters & Buildings | Vol 1 | Volume 1 – As-built metadata standard What we like: • Provides reasonable coverage of possible data fields • As a collection of possible attributes it will help to drive a culture of good practice to capture metadata • It brings attention to the need for good base data What we consider could be further developed: • In its current format the standard is not adoptable due to the constraints it will place on systems and business processes this needs to be addressed before it can be adopted. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1016 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • The layout should be modified to clarify the distinctions between master data and metadata. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1017 | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • A number of elements have been included but are not complete, and an understanding of industry definitions, hierarchies and processes is required to complete this volume. We would welcome the opportunity to assist with this. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1018 | 3-Waters & Buildings | Vol 2 | Volume 2 – Asset management performance standard What we like: • Recognition of the notion that data is only useful if it is used • An approach that recognises the value of rigorous analysis to inform decision making What we consider could be further developed: • In general, we consider that this volume is under developed with inconsistencies and cross-overs to Volume 1. We would welcome an opportunity to further input into its development, as we recognise that it can provide a useful tool, particularly for organisations with limited capability in this area. | Noted: no action required | Volume 2 is now a comprehensive document | No Specific Reference | No action
1019 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • This volume assumes generalist practices that are inadequate for non-linear assets and includes operational and derived data that is not suitable for inclusion in an AMIS system. | Noted: no action required | This volume is spatially aware, and will attribute point, line, ployline and 3D objects. It is also agnostic to any AMIS and GIS system | No Specific Reference | This will be discussed at the technical workshops
1020 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Needs to be carefully framed for the asset types that it relates to. | Noted: no action required | Asset types are specifically defined within the standards - See Volume 1 of each Group of Assets | No Specific Reference | No action
1021 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Replacement trigger points should be broadened from reliance on subjective visual condition to incorporate best practice for optimal replacement, that is, based on objective measurement and sound engineering judgement. | Included | Visual inspections are only one type of condition assessment to trigger an interventi. Capacity could be another (at Very High > 95%) | Code List 31: Demand – Capacity Unit of Measure | No action
1022 | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Reference should also be made to failure mode effects analysis (FMEA/FMECA) as a means to support optimal replacement points. Our feedback does not further consider this volume due to the large disparity with practice and limited workshops to fully capture industry needs. | Included | The standards do not preclude failure mode analysis of any type. The standard captures some of the attributes for this analysis. | 2.3.5 Code Lists | This will be discussed at the technical workshops - mor ework is required here with the sector
1023 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 1. Create a separate volume that covers strategic fit and business needs across all asset categories. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1024 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 2. Focus on a business standard for assets including improving the hierarchy to cover both asset and data hierarchies and outline the relationship between them. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | No Specific Reference | No action
1025 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 3. Review publishing formats to maximise the impact of the standard. | Included | The drafts have now had a full publishing edit | General | No action
1026 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 4. Remove content that is not related to the business standard including those referring to implementation paths, delivery mechanisms and quality control rules. | Sector Discussion | To discuss - for example? | General | More information required for a decision |  | haydn to chase up | There are placeholders for Volume 3 / 4 / 5. These require context from time to time, so it is not inappropriate to describe the applicatrion circumstances. | N/A | Close: -
1027 | 3-Waters & Buildings | Vol 1 & Vol 2 | The Workshops The working groups were presented with A-Spec as a straw-man and tasked to focus on the possible data that could be captured for individual asset types. The working groups started with limited traction and concern was raised early on as to the purpose of the workshops in diving into attribute detail that is quite easily obtainable from various sources. A basic data hierarchy was established that allowed the attributes to be tackled in a constructive manner. In hindsight, it would have been useful to consider other industry standards as part of the process. We feel that such consideration could still be undertaken as part of the follow on from this feedback. Despite the concerns mentioned above, the workshop groups generally worked well and came to agreement on the things that were required. It would be extremely useful for the working groups to go over the feedback and address it as appropriate. Strategic, governance and procedural feedback should also be reviewed by the governance groups. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | General | No action
1028 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Definitions of industry terminologies and attributes. | Sector Discussion | Examples required | General | More information required for a decision |  | haydn to chase up | This is a discussion for the Pilot. There are many commercial considerations here, alongside a variety of 'industry standards' as described by the 'industry'. | N/A | Close: -
1029 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Identification of business needs. | Noted: no action required | Business case will outline / describe benefits | N/A | No action
1030 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • An assessment of “fit for purpose” data capture. A matrix and understanding of the minimum data capture required based on organisational needs. | Noted: no action required | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | N/A | No action
1031 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Exploring the origin of the data and identifying whether it belongs to volume one (As constructed) of these standards or is better suited with other data sources, for example geotechnical data. | Noted: no action required | These data sets are what are required for asset management purposes | General | No action
1032 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Validation of the Codes list or optional pick lists. | Noted: no action required | Reviewed and implemented | General | No action
1033 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • The standard is required to be system agnostic. Identifying how the standard will be implemented has an effect on the data capture requirements. To enable this we need to understand what the systems and processes look like. The standard needs to be reconciled with these systems and processes at organisation level. | Noted: no action required | Updated | General | No action
1034 | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Comparison to international practice and other complimentary standards. | Sector Discussion | Information to be provided for discussion | General | More information required for a decision |  | haydn to chase up | There has been a number of reviews against international standards. These (eg OGC) have been aligned to the standards. We will continue to review the standards throughout the pilot for application, due to the variable nature of these standards | N/A | Close: -
1035 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • There is a logical split between roads, buildings and three waters; however there is less logic to further splitting up the three waters when the majority of the components and attributes are the same. It would be sensible to consider consolidating these. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
1036 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Rather than repeating the introductory statements in both volumes of each version of the standard a covering or base document (as seen in most other standards) should be considered, as the principles of data collection are the same. This would also have the advantage of slimming the volumes down. | Noted: no action required | Format based on technical differentiation | General | No action
1037 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Common data sets are repeated at every asset class adding unnecessary volume. | Noted: no action required | Action on data scientists. | General | No action
1038 | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • The standard seems to reference the manner in which data will be collected. This is the responsibility of the various organisations and should not form part of the standard. | Noted: no action required | This is not within the scope of these standards | General | No action
1039 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The document will benefit from a better structure around the rationale, strategic drivers and added benefits, of the standard. Some of this information is scattered across the introduction section but it could be strengthened and focused on the purpose of the standard, which is about agreeing on common classifications and definitions. We think there is general agreement that data standards are needed and this doesn’t need to be emphasised. | Noted: no action required | This is not a policy report, an asset management plan, nor a 30 Year Infratsructure Plan (where you would find this requirement). This is a metadata standard for assets at an assetID level of granularity. It does however capture the context of the analytics which inform these types of documents which support organisations asset management | No Specific Reference | No action
1040 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • We believe that the key purpose of this standard should be to outline data requirements that enable organisations to compare their performance and share asset lifecycle knowledge while continuing to measure their performance in a meaningful and cost effective manner in the context of their strategic objectives. | Noted: no action required | Statement noted. | General | No action
1041 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The intention of this standard development was to produce a metadata capture culture and identify the appropriate level of capture. This intention has been somewhat obscured by the very much “field-base” information that is supplied by suppliers and contractors on the physical attributes of assets. We believe that it would be useful to reconsider the audience of this standard and review it to ensure that the audience is appropriately targeted. In that way the business strategy can direct appropriate attribute fields, which will then be common sense as long as common definitions are understood. | Noted: no action required | This observation describes on audience, this is not the only audience, for example design engineers. | General | No action
1042 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Data capture, as acknowledged in the standard is but one component of good asset management and the ways in which this initiative will support organisational challenges such as achieving ISO 55001 accreditation could be made clearer within it. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1043 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The standard strategic goal is to enable organisations and the country “to collect locally and use globally”. It is unclear how this standard compares and incorporates international best practice. There are examples of other international metadata standards however only A-Spec was examined. | Noted: no action required | A number of other standards have been investigated. (Uniclass, Cbi, Omniclass, Master Spec etc. etc.) The strategic goal is to enable organisations and the country “to collect locally and use nationally” | No Specific Reference | No action
1044 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The way in which the standard is currently written presents the data capture requirements in a set manner and format thereby requiring business needs to be moulded for the data specific needs. These limitations are likely to prevent users from taking opportunities in system and process advances that may become available. Some of these initiatives already exist such as open data sources from product suppliers. We expect these advances to become more readily available in the future. It is not clear how the static two-dimensional model presented by this standard will allow business to incorporate these changes. | Noted: no action required | The standard does exactly the opposite to what this is suggesting. The question is not so much about how it is collected but how the data is manipulated into a common format when it is (see FME) | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1045 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Existing systems have been heavily invested in and are very diverse, even in the Auckland council family, to tailor for specific needs. With the possibility of the standard purely becoming a mapping exercise; it then does not support the need to prescribe data fields to intricate detail. The level of data capture required to complete the national level analytics is not identified. Anything else is considered optional and does not support the reason for capturing data at every level. | Noted: no action required | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. But Note use of tools like FME. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1046 | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • In order to address the matters referred to in the point above, the standard could be reconfigured to provide the required performance outcome and guidance on how these requirements may be met, while allowing flexibility in means and methods of demonstrating compliance. | Noted: no action required | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. And, there are many analytcal options on the same data sets depending upon he problem being solved. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups
1047 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • As has been mentioned previously, the document uses terminology and jargon that is not consistent with those used in NZ. This is an easy fix, and appropriate language is a great factor in the ease of adopting new things. | Included | The drafts have now had a full publishing edit | General | More information required for a decision
1048 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • There are plenty of NZ examples of assets of each class and type, and we will be happy to provide some if required. Using Australian examples in a NZ standard is not appropriate where there is a suitable local example available. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | to be done | Refer to Volume 1 Will be updated by 30 June | N/A | Close: -
1049 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • It is also important that the examples used are relevant to the asset type contemplated in the standard. Building examples for the residential housing and light commercial standard will make the logic of the approach more apparent. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision
1050 | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • Most of the terminology used in the attribute fields is not defined. Without these definitions data cannot be accurately mapped and the data collector will be left to assumptions that will compromise data integrity. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision
1051 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • At the beginning of the working group workshops we agreed that these are business standards – hence system agnostic; this is even mentioned in the document. At the same time the proposed standard – language, data formats and terminology – has been prepared for an easy input to a functional specification for a GIS application. It is evident that the asset classification and the attributes were “flattened” to fit this particular implementation. This has detrimentally affected the business value of the standard – we have a number of attributes that do not belong to the asset class they are listed against. An example: in stormwater, swale only attributes are elevated at channel level, at which level they are meaningless. | Sector Discussion | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | General | More information required for a decision
1052 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The current format of data requirements as a mix of business standard and specification is of particular concern. On one hand it makes the business part of the standard logic hard to follow, while on the other hand the document is not sufficiently detailed to be effective as a functional specification. As a consequence standard does not show the business what it needs to collect and the application vendors will not understand what they need to build. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1053 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The asset data hierarchy needs to be completed. Most importantly the way assets have been grouped for data capture needs to be reconsidered in order to represent the business asset hierarchy. Business hierarchy is of great importance for FMEA, operation and maintenance of complex assets, for example. The exclusion of business hierarchies from the standard will require every organisation to create another set of rules outside of the standard in order to maintain these relationships. | Sector Discussion | The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers that in turn will provide consistency to the asset owners. As each organisation has their own hierachy it is expected that they will categorise the data being provided according to their needs | General | More information required for a decision
1054 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • We strongly recommend that all implementation related fields be removed from the document, as outlined below: o Attribute abbreviations – these are in many cases system related setup and for instance instrumentation may be adopted by numbering systems such as ISA55 that is international practice. The purpose of these abbreviations is not clear. o Character length – This serves no purpose and is not supportive of being system agnostic. By providing full and proper definitions to the attribute field data may be mapped correctly, regardless of character lengths. o Comments – This filed has no purpose that cannot be fulfilled by either the unit filed or description fields o QA validation – These are rules set by business and specific software systems. It also does not serve any purpose to identify minimum capture level. This could be done in a better way through a developed hierarchy that identifies, master data from metadata and compulsory fields from conditional or optional fields | Included | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | General | No action
1055 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • To date geometrical and topology rules have not been discussed. Currently there are different requirements governing the way geospatial data is captured. As with the asset management systems, investment has been made in maintaining systems to these rules. From an analytics point this does not seem to have any impact on the analytic output. Development of such a standard is considered to be a separate endeavour in its own right and has the potential for having great cost impacts to organisations. In the same way one could argue other data sets must then be prescribed – such as geotechnical information, drawings and so on. Flexibility is key, as planning for known technology, given the pace of technological change, will mean that the standard is out of date before it is published. | Included | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | General | No action
1056 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • Attribute sets are not normalised across the asset classes. An example of this is the repetitive material types in the codes lists. (Note. Watercare, Wellington Water and Christchurch City Council were the only parties to receive the codes lists later on request. This was never published. | Included | It is acknowledged that codelists will need to be dynamic in nature and will be open to continued contribution from the sector. The code lists are now incorporated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | General | No action
1057 | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • As-built data versus operational data versus derived data is crossed over between the volumes. Separation is required through the data hierarchy. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1058 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 1. Create a separate volume for strategic fit and business needs | Noted: no action required | To discuss | No Specific Reference | More information required for a decision
1059 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Improve the Asset Hierarchy section to cover both asset and data hierarchy and to outline the relationship between them. | Included | Asset Classifications have been defined in the Standards | General | No action
1060 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and simplify attributes specifications; all attributes that do not belong to the As Built standard, such as demand, repair and maintenance, health and safety issues, service and financial performance should be removed. These are time related measures and events that are covered by other parts of the standard. Connecting these events and measures to assets is the subject of asset analytics, not the as built standard. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
1061 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and clean the attribute tables – remove all values that are included as they are not relevant. | Sector Discussion | The standards have harmonised and standardised data and hierarchies across the standards | General | More information required for a decision |  | haydn to chase up | An addition of explanation has been added to standards - completed | page 1 | Close: -
1062 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Clean the relationship between asset classes, attributes and values. One asset class has to belong to one asset category. | Included | Asset Classifications have been defined in the Standards | General | More information required for a decision
1063 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Outline a list of core asset characteristics – the whole concept of the standard as vehicle for comparability becomes meaningless if we don’t agree on a few critically important attributes that must be collected. | Noted: no action required | Mandatory, Optimal, Optional will be discussed with the sectors | No Specific Reference | More information required for a decision
1064 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Our recommendation is to add a section on asset geometry and topology for water networks – but not one that could be mistaken for a specification for GIS applications. This section needs to address the core rules for creating geometric networks and outline the participation of all assets in these networks. | Included | Included in the draft Standards | General | No action
1065 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Since all standards are related and are part of the same suite of documents it would make sense for them to be published as related volumes (chapters?) rather than independent books. | Included | This has been reviewed, and a decision to keep as separate documents made - at this time (the documents would be 300+ pages if combined | No Specific Reference | No action
1066 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Another approach to publishing standards which would be effective is by using links to look up the list of attribute values. | Included | Other access toolss will be reviewed before release in July 2017 | No Specific Reference | No action
1067 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Think about publishing the data tables in a data view in addition to the document | Included | Included in the draft Standards | General | More information required for a decision
1068 | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 4. Remove content that is not related to the business asset data standard: • We strongly recommend that all references to implementation paths, delivery mechanisms and quality control rules be removed from this document. This should be a subject to a separate project/ research due to the variety of business models that can be applied. Unless there is a directive for a centralised implementation of these standards, they remain the responsibility of each organisation and have to be adapted to the particular technology platform. | Noted: no action required | Unclear of where there are examples of this | No Specific Reference | No action
1069 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1070 | 3-Waters | Vol 1 | Asset class definitions needed: Need clear definition of asset classes. Channels are particularly bad examples; they cover a range of assets with various function and purpose - and badly. Under current structure there is no way to describe sw treatment devices. | Sector Discussion | Classifications and types defined in the standards Refer to code lists | General | More information required for a decision
1071 | 3-Waters | Vol 1 | Attribute definitions needed: Many definitions are unclear or missing. Some appear to be database oriented - need to be business meaningful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1072 | 3-Waters | Vol 1 | Standard is about structured data, not any information about assets: This standard should cover the data that needs to be captured in as structured way for further analytical and reporting use. Hence all data that has no such value needs to be removed. In complex assets most of the asset specific data is kept in operation manuals and other operation related documentation. | Noted: no action required | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | General | No action
1073 | 3-Waters | Vol 1 | This is volume one - as constructed assets. Remove all data that is not relevant to as constructed - there are other volumes that this data is described | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1074 | 3-Waters | Vol 1 | Huge number of attributes that are not relevant and not agreed. Need to go back to the workshop discussions and agree how feedback following working sessions will be captured - cannot afford to continue like that. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision
1075 | 3-Waters | Vol 1 | Renewal material in pipes. This should be relabeled to say lining material. | Included | Attributes included, lining material included in standards see code lists | General for Pipes | No action
1076 | 3-Waters | Vol 1 | Missing attributes. Lining material installation data is critical | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision
1077 | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Noted: no action required | Information to be provided for discussion refer to ID1069 | General | More information required for a decision
NEW001 | 3-Waters | Vol 2 | Code List 9 - people with a spade won't understand the difference between these codes, as they are all the same thing to the person on the ground | Sector Discussion | Codelist 21 on page 45 | [6 empty] | Action: - Graeme to provide a new table to Haydn, who will copy and replace the existing table | Graeme provide the codelist |  | DUPLICATE see NEW005
NEW002 | 3-Waters & Buildings | Vol 1 & Vol 2 | In volume 2 there is a space to define mandatory - but there isn't the same in volume 1. what's going on? | Sector Discussion |  | General |  |  |  | understanding the importance of data, and what is essential v optional, will be determined during initial implementation | understanding the importance of data, and what is essential v optional, will be determined during initial implementation | Action: - Haydn Remove the mandatory field from volume 0 | Haydn |  | Completed
NEW003 | 3-Waters & Buildings | Vol 2 | Need to include an attribute where something hasn't been assessed yet | Sector Discussion |  | General |  |  |  | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty |  | Action: - George to add 'not assessed' as an attribute where needed | GISSA |  | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty
NEW004 | 3-Waters & Buildings | Vol 1 & Vol 2 | There are potentially occurances where the standards include code lists, where not enough information is known to make the code lists finite - suggestion that these code lists are flagged as being examples etc | Sector Discussion |  | General |  |  |  | Completed Added to standard |  | Action: All required additions/changes to code lists to be provided to GISSA by COB 2nd June 2015 | GISSA |  | Completed Added to standard
NEW005 | 3-Waters & Buildings | Vol 2 | Table 2 - looks more transactional than elemental, why connected to an 'event' rather than directly to the 'table'? | Sector Discussion |  | General |  |  |  | multivariate analysis | multivariate analysis | Action: Nick and Haydn to discuss and determine if changes are needed to the standards pre relase | Haydn |  | No further action required

## Full Data
NZAMS - Sector Feedback - Final Version
ID | Outcome | Standard | Volume | Feedback | Status Included, Excluded, Sector discussion, Noted: no action required | Final Comments for Publication | Section Reference in Final Version - per Contents page | Additional Work | Proposed Codelists / Attributes | Outcome fropm Workshops 1-3/5/2017 | Notes | Outcome from Workshops 23-24/5/2017 | Notes
1 | Included | Potable water | Vol 2 | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Completed with Metaconnect | No Specific Reference | No action
2 | Included | Potable water | Vol 2 | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Included | Completed with Metaconnect | No Specific Reference | No action
3 | Included | Potable water | Vol 2 | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Included | Completed with Metaconnect | No Specific Reference | No action
4 | Included | Buildings | Vol 2 | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Included | Completed with Metaconnect | No Specific Reference | No action
5 | Included | Stormwater | Vol 2 | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | Completed with Metaconnect | No Specific Reference | No action
6 | Included | Stormwater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
7 | Included | Wastewater | Vol 2 | Should be "coordinate reference system" as in ISO 19111 | Included | Standards are OGC spatial attribution compliant | Use of the Specification | No action
8 | Included | Wastewater | Vol 2 | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Included | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System | No action
9 | Included | Potable water | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | not required in this section, covered in later sections | Use of the Specification | No action
10 | Completed | Potable water | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
11 | Completed | Potable water | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
12 | Completed | Potable water | Vol 1 | or vertical datum | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
13 | Completed | Potable water | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | changed precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | Change made document updated
14 | Included | Buildings | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
15 | Completed | Buildings | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
16 | Included | Stormwater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Reviewed and Noted for Inclusion | Use of the Specification | No action
17 | Completed | Stormwater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
18 | Completed | Stormwater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | Change made document updated
19 | Completed | Stormwater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | Change made document updated
20 | Included | Wastewater | Vol 1 | Should be "coordinate reference system" as in ISO 19111 | Included | Updated in draft standards | Use of the Specification | No action
21 | Completed | Wastewater | Vol 1 | Should label this "Horizontal Coordinate System" to distinguish it from the vertical | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
22 | Completed | Wastewater | Vol 1 | Should label this "Vertical Datum" since datums can also be horizontal | Included | Updated in draft standards | 1.5 Deliverables | Change made document updated
23 | Completed | Wastewater | Vol 1 | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. | Included | Updated in draft standards | 2.1.2 Projections and Datums | Change made document updated
24 | Completed | Wastewater | Vol 1 | Update to NZVD2016 | Included | Updated in draft standards | Glossary | Change made document updated
25 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General | No action
26 | No Action Required | 3-Waters | Vol 1 & Vol 2 | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Noted: no action required | Reviewed and Noted only | General | No action
27 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference | No action
28 | Completed | 3-Waters | Vol 1 & Vol 2 | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | Included | The drafts have now had a full publishing edit | General | Change made document updated
29 | Awaiting Implementation Phase | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Noted: no action required | The adoption of extents of fields is determined by each organisation To be also reviewed during pilot implementation phase | General | No action
30 | No Action Required | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General | No action
31 | No Action Required | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General | No action
32 | No Action Required | 3-Waters | Vol 1 & Vol 2 | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | Noted: no action required | Future work is yet to be determined | General | No action
33 | Completed | 3-Waters | Vol 1 & Vol 2 | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | Included | The classification has been defined in the Standards. Modifications have been made to resolve inconsistencies | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
34 | Included | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | Included | The classification has been defined in the Standards Code Lists included | General | No action
35 | Included | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | Included | The classification has been defined in the Standards | General | No action
36 | Included | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | Included | Asset Classifications have been defined in the Standards. The Group classification is at a high level the asset classes have then been identified under the groups Code Lists included | General | No action
37 | No Action Required | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy | No action
38 | No Action Required | 3-Waters | Vol 1 & Vol 2 | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Noted: no action required | The adoption of extents of fields is determined by each organisation Each and every organisation can apply their specific requirements after the data is received. | General for Hierarchy | No action
39 | Excluded | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference | No action
40 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference | No action
41 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics | No action
42 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums | No action
44 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Included | Suggestion adopted. Change made documents updated | General | Change made document updated
45 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Noted: no action required | Organisations may map the full name into their systems from the Code lists supplied | General | No action
46 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Noted: no action required | Reviewed and Noted only | General | No action
47 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Included | Photographic Evidence is an optional attribute | General | change made document updated
48 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Sector Discussion | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General | New Code List proposed | Health & Safety Type | Refer to New attribute or Codelist tab | Modified 'Hlth_Sfty' from a free text field to a codelist To be modified in all the 3 Waters and BH documents
49 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Included | Suggestion adopted. Change made documents updated | General | Change made document updated
50 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | No action
51 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | No action
52 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | Included | Code lists included in standards | 2.3.3 Retaining Structure | No action
53 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Sector Discussion | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | No action
54 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves | More information required for a decision |  | Mark and Marty to discuss and come up with a reccomended outcome |  | Refer to New Attribute or Codelist tab | Changes made to all 3Waters documents Valve removed from codelist of Mechanical equipment Purpose - Attribute and Codelist already exists Valve table modified with new attributes and associated codelists Attribute - Valve Powered By Codelist - Valve Power Attibute - Valve Configuration Codelist - Valve Configuration
55 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Noted: no action required | These standards have not considered Treatment Plants | General | No action
56 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | Included | Code lists included in standards Pump has been removed from Mechanical Equipment as it is an asset class in its own right | General Equipment | Gauge input from next review |  | Gauge input from next review
57 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Refer to New attribute or Codelist tab |  | Refer to New Attribute or Codelist tab
58 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments | No action
59 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | Gauge input from next review |  | Gauge input from next review
60 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General | No action
61 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | Change made document updated
62 | Included | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | Change made document updated
63 | Completed | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA) | Refer to New attribute or Codelist tab | Created new attribute field and code list OMA To be included in all the 3 Waters documents
64 | No Action Required | 3-Waters | Vol 1 & Vol 2 | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | Noted: no action required | resolved in updated version | 2.5.1 Equipment | Change made document updated
65 | Completed | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option | Refer to New attribute or Codelist tab | Created new attribute field Rig_Flex To be included in all the 3 Waters documents
66 | Completed | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision |  |  |  | Refer to New attribute or Codelist tab | Created new attribute field and code list Testing Type To be included in all the 3 Waters documents
67 | Completed | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision |  |  |  | Closed | Duplicate see ID 67
68 | Included | Stormwater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | AddCCTV & Laser Profiling testing to code list testing type | General | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling | Refer to New attribute or Codelist tab
69 | Completed | Stormwater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Sector Discussion | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | New attribute proposed | Installer of Asset | Refer to New attribute or Codelist tab | Created new attributes for Installer, Installer Warranty, Manufacturer Warranty
70 | Completed | Stormwater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Sector Discussion | Reviewed and Noted for Inclusion | 2.3.4 Pipe | More information required for a decision |  | Refer to New attribute or Codelist tab | Added to new code list Test Type
71 | Included | Stormwater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | General | New Code List entry for Condition Assessment Type proposed | Deflection Test | Refer to New attribute or Codelist tab
72 | No Action Required | Stormwater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
73 | Completed | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation | Refer to New attribute or Codelist tab | Added to new code list Test Type
74 | Completed | Stormwater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Sector Discussion | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation | Refer to New attribute or Codelist tab | Added to new code list Test Type
75 | Included | Stormwater | Vol 1 | Deflection Test result | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | New Code List entry for Condition Assessment Type proposed | Compaction Test | Refer to New attribute or Codelist tab
76 | Completed | Stormwater | Vol 1 | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Refer to New attribute or Codelist tab | Created new attributes and associated codelists Frame Class Cover Class Seal Type To be included in all the 3 Waters documents | Closed | Cover Class changed to LID Class
77 | Completed | Stormwater | Vol 1 | Seal Access Safety | Sector Discussion | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber | New Code List & entries proposed | Health & Safety Type | Refer to New attribute or Codelist tab
78 | Completed | Stormwater | Vol 1 | Manufacturer Manufacturing Standard Third Party QA Accreditation | Sector Discussion | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion | Refer to New attribute or Codelist tab | Created new attributes Manufacturer Manufacturing Standard Third Party QA Accreditation The year of the standard is recorded as party of the Standard used To be included in all the 3 Waters documents
79 | Completed | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.4.4 Pipe | New attribute proposed | Rigid or Flexible as option | Refer to New attribute or Codelist tab
80 | Included | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling | Refer to New attribute or Codelist tab | Created attribute field "Observed" to enable recording of results To include in all the 3 Waters documents
81 | Completed | Stormwater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | Additional entries included in Code list Condition Assessment Type |  | Refer to New attribute or Codelist tab (same as ID68) | Create attribute field "Observation" to enable recording of results
82 | Included | Stormwater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling | Refer to New attribute or Codelist tab
83 | Completed | Stormwater | Vol 1 | Rigid material standard and QA Separate Flexible material standard and it's QA | Sector Discussion | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA | Refer to New attribute or Codelist tab | Created new attributes Rigid Materil Standard Rigid Material Accreditation Flexible Material Standard Flexible Material Quality Accreditation To be included in all the 3 Waters documents
84 | Included | Stormwater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test | Refer to New attribute or Codelist tab
85 | Completed | Stormwater | Vol 1 | Compaction strength per NZS4566.2 | Sector Discussion | More information required for a way forward | 2.4.4 Pipe | More information required for a decision |  | Change made document updated | Created attribute field "Observation" to enable recording of results To include in all the 3 Waters documents
86 | Completed | Stormwater | Vol 1 | Third Party QA for pipe material manufacturer | Sector Discussion | Third Party QA Accreditation to code lists | 2.4.4 Pipe | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list | Refer to New attribute or Codelist tab
87 | Included | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option | Refer to New attribute or Codelist tab
88 | Included | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing | Refer to New attribute or Codelist tab
89 | Included | Wastewater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Included | Add Deflection Testing to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing | Refer to New attribute or Codelist tab
90 | Included | Wastewater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling | Refer to New attribute or Codelist tab
91 | Included | Wastewater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments | New attribute proposed | Installer of Asset | Refer to New attribute or Codelist tab
92 | Included | Wastewater | Vol 1 | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling | Refer to New attribute or Codelist tab
93 | Included | Wastewater | Vol 1 | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. | Included | Add Table | 1.7 Heirarchy | Create entries Desktop Visual cctv laser etc |  | Refer to New attribute or Codelist tab
94 | No Action Required | Wastewater | Vol 1 | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes | No action
95 | Included | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation | Refer to New attribute or Codelist tab
96 | Included | Wastewater | Vol 1 | Flexible Pipe: Compaction Tests Deflection Test post installation | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation | Refer to New attribute or Codelist tab
97 | Completed | Wastewater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option | Refer to New attribute or Codelist tab
98 | Included | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling | Refer to New attribute or Codelist tab
99 | Completed | Wastewater | Vol 1 | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test | Sector Discussion | More information is required to inform a way forward | 2.3.4 Pipe | More information required for a decision |  | Closed
100 | Included | Wastewater | Vol 1 | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling | Refer to New attribute or Codelist tab
101 | Included | Wastewater | Vol 1 | Foundation strength pre-install Compaction strength per NZS4566.2 | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | New Code List entry for Condition Assessment Type | Compaction Test per NZ4566.2 Foundation strength pre-install | Refer to New attribute or Codelist tab
102 | Completed | Wastewater | Vol 1 | Compaction strength per NZS4566.2 or NZS3725 | Sector Discussion | More information required for a way forward | 2.3.4 Pipe | More information required for a decision |  | Closed
103 | Included | Wastewater | Vol 1 | Third Party QA for pipe material manufacturer | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion | Refer to New attribute or Codelist tab
104 | No Action Required | Stormwater | Vol 1 | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure | More information required for a decision |  | No further action | Morphum Environmental Ltd provided this feedback. Auckland Stormwater have been heavily involved in the standard from Day 1, and the compromises made made have been agreed to by all parties.
105 | Completed | Stormwater | Vol 1 | Spillway should be its own Asset Class | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure | More information required for a decision |  | Closed | Discussed during the May 1-3 workshops Determined that this can be addressed by the asset owner as a post process
106 | Completed | Stormwater | Vol 1 | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles | More information required for a decision |  | Close, refer to Roading Standards Gissa to follow up on Giabon |  | No further action required | Watercourse - out of scope Forebay bund - included as Embankment type Bridge - part of Roading Maintenance track - - part of Roading Fence - part of Roading Viewing platform - part of Roading Gabion basket- part of Roading (retaining wall type) Roading standard refer to TAGG
107 | Completed | Stormwater | Vol 1 | Source for what? This should have more detail. | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | Change made document updated
108 | Completed | Stormwater | Vol 1 | Does this include forebay bunds and pond banks associated with ponds? | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks | Refer to New attribute or Codelist tab | Added Forebay Bund and Pond Bank to code list EMBANKMENT TYPE Weir spelling corrected Carried out post publication of 23 MAY documents
109 | No Action Required | Stormwater | Vol 1 | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure | More information required for a decision |  | Closed |  | Closed
110 | Included | Stormwater | Vol 1 | Bathymetry Attribute? | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | Haydn suggest this is excluded as I think it can be sourced from LINZ |  | Out of scope
111 | No Action Required | Buildings | Vol 1 | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable | Noted: no action required | Reviewed and Noted only | General | No action
112 | No Action Required | Buildings | Vol 1 | The Hierarchy table works well | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy | No action
113 | Awaiting Implementation Phase | Buildings | Vol 1 | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. | Sector Discussion | Reviewed and Noted only for discussion | General | No action |  | To be resolved during implementation phase
114 | No Action Required | Buildings | Vol 1 | Complex requirement for such a large property portfolio | Noted: no action required | Reviewed and Noted only | General | No action
115 | No Action Required | Buildings | Vol 1 | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles | No action
116 | No Action Required | Buildings | Vol 1 | This is a huge task for as constructed / as built for a large portfolio | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
117 | No Action Required | Buildings | Vol 1 | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | Reviewed and Noted only | General | No action
118 | No Action Required | Buildings | Vol 1 | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General | No action
119 | Included | Buildings | Vol 1 | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | No action
120 | No Action Required | Buildings | Vol 1 | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes | More information required for a decision |  | Closed
121 | No Action Required | Buildings | Vol 1 | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) | Noted: no action required | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General | No action
122 | No Action Required | Buildings | Vol 1 | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
123 | No Action Required | Buildings | Vol 1 | V_Proc  what is this and what is it to relate to? | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes | No action
124 | Included | Buildings | Vol 1 | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? | Included | Tables will be referenced in Final Versions | General | No action
125 | Completed | Buildings | Vol 1 | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attribute in Project | Closed
126 | Completed | Buildings | Vol 1 | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof | More information required for a decision |  | GISSA to review wording to ensure clarity | Reviewed wording no change | Closed
127 | Completed | Buildings | Vol 1 | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision |  | GISSA to review wording to ensure clarity | Reviewed wording no change | Closed
128 | Completed | Buildings | Vol 1 | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor | More information required for a decision |  | GISSA to review wording to ensure clarity | The schemas are designed for recording of data at time of construction. | Closed
129 | No Action Required | Buildings | Vol 1 | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone | Noted: no action required | This detail is to be provided at the time it was built not at time of capture This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint | No action
130 | No Action Required | Buildings | Vol 1 | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
131 | Completed | Buildings | Vol 1 | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint | Change made document updated |  | External data set - out of scope
132 | No Action Required | Buildings | Vol 1 | Graffiti  irrelevant | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint | No action
133 | No Action Required | Buildings | Vol 1 | Flood  applicable only in related areas, and this information is on local council records | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint | No action
134 | No Action Required | Buildings | Vol 1 | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint | No action
135 | No Action Required | Buildings | Vol 1 | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint | No action
136 | No Action Required | Buildings | Vol 1 | Design life how is this applied to existing property | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint | No action
137 | No Action Required | Buildings | Vol 1 | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling | No action
138 | No Action Required | Buildings | Vol 1 |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
139 | No Action Required | Buildings | Vol 1 | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling | No action
140 | No Action Required | Buildings | Vol 1 | Finish  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
141 | No Action Required | Buildings | Vol 1 | Finish condition assessment, condition and repairs  ✓ The rest is superfluous | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
142 | No Action Required | Buildings | Vol 1 | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satisfy both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling | No action
143 | No Action Required | Buildings | Vol 1 | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
144 | No Action Required | Buildings | Vol 1 | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
145 | No Action Required | Buildings | Vol 1 | Design life  If new = Ok | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
146 | No Action Required | Buildings | Vol 1 | Cost  Not needed? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
147 | No Action Required | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
148 | No Action Required | Buildings | Vol 1 | Too much detail required for ceilings. Condition, material, surface finish = Yes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling | No action
149 | No Action Required | Buildings | Vol 1 | Risk, Resilience, and Financial performance  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
150 | No Action Required | Buildings | Vol 1 | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
151 | Completed | Buildings | Vol 1 | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling | More information required for a decision |  | GISSA to review wording to make more expilicit |  | Closed
152 | No Action Required | Buildings | Vol 1 | Smoke_Barr  Smoke relevant to multiunit development only. | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
153 | Completed | Buildings | Vol 1 | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling | Change made document updated |  | Closed | Implementation to identify optional/mandatory split of these fields
154 | No Action Required | Buildings | Vol 1 | Des_Life - ? | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
155 | No Action Required | Buildings | Vol 1 | Cost ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
156 | No Action Required | Buildings | Vol 1 | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
157 | No Action Required | Buildings | Vol 1 | Whole page  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling | No action
158 | No Action Required | Buildings | Vol 1 | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor | No action
159 | No Action Required | Buildings | Vol 1 | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
160 | No Action Required | Buildings | Vol 1 | Live load rating of floor à too difficult to define | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
161 | No Action Required | Buildings | Vol 1 | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
162 | No Action Required | Buildings | Vol 1 | Repairs and Maintenance à what’s the need for this? | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema | No action
163 | No Action Required | Buildings | Vol 1 | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference | No action
164 | No Action Required | Buildings | Vol 1 | First 5 rows à Very detailed for residential use. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
165 | No Action Required | Buildings | Vol 1 | Bracing is as per ceiling notes | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
166 | Completed | Buildings | Vol 1 | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision |  | Closed | Fields are optional
167 | Completed | Buildings | Vol 1 | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor | More information required for a decision |  | Closed | Cost is part of asset management requirements
168 | No Action Required | Buildings | Vol 1 | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
169 | No Action Required | Buildings | Vol 1 | Third row à Maybe | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
170 | No Action Required | Buildings | Vol 1 | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
171 | No Action Required | Buildings | Vol 1 | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor | No action
172 | No Action Required | Buildings | Vol 1 | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
173 | No Action Required | Buildings | Vol 1 | Multi storey application only. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
174 | No Action Required | Buildings | Vol 1 | - Multi storey application only. Too much detail required. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
175 | No Action Required | Buildings | Vol 1 | Last 5 yellow rows à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
176 | No Action Required | Buildings | Vol 1 | - 2nd row à ? Building Code complaint for new works. Unknown for much existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor | No action
177 | No Action Required | Buildings | Vol 1 | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
178 | No Action Required | Buildings | Vol 1 | Thermal barrier à ? Floor insulation is all that is relevant in residential. | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
179 | No Action Required | Buildings | Vol 1 | All pages à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
180 | No Action Required | Buildings | Vol 1 | Whole page à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
181 | No Action Required | Buildings | Vol 1 | Acoustic row, content  maybe Cost  X Rest of page  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
182 | No Action Required | Buildings | Vol 1 | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor | No action
183 | No Action Required | Buildings | Vol 1 | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
184 | No Action Required | Buildings | Vol 1 | Whole page  undefinable in existing housing. | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation | No action
185 | No Action Required | Buildings | Vol 1 | Vents  ✓ Membrane rows  Define what membrane? | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation | No action
186 | No Action Required | Buildings | Vol 1 | Foundation area, content à ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation | No action
187 | No Action Required | Buildings | Vol 1 | à See previous foundation notes | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision |  | Closed
188 | No Action Required | Buildings | Vol 1 | All pages à ✕ | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation | More information required for a decision |  | Closed
189 | No Action Required | Buildings | Vol 1 | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof | No action
190 | No Action Required | Buildings | Vol 1 | Load wind/fix  Not known in existing stock | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof | No action
191 | No Action Required | Buildings | Vol 1 | Frame_Tr  not always identifiable Frame_ Sp  why? | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
192 | No Action Required | Buildings | Vol 1 | Cost row à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
193 | No Action Required | Buildings | Vol 1 | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
194 | Completed | Buildings | Vol 1 | Last 3 rows  Is this needed and how is it defined? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision |  | Closed | H&S, Photos, Comments - these are all optional -= close
195 | No Action Required | Buildings | Vol 1 | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action |  |  | 194 + Financial Performance + service performance are optional, close
196 | No Action Required | Buildings | Vol 1 | First row, QA Validation  N/A needs to be applied here | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof | No action
197 | No Action Required | Buildings | Vol 1 | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
198 | Completed | Buildings | Vol 1 | Last 5 rows  as per previous notes | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision |  | Closed | 194 + Financial Performance + service performance are optional, close
199 | No Action Required | Buildings | Vol 1 | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof | No action
200 | No Action Required | Buildings | Vol 1 | Whole page  ✓ apart from: Cost row  ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
201 | No Action Required | Buildings | Vol 1 | First 3 rows  ? | Sector Discussion | Please specify the rows. | 2.4.4 Roof | More information required for a decision |  | Closed | Optional
202 | No Action Required | Buildings | Vol 1 | Last row, QA validation à Critical | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof | More information required for a decision |  |  |  | Closed
203 | No Action Required | Buildings | Vol 1 | Risk  ✓ Resil, Des_Perf  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
204 | No Action Required | Buildings | Vol 1 | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
205 | No Action Required | Buildings | Vol 1 | Whole page à ✓ Apart from Cost row à ? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
206 | No Action Required | Buildings | Vol 1 | First 3 rows à? | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
207 | No Action Required | Buildings | Vol 1 | critically, QA Validation à Critical | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
208 | No Action Required | Buildings | Vol 1 | All 3 rows  ? Row 3  Too much detail | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
209 | No Action Required | Buildings | Vol 1 | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
210 | No Action Required | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
211 | No Action Required | Buildings | Vol 1 | All 4 rows  ✕, ?, ?, ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
212 | No Action Required | Buildings | Vol 1 | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
213 | Included | Buildings | Vol 1 | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | No action
214 | No Action Required | Buildings | Vol 1 | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
215 | No Action Required | Buildings | Vol 1 | Whole page à✕. Risk – could relate to a water risks | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
216 | No Action Required | Buildings | Vol 1 | Whole page à ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
217 | No Action Required | Buildings | Vol 1 | Classifications, Masterpec, Enclosure à not sure what this is representing? | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof | No action
218 | No Action Required | Buildings | Vol 1 | Ins-Type, R_Value à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
219 | No Action Required | Buildings | Vol 1 | Whole page  ✓ Insulation installer and warranty  maybe | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
220 | No Action Required | Buildings | Vol 1 | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
221 | No Action Required | Buildings | Vol 1 | Whole pink pages/part  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof | No action
222 | No Action Required | Buildings | Vol 1 | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls | No action
223 | No Action Required | Buildings | Vol 1 | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
224 | No Action Required | Buildings | Vol 1 | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
225 | No Action Required | Buildings | Vol 1 | Grout and Wall Structure Joint  ✕ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
226 | No Action Required | Buildings | Vol 1 | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
227 | No Action Required | Buildings | Vol 1 | Condition  ✓ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
228 | No Action Required | Buildings | Vol 1 | Structure, Bracing à As per floor and roof bracing | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
229 | No Action Required | Buildings | Vol 1 | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
230 | No Action Required | Buildings | Vol 1 | Wall, Design Life à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
231 | No Action Required | Buildings | Vol 1 | Condition  ✓ Cost row  ✕ Repairs  ? | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
232 | No Action Required | Buildings | Vol 1 | Fire barrier à Multiunit. May not be known on existing stock | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
233 | No Action Required | Buildings | Vol 1 | Orange à ✓ | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls | No action
234 | No Action Required | Buildings | Vol 1 | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls | No action
235 | No Action Required | Buildings | Vol 1 |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor | No action
236 | No Action Required | Buildings | Vol 1 | Whole page à why would we use this information? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
237 | No Action Required | Buildings | Vol 1 | Acoustic and Thermal rating à Not used. Where applicable? | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor | No action
238 | No Action Required | Buildings | Vol 1 | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor | No action
239 | No Action Required | Buildings | Vol 1 | à Why / how would we use this? Too much information required. | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs | No action
240 | No Action Required | Buildings | Vol 1 | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs | No action
241 | No Action Required | Buildings | Vol 1 | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
242 | No Action Required | Buildings | Vol 1 | Pages  ✕ | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs | No action
243 | No Action Required | Buildings | Vol 1 | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision |  | Closed | Optional
244 | Completed | Buildings | Vol 1 | Framed and Frame material à not defined in window anatomy page 149 | Sector Discussion | Update diagram on p149 | 2.5.3 Windows | Modify Diagram |  | Change made document updated
245 | No Action Required | Buildings | Vol 1 | Height of windows in mm à what value? | Noted: no action required | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | No action
246 | No Action Required | Buildings | Vol 1 | Condition  ✓ Width  why needed? | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows | More information required for a decision |  | Closed
247 | No Action Required | Buildings | Vol 1 | Manufacturer, warranty, installation date, installer àUnknown on existing | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
248 | No Action Required | Buildings | Vol 1 | Design life à How to define? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
249 | No Action Required | Buildings | Vol 1 | Repairs à ? | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
250 | No Action Required | Buildings | Vol 1 | Page à✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
251 | No Action Required | Buildings | Vol 1 | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows | No action
252 | No Action Required | Buildings | Vol 1 | Hardware à Locks, Yes. Lever/knobs maybe. | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
253 | No Action Required | Buildings | Vol 1 | Whole Column Name – Full is circled à Not always known on existing. Why needed? | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows | No action
254 | No Action Required | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows | No action
255 | No Action Required | Buildings | Vol 1 | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | No action
256 | No Action Required | Buildings | Vol 1 | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
257 | No Action Required | Buildings | Vol 1 | Services, pink section àmore commercial application. | Noted: no action required | Reviewed and Noted only | 2.6 Utilities | No action
258 | No Action Required | Buildings | Vol 1 | à No! How is this captured realistically and why? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components | No action
259 | No Action Required | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
260 | No Action Required | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
261 | No Action Required | Buildings | Vol 1 | Not applicable to Residential | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC | No action
262 | No Action Required | Buildings | Vol 1 | à Would we use this at a per item attribute? | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
263 | No Action Required | Buildings | Vol 1 | Type à ✓ Last row, content à NA | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings | No action
264 | No Action Required | Buildings | Vol 1 | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
265 | No Action Required | Buildings | Vol 1 | àToo difficult and unnecessary info | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework | No action
266 | No Action Required | Buildings | Vol 1 | à Stove have heater fans | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment | No action
267 | No Action Required | Buildings | Vol 1 | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment | No action
268 | No Action Required | Buildings | Vol 1 | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment | No action
269 | No Action Required | Buildings | Vol 1 | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) | No action
270 | No Action Required | Buildings | Vol 1 | Pink section  Not sure how much of this is required/useful | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) | No action
271 | No Action Required | Buildings | Vol 1 | Blue section - ✓ | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings | No action
272 | Included | Buildings | Vol 1 | Asset type à ✓ Kitchen Vanities in contents | Included | Add to codelist | 2.7.4 Fixtures & Fittings | New Code List entry for Fittings Type proposed | Kitchen Vanities | Refer to New attribute or Codelist tab
273 | No Action Required | Buildings | Vol 1 | Length, Height, Width à Why? | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings | More information required for a decision |  | Closed
274 | No Action Required | Buildings | Vol 1 | Whole page à Doubt this would be known | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings | No action
275 | No Action Required | Buildings | Vol 1 | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) | No action
276 | No Action Required | Buildings | Vol 1 | à Covered in Building WOF. *Specialist area = consultant needed = $$ | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components | No action
277 | No Action Required | Buildings | Vol 1 | àSpecialists information and only applicable to multi-unit/storey complexes. | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts | No action
278 | No Action Required | Buildings | Vol 1 | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. | Noted: no action required | Reviewed and Noted only | 2.7.9 Security | No action
279 | No Action Required | Buildings | Vol 1 | à Not so useful in residential and difficult to maintain/update. | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage | No action
280 | No Action Required | Buildings | Vol 1 | à Not really applicable to existing housing. Maybe some use in multi-unit development. | Noted: no action required | Reviewed and Noted only | 2.8.1 Space | No action
281 | No Action Required | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
282 | Included | Buildings | Vol 1 | à ✕ | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | No action
283 | No Action Required | Buildings | Vol 1 | à ✕ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
284 | No Action Required | Buildings | Vol 1 | Material à ✓ | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data | No action
285 | No Action Required | Buildings | Vol 1 | Pipe type à ✕ | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data | No action
286 | No Action Required | Buildings | Vol 1 | Water type à ? | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data | No action
287 | No Action Required | Buildings | Vol 2 | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference | Change made document updated
288 | Completed | Buildings | Vol 2 | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Included | Edited to make clearer | No Specific Reference | Change made document updated
289 | Completed | Buildings | Vol 2 | This document excludes industrial buildings and Ancillary building’s  provide examples | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
290 | Completed | Buildings | Vol 2 | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
291 | Completed | Buildings | Vol 2 | Added Laundry to Outbuildings, included in the Residential standard | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | Change made document updated
292 | Included | Buildings | Vol 2 | The bullet points à are they attributes or measures? | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | Haydn |  | Closed
293 | Excluded | Buildings | Vol 2 | What is Boolean data type? | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type | Change made document updated
294 | Completed | Buildings | Vol 2 | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | Change made document updated
295 | Included | Buildings | Vol 2 | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | no action
296 | No Action Required | Buildings | Vol 2 | The third and fourth suite of analytics à seems very granular? | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
297 | No Action Required | Buildings | Vol 2 | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Noted: no action required | References are being considerd | No Specific Reference | No action
298 | Included | Buildings | Vol 2 | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | Haydn |  | Closed
299 | No Action Required | Buildings | Vol 2 | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference | No action
300 | No Action Required | Buildings | Vol 2 | Table 4. à unclear what this actually shows? | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas | No action
301 | Included | Buildings | Vol 2 | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | No action
302 | Included | Buildings | Vol 2 | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Included | Updated in draft Standards | Code List 16: Condition Rating | No action
303 | No Action Required | Buildings | Vol 2 | Operations definition à What does this mean? Is this routine/preventative maintenance? | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
304 | Included | Buildings | Vol 2 | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
305 | Included | Buildings | Vol 2 | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
306 | Awaiting Implementation Phase | Buildings | Vol 2 | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Sector Discussion | Mandatory / Optimal and Optional will be discussed | No Specific Reference | No action |  |  |  | Closed | To be resolved during implementation phase
307 | No Action Required | Buildings | Vol 2 | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) | No action
308 | No Action Required | Buildings | Vol 2 | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
309 | No Action Required | Buildings | Vol 2 | 1st bullet point à E.g. roof? Fire alarms? | Noted: no action required | Can be as granular as needed. | No Specific Reference | No action
310 | Included | Buildings | Vol 2 | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Included | Updated in Draft Standards | No Specific Reference | Haydn |  | Change made document updated
311 | No Action Required | Buildings | Vol 2 | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference | No action
312 | No Action Required | Buildings | Vol 2 | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
313 | Included | Buildings | Vol 2 | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | No action
314 | No Action Required | Buildings | Vol 2 | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
315 | No Action Required | Buildings | Vol 2 |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating | No action
316 | No Action Required | Buildings | Vol 2 | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes | No action
317 | No Action Required | Buildings | Vol 2 | Code G, Malicious damage à Does this include tenant damage? | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
318 | No Action Required | Buildings | Vol 2 | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating | No action
319 | No Action Required | Buildings | Vol 2 |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating | No action
320 | No Action Required | Buildings | Vol 2 |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference | Change made document updated
321 | Completed | Buildings | Vol 2 |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
322 | No Action Required | Buildings | Vol 2 |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema | No action
323 | No Action Required | Buildings | Vol 2 | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference | No action
324 | No Action Required | Buildings | Vol 2 | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Noted: no action required | No action required. Understood. | No Specific Reference | No action
325 | Included | Buildings | Vol 2 | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | Haydn |  | Change made document updated
326 | No Action Required | Buildings | Vol 2 | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element | To discuss with technical Working Groups |  | Closed
327 | No Action Required | Buildings | Vol 2 | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Noted: no action required | The attribute is optional. | No Specific Reference | No action
328 | No Action Required | Buildings | Vol 2 | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference | No action
329 | No Action Required | Buildings | Vol 2 | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference | No action
330 | No Action Required | Buildings | Vol 2 | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Noted: no action required | These are at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists | No action
331 | Completed | Potable water | Vol 1 | Add USB memory sticks/hard drives to this list. | Included | Changed in all documents | 1.5 Deliverables | Change made document updated
332 | No Action Required | Potable water | Vol 1 | Question: Are there requirements for developers to retain information after transmission? | Noted: no action required | We see this as something for the developer to make the call if they retain a copy or not. | 1.5 Deliverables | No action
333 | Excluded | Potable water | Vol 1 | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. | Excluded | Keeping current practice. | 2.1.5 Attribute Data Fields | No action |  |  | Discussed during the May 1-3 workshops Noted no further discussion or action required
334 | No Action Required | Potable water | Vol 1 | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. | 2.1.10 Common Attributes | No action
335 | Completed | Potable water | Vol 1 | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters | 2.2.1 Area of Work Extent | More information required for a decision |  | Closed | Fine to use locally, not to be included in standards so that they remain system agnostic
336 | Completed | Potable water | Vol 1 | For circular assets, should length and width both be populated and be the same (diameter)? | Included | For circular assets, length is not required and will be made conditional | 2.3.1 Containment Structure | Change made document updated
337 | Completed | Potable water | Vol 1 | Rename to Length Metres for consistency | Included | Changed all instances to length metres and length millimetres as appropriate | 2.3.1 Containment Structure | Change made document updated
338 | No Action Required | Potable water | Vol 1 | Overflow = OS? What does OS stand for? Should this be OF? | Noted: no action required | This term was agreed to by the TWG, retained | 2.3.1 Containment Structure | No action |  | No further action
339 | Completed | Potable water | Vol 1 | Earlier wells were requested to be polygon type. Is the point supplementary? | Included | Typo corrected, is to be polygon. | 2.3.4 Well | Change made document updated
340 | Completed | Potable water | Vol 1 | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station | More information required for a decision |  | Closed | Discussed during the May 1-3 workshops Determined that this is a post processing exercise by each organisation as required
341 | Completed | Potable water | Vol 1 | I believe this table and its attribute names have become mis-aligned. | Sector Discussion | Looks OK, need more information | 2.5.1 Equipment | More information required for a decision |  | Closed
342 | No Action Required | Wastewater | Vol 1 | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe | No action
343 | No Action Required | Wastewater | Vol 1 | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. | Noted: no action required | The standards are recording as-constructed | 1.8 Theme Structure | No action
344 | No Action Required | Wastewater | Vol 1 | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? | Noted: no action required | Each organisation will decide how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure | No action
345 | No Action Required | Wastewater | Vol 1 | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets | No action
346 | No Action Required | Wastewater | Vol 1 | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets | No action
347 | Completed | Wastewater | Vol 1 | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent | More information required for a decision |  | Closed | Covered at a Project level
348 | No Action Required | Wastewater | Vol 1 | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent | No action
349 | Completed | Wastewater | Vol 1 | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | Change made document updated |  | Change made document updated
350 | No Action Required | Wastewater | Vol 1 | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
351 | No Action Required | Wastewater | Vol 1 | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? | Noted: no action required | see ID 349 | 2.3.1 Access Chamber | No action
352 | No Action Required | Wastewater | Vol 1 | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber | No action
353 | No Action Required | Wastewater | Vol 1 | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. | 2.3.3 Fitting | No action
354 | No Action Required | Wastewater | Vol 1 | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting | No action
355 | Completed | Wastewater | Vol 1 | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting | More information required for a decision |  | Closed | There are a number of assets featured in this comment. Each asset class will be recorded according to the standard therefore resulting in multuiple entries Can utilise Support Structure class for protection
356 | Completed | Wastewater | Vol 1 | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. | Sector Discussion | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe | More information required for a decision |  | Closed
357 | Completed | Wastewater | Vol 1 | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe | More information required for a decision |  |  |  | Refer to New Attribute or Codelist tab | Node definition also modified
358 | Included | Wastewater | Vol 1 | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. | Included | Precision is defined in the standards | 2.3.4 Pipe | No action
359 | Completed | Wastewater | Vol 1 | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision |  |  |  | Closed | In this schema, all activities undertaken on an asset are categorised into four broad ‘Event Types’ as defined below, these are in the right place
360 | No Action Required | Wastewater | Vol 1 | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe | No action
361 | No Action Required | Wastewater | Vol 1 | These changes should be coded into the pipe geometry, not as separate notes about the pipe. | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe | More information required for a decision |  |  |  | Closed
362 | Completed | Wastewater | Vol 1 | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | Change made document updated
363 | No Action Required | Wastewater | Vol 1 | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe | More information required for a decision |  |  |  | Closed
364 | No Action Required | Wastewater | Vol 1 | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe | No action
365 | No Action Required | Wastewater | Vol 1 | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. | Noted: no action required | Reviewed and Noted only | General | No action
366 | Included | Wastewater | Vol 1 | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | No action
367 | Completed | Wastewater | Vol 1 | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe | More information required for a decision |  | Closed | Removed attribute 'Soil Type' from Pipes Table Removed from all 3 Waters documents
368 | Included | Wastewater | Vol 1 | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? | Included | The intent of the schema is to record what has been contructed at practical completion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | No action
369 | Completed | Wastewater | Vol 1 | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe | More information required for a decision |  | Closed | The schema incorporates conditional fields to use for this scenario
370 | Completed | Wastewater | Vol 1 | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General | More information required for a decision |  | Closed
371 | Awaiting Implementation Phase | Stormwater | Vol 1 & Vol 2 | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General | More information required for a decision |  |  |  | Closed | The mapping between standards will need to be completed post release (as part of implementation)
372 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | What are the timeframes for this being adopted as mandatory? | Noted: no action required | Business Case. | General | No action
373 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Will there be a further round of submissions / comments? | Noted: no action required | Yes. Seminars in November. | N/A | No action
374 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 & Vol 2 | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Included | Mandatory, Optimal, Optional will be discussed with the sectors and addressed during the pilot implementation phase | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
375 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General | No action
376 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference | Sector discussion |  |  |  | Closed
377 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Noted: no action required | Treatment is not included | No Specific Reference | No action
378 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | Included | Asset Classifications have been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | Change made document updated
379 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | Noted: no action required | Included in Instruments | Instruments | No action
380 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | Noted: no action required | Separate sections of data cohorts | General | No action
381 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | Sector Discussion | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments | More information required for a decision |  |  |  | Closed | New code of practice to be released in a few weeks - Noel to forward to George when it comes out. To be completed before release
382 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | Included | Statement noted. To be actioned. | General | Change made document updated
383 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well | No action |  | No further action | Wells and bores can be created as separarte asset types by each organisation as required | Closed
384 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | Included | Suggestion adopted Standards will be updated | 1.5 Deliverables | Change made document updated
385 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 & Vol 2 | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Sector Discussion | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | More information required for a decision |  | Closed | To be addressed as part of implementation phase |  | To be resolved during implementation
386 | No Action Required | Wastewater | Vol 1 | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. | Noted: no action required | Reviewed and Noted only | General | No action
387 | No Action Required | Wastewater | Vol 1 | a standardised approach to the collation of data relating to As Built (As Constructed) asset information | Noted: no action required | Reviewed and Noted only | Abstract | No action
388 | Included | Wastewater | Vol 1 | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. | Included | Will consdider for final edit - happy to add in. | Executive Summary | Haydn |  |  |  | Closed | changes made document updated
389 | Completed | Potable water | Vol 1 | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. | Sector Discussion | Need recommended maximum attachment size | 1.5 Deliverables | More information required for a decision |  | Closed | Change made document updated
390 | No Action Required | Potable water | Vol 1 | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. | 2.1.1 Accuracy Requirements for Locating Assets | No action
391 | Completed | Potable water | Vol 1 | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. | Included | picked up previously | 2.1.2 Projections and Datums | Change made document updated
392 | No Action Required | Potable water | Vol 1 | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. | Noted: no action required | agreed, but per pipe section, there is a from-node and a to-node, one of each. | 2.4.4 Node | No action
393 | No Action Required | Potable water | Vol 1 | We split pipes when there is a valve or hydrant on them. While other councils may not | Noted: no action required | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. | 2.4.5 Pipe | No action
394 | Completed | Potable water | Vol 1 | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. | Sector Discussion | need examples | 2.4.5 Pipe | More information required for a decision |  |  |  | Closed | Modification in description to indicate primary flow
395 | Included | Potable water | Vol 1 | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | No action
396 | No Action Required | Potable water | Vol 1 | A lot of the attributes seem to be duplicated | Noted: no action required | attributes are all different | 2.5.2 Pump | No action
397 | Included | Potable water | Vol 1 | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. | Included | agreed, diagram will be corrected | 2.7.1 Instruments | No action
398 | Completed | 3-Waters | Vol 1 & Vol 2 | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | Included | Updated | General | Change made document updated
399 | Completed | 3-Waters | Vol 1 & Vol 2 | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | Included | Updated | General | Change made document updated
400 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General | No action
401 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Noted: no action required | This is a metadata standard not asset management standards. | General | No action
402 | Completed | 3-Waters | Vol 1 & Vol 2 | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Included | Updated | General | Change made document updated |  | Change made document updated
403 | No Action Required | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | Noted: no action required | These are different in some cases / in others they are not, not the same definitions across sectors | General | No action
404 | No Action Required | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | Noted: no action required | Updated and acknowledge that this will be upto the individual organisation to address | 1.5 Deliverables | No action
405 | No Action Required | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | No action
406 | No Action Required | 3-Waters | Vol 1 & Vol 2 | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | Noted: no action required | References to be removed. | No Specific Reference | No action
407 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Noted: no action required | Treatment facilities are not included as part of these standards | No Specific Reference | No action
408 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Noted: no action required | Out of scope. However resourse consents maybe recorded against the specifc works for each project. | No Specific Reference | No action
409 | Excluded | 3-Waters | Vol 1 & Vol 2 | Content: • Land – no parameters are set for the recoding of land information. | Excluded | Out of scope. | No Specific Reference | No action
410 | Included | 3-Waters | Vol 1 & Vol 2 | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | No action
411 | Included | 3-Waters | Vol 1 & Vol 2 | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | No action
412 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Noted: no action required | Detailed in business case only | No Specific Reference | No action
413 | Awaiting Implementation Phase | 3-Waters | Vol 1 & Vol 2 | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Noted: no action required | Applies to all assets. Mandatory and optional fields to be determined during implementation. The benefits to costs covered in business case. | General | No action
414 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Noted: no action required | Covered in business case. | General | No action
415 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Noted: no action required | Covered in business case. | General | No action
416 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General | No action
417 | Awaiting Implementation Phase | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | Noted: no action required | Noted Will be further addressed during the pilot implementation phase | General | No action
418 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | Noted: no action required | This is not within the scope of these standards | General | No action
419 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | Noted: no action required | This is not within the scope of these standards | General | No action
420 | Included | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | No action
421 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Closed
422 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Noted: no action required | Included in the draft Standards | General | No action
424 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums | No action
425 | Completed | 3-Waters | Vol 1 & Vol 2 | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Included | Included in the draft Standards | 2.1.2 Projections and Datums | Change made document updated |  | Change made document updated
426 | Included | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Included | Included in the draft Standards Asset categories included as guidance for each organisation | General | No action
427 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure | No action
428 | Included | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | Included | Included in the draft Standards | General | No action
429 | Included | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Included | Included in the draft standards | General | No action
430 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General | No action
431 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference | No action
432 | Included | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Included | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General | No action
433 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes | No action
434 | Completed | 3-Waters | Vol 1 & Vol 2 | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) | General for Pipes | More information required for a decision |  | External data set - out of scope | These are other data sets (layers) applied to any analytic and out of scope - per earlier discussions
435 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings | No action
436 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General | No action
437 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes | No action
438 | Completed | 3-Waters | Vol 1 & Vol 2 | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | Sector Discussion | More information is required to inform a way forward | General for Nodes | More information required for a decision |  | Closed
439 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure | No action
440 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General | No action
441 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General | No action
442 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure | No action
443 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles | No action
444 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW | No action
445 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | Noted: no action required | Data collection is out of scope from these standards | General | No action
446 | Included | 3-Waters | Vol 1 & Vol 2 | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference |  |  |  |  | Closed
447 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node | No action
448 | Excluded | 3-Waters | Vol 1 & Vol 2 | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Excluded | Junctions / end points are not assets. | General | No action
449 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Noted: no action required | Junctions / end points are not assets. | No Specific Reference | No action
450 | Completed | 3-Waters | Vol 1 & Vol 2 | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  |  |  | Closed | Action: - there is the need to be able to capture the 3 diameters. One of the diameters is needed to be populated, but it doesn't matter which one it is.
451 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | Noted: no action required | The ID proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes | No action
452 | Completed | 3-Waters | Vol 1 & Vol 2 | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | Included | Included in the draft standards Code lists have been supplied | General | Change made document updated |  | Change made document updated
453 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Noted: no action required | Action on volume 1 and business case. The definition of a node has been reviewed and clarified | General | No action
454 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Noted: no action required | Statement noted. | General | No action
455 | No Action Required | 3-Waters | Vol 1 & Vol 2 | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Noted: no action required | Statement noted. Data transfer is not in scope. | No Specific Reference | No action
456 | No Action Required | 3-Waters | Vol 1 & Vol 2 | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference | No action
457 | Awaiting Implementation Phase | 3-Waters | Vol 1 & Vol 2 | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | Noted: no action required | 1. Completed 2. Further information required from respondent. Codelists are now included 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General | No action
458 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | Noted: no action required | Statement noted. Consideration for Volume 1. | General | No action
459 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | Noted: no action required | Statement noted. No action required. | General | No action
460 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | Noted: no action required | Statement noted. No action required. | General | No action
461 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | Noted: no action required | Statement noted. No action required. | General | No action
462 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | Noted: no action required | Business case. | General | No action
463 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | Noted: no action required | Statement noted. | General | No action
464 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
465 | Included | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Included | These inconsistencies have been actioned in the draft standards | General | No action
466 | Included | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | These inconsistencies have been actioned in the draft standards | General | No action
467 | Completed | 3-Waters | Vol 1 & Vol 2 | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | Sector Discussion | To discuss | No Specific Reference | More information required for a decision |  | Closed | Part of the governance / ownership step
468 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | Noted: no action required | Action for volume 1. Codelists have been included defining the types of assets covered in each asset class. These codelists are dynamic in nature and over time will be added to as new materials, products etc enter the market | 1.7 Heirarchy | No action
469 | Completed | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Sector Discussion | Tables to be discussed in Final Version Vol 1 | No Specific Reference | More information required for a decision Tunnels have been included |  | Closed | Civil structures added
470 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy | No action
471 | Included | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
472 | Included | 3-Waters | Vol 1 & Vol 2 | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action
473 | Included | 3-Waters | Vol 1 & Vol 2 | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Included | Tables will be referenced in Final Versions | General | No action
474 | Included | 3-Waters | Vol 1 & Vol 2 | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | No action
475 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Noted: no action required | Statement Noted. Business case. | No Specific Reference | No action
476 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Noted: no action required | Statement noted. | No Specific Reference | No action
477 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Noted: no action required | Business case. | No Specific Reference | No action
478 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference | No action
479 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Noted: no action required | Implenmentation is not within scope | No Specific Reference | No action
480 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Noted: no action required | Business Case | No Specific Reference | No action
481 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Noted: no action required | Business Case. | No Specific Reference | No action
482 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
483 | No Action Required | 3-Waters | Vol 1 & Vol 2 | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
484 | Included | 3-Waters | Vol 1 & Vol 2 | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | Included | Included in the draft Standards | General | No action
485 | Included | 3-Waters | Vol 1 & Vol 2 | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | No action
486 | No Action Required | 3-Waters | Vol 1 & Vol 2 | The current drafts need additional work at the hierarchy level and better definition / guidance. | Sector Discussion | Asset Classifications have been defined in the Standards | General | More information required for a decision |  |  |  | Closed
487 | Included | 3-Waters | Vol 1 & Vol 2 | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Included | This is about context for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | Further discussion with Sector |  |  |  | Closed
488 | Completed | 3-Waters | Vol 1 & Vol 2 | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | Included | Included in the draft Standards | General | Change made document updated
489 | Completed | Potable water | Vol 1 | savvy - edit out slang words like this | Included | removed in current version | Executive Summary | Change made document updated
490 | Completed | Potable water | Vol 1 | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? | Included | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. | In Summary | Change made document updated
491 | Completed | Potable water | Vol 1 | Consultants - Replace by organisations? | Included | Term consultants now included in glossary. | 1.1 Register | Change made document updated
492 | Completed | Potable water | Vol 1 | Again, misuse of term 'consultants. edit through the document to correct this. | Included | Term consultants now included in glossary. | 1.4 Disclaimer | Change made document updated
493 | No Action Required | Potable water | Vol 1 | Is this still used? | Noted: no action required | optional supply | 1.5 Deliverables | No action
494 | No Action Required | Potable water | Vol 1 | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? | Noted: no action required | both schemata and schemas are both acceptible words for the plural of schema. | 1.6 Global Schemas | No action
495 | No Action Required | Potable water | Vol 1 | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? | Noted: no action required | This is not within the remit of the standards | No Specific Reference | No action
496 | Included | Potable water | Vol 1 | how can the analytics standardise the data that has already been standardised? | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | No action
497 | No Action Required | Potable water | Vol 1 | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference | No action
498 | Included | Potable water | Vol 1 | i.e. not fixed and topics can be added? | Included | Agree, asset classes can be added as agreed to | 1.8 Theme Structure | No action
499 | Completed | Potable water | Vol 1 | what does this mean? No? but no Y for yes? | Included | N changed to N/A | 1.9 Data Principles | Change made document updated |  | Change made document updated
500 | No Action Required | Potable water | Vol 1 | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.1.1 Accuracy Requirements for Locating Assets | No action
501 | Completed | Potable water | Vol 1 | precisely? 'well' is a subjective term | Included | changed | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
502 | Completed | Potable water | Vol 1 | no 's' | Sector Discussion | cannot identify | 2.1.1 Accuracy Requirements for Locating Assets | More information required for a decision |  | Closed
503 | No Action Required | Potable water | Vol 1 | change 'issues' to 'risks' throughout document | Noted: no action required | not a risk but an issue | 2.1.10 Common Attributes | No action
504 | No Action Required | Potable water | Vol 1 | Well - change to 'bore' | Noted: no action required | term agreed to by TWG | 2.3.4 Well | No action
505 | Included | Potable water | Vol 1 | does this create a 'node'/ if not then it is a problem for modelling. | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | More information required for a decision |  |  |  | Closed
506 | Completed | Potable water | Vol 1 | how is a locator or IP cable taped to the pipe represented? | Sector Discussion | Need more information and example | 2.4.5 Pipe | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attribute field L_or_IP To be included in all the 3 Waters documents
507 | Included | Potable water | Vol 1 | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | No action
508 | Completed | Potable water | Vol 1 | Is a backflow preventer a mechanical equipment asset or a valve/ | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment | More information required for a decision |  |  |  | Closed | Added as a Valve
509 | No Action Required | Potable water | Vol 1 | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure | No action
510 | No Action Required | Potable water | Vol 1 | this could be much larger with additional definitions e.g.. 'trunk main' | Noted: no action required | Codelists are dynamic and wil expand over time | Glossary | No action
511 | Included | 3-Waters | Vol 1 & Vol 2 | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
512 | Included | 3-Waters | Vol 1 & Vol 2 | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
513 | No Action Required | 3-Waters | Vol 1 & Vol 2 | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
514 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | Noted: no action required | Volume 2 is now complete | No Specific Reference | No action
515 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General | No action
516 | Completed | 3-Waters | Vol 1 & Vol 2 | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | Sector Discussion | Included in the draft Standards Asset Classes included that are relevant to each network. These can be added to over time. The pilot implementation phase will be used as a guide | 1.7 Heirarchy | More information required for a decision |  | Closed | Duplicate
517 | Included | 3-Waters | Vol 1 & Vol 2 | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | No action
518 | Included | 3-Waters | Vol 1 & Vol 2 | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Included | Tables will be referenced in Final Versions However it is upto each organisation to determine the most approapriate way to create these links based on their systems | General | No action
519 | No Action Required | 3-Waters | Vol 1 & Vol 2 | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference | No action
520 | No Action Required | 3-Waters | Vol 1 & Vol 2 | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Noted: no action required | This is not within the scope of these standards | No Specific Reference | No action
521 | No Action Required | 3-Waters | Vol 1 | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General | No action
522 | No Action Required | 3-Waters | Vol 1 | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. | Noted: no action required | Service level performance is included in Volume 2 | General | No action
523 | Completed | 3-Waters | Vol 1 | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes | More information required for a decision |  | Closed | CODE LISTS INCLUDED
524 | No Action Required | 3-Waters | Vol 1 | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
525 | No Action Required | 3-Waters | Vol 1 | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. | Noted: no action required | Please refer to Project and common data | General | No action
526 | No Action Required | 3-Waters | Vol 1 | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset owners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General | No action
527 | No Action Required | 3-Waters | Vol 1 | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes | No action
528 | No Action Required | 3-Waters | Vol 1 | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  | Closed
529 | Completed | 3-Waters | Vol 1 | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. | Sector Discussion | More information is required to inform a way forward | General for Pump Station | More information required for a decision |  | Closed
530 | No Action Required | Stormwater | Vol 1 | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. | Noted: no action required | This will be catered for through recording the "Source" | General | No action
531 | Included | Stormwater | Vol 1 | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. | Included | This is a derivation for Volume 3, including precision of survey data | General | No action
532 | Included | Stormwater | Vol 1 | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. | Included | Now normalised and standardsed with Metaconnect | General | No action
533 | Excluded | Stormwater | Vol 1 | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General | No action
534 | No Action Required | Stormwater | Vol 1 | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General | More information required for a decision |  | Closed
535 | No Action Required | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure | No action
536 | Included | Stormwater | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). | Included | Already incorporated into the table | 2.3.1 Containment Structure | No action
537 | No Action Required | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure | No action
538 | No Action Required | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure | No action
539 | No Action Required | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure | No action
540 | No Action Required | Stormwater | Vol 1 | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure | More information required for a decision |  |  |  | Closed
541 | Completed | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall | More information required for a decision |  |  |  | Refer to New attribute or Codelist tab | Created new attribute field 'Apron' is a Yes or No field
542 | Included | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | No action
543 | Completed | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment | More information required for a decision |  |  |  | Refer to New attribute or Codelist tab
544 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber | No action
545 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | Change made document updated
546 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber | More information required for a decision |  | Refer to New attribute or Codelist tab same as ID85 | Duplicate
547 | Included | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | No action
548 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision |  | Closed | To reference operating procedures
549 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber | More information required for a decision |  | Closed | Changed to RL
550 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber | More information required for a decision |  | No further action
551 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. | Sector Discussion | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | More information required for a decision |  |  |  | Closed
552 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). | Noted: no action required | Please refer to comment above | 2.4.2 Channels | No action
553 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. | Sector Discussion | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | More information required for a decision |  |  | Covered by 'Shape' attribute field | Closed
554 | Included | Stormwater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | No action
555 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe | No action
556 | Included | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | Haydn |  | Closed
557 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | Change made document updated
558 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe | More information required for a decision |  | Closed | Modified description to the following 'Protective material enveloping the asset to protect it from damage or intrusion'
559 | Included | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | No action
560 | Included | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | No action
561 | Included | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? | Included | yes in Volume 2 | 2.4.4 Pipe | No action
562 | Completed | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | Change made document updated |  | Closed
563 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe | More information required for a decision |  | Closed
564 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). | Noted: no action required | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station | No action
565 | No Action Required | Stormwater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station | No action
566 | Included | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. | Included | Attribute fields are included in the Pump asset class for motors. Please review and provide details of additional | 2.5.2 Pump | No action
567 | Included | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | No action
568 | Completed | Stormwater | Vol 1 | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. | Sector Discussion | Will include for ratification by the reviewers. | 2.5.2 Pump | New attribute proposed | Trigger level | Refer to New attribute or Codelist tab
569 | No Action Required | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve | More information required for a decision |  | Closed
570 | Included | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | No action
571 | No Action Required | Stormwater | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve | No action
572 | No Action Required | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment | No action
573 | Completed | Stormwater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | Change made document updated |  | Change made document updated
574 | No Action Required | Potable water | Vol 1 | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date | Noted: no action required | Reviewed and Noted only | General | No action
575 | Completed | Potable water | Vol 1 | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General | New Code List proposed | Health & Safety Type | Refer to New attribute or Codelist tab | Modified H&S field from attribute field to Code List
576 | No Action Required | Potable water | Vol 1 | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General | More information required for a decision |  | Closed
577 | No Action Required | Potable water | Vol 1 | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) | Noted: no action required | 10 character fields have been adopted to allow for expansion | General | No action
578 | No Action Required | Potable water | Vol 1 | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General | More information required for a decision |  | Closed
579 | Awaiting Implementation Phase | Potable water | Vol 1 | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. | Sector Discussion | Need more information and example | General | More information required for a decision |  | Closed | Determined that this would be addressed during the Pilot / Implementation phase
580 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). | Sector Discussion | Need more information and example | 2.3.1 Containment Structure | More information required for a decision |  | Closed | Determined that this is a post processing exercise by each organisation as required
581 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | Closed | Added to Specific validation Rule the following. 'If Yes then populate the Health and Safety field'
582 | Included | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | No action
583 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | New Code List proposed | Burial Status Above ground Below ground Partially buried | Refer to New attribute or Codelist tab | Created new attribute field and associated code list 'Burial State'
584 | No Action Required | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure | No action
585 | No Action Required | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure | No action
586 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | Closed | Created new attribute and associated code list 'Inlet Protection Type'
587 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attribute 'Inlet Feed Type'
588 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | Refer to New attribute or Codelist tab | Modified attribute from Shut Off Valve field to Outlet Shut Off Valve
589 | Completed | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attribute 'Partition'
590 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision |  | Refer to New attribute or Codelist tab | Removed 'Con_spc' field and added created new attribute field 'Acc_Rest' and associated codelist
591 | Included | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | No action
592 | Excluded | Potable water | Vol 1 | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment | No action
593 | No Action Required | Potable water | Vol 1 | Asset Class: Civil Structure - WELL a. Include Ground Water Level | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well | No action
594 | Included | Potable water | Vol 1 | Asset Class: Civil Structure - WELL b. Resource Consent number | Included | Included in Project Attributes | 2.3.4 Well | No action
595 | No Action Required | Potable water | Vol 1 | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading | Sector Discussion | Code lists for NZDWS could be included - for discussion | 2.3.4 Well | More information required for a decision |  | Closed
596 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attributes 'Link Feature 2' 'Link Identifier 2' 'Link Feature 3' 'Link Identifier 3'
597 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed | Manufacturer | Refer to New attribute or Codelist tab | Created new attribute fields 'Manufacturer' Manufacturers Warranty'
598 | Included | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | No action
599 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. | Included | Agreed | 2.4.3 Fitting | Change made document updated
600 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting | More information required for a decision |  | Closed | A description has been provided to clarify what a Node is.
601 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe | New Asset Class proposed Detail of data requirements needed | Support Structures | New asset class created 'Support Structure' |  | Closed | Created 'Support Structure' asset class in all 3 waters documents.
602 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. | 2.4.5 Pipe | No action
603 | Included | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | No action
604 | Included | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. | Included | Already catered for | 2.4.5 Pipe | No action
605 | Included | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe | No action
606 | No Action Required | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe | No action
607 | Included | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | No action
608 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. | Included | change in all documents | 2.4.5 Pipe | Change made document updated
609 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter | Included | removed nom_Bore | 2.4.5 Pipe | Removal of attribute proposed Have marked for removal in documents |  | Attribute removed | Removed attribute Nominal Bore from pipes table
610 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe | More information required for a decision |  | Closed | Points can be determined from spatial element provided
611 | No Action Required | Potable water | Vol 1 | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe | More information required for a decision |  | Closed
612 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision |  |  |  | Closed | Modifed 'Cover' entries to 'Lid'
613 | No Action Required | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber | More information required for a decision |  | Closed
614 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attribute field 'Sealed'
615 | No Action Required | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber | More information required for a decision |  | Closed
616 | No Action Required | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | More information required for a decision |  | Closed
617 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | New attribute proposed | Portable generator (Y/N) | Refer to New attribute or Codelist tab | received details from Noel 12/5 Created new attribute field and associated code list 'Power Backup'
618 | Completed | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | New attribute proposed | Calculation | Refer to New attribute or Codelist tab | received details from Noel 12/5 Included attribute fields for Seismic Performance Status Seismic Standard Seismic calculation
619 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve | More information required for a decision |  | Refer to New attribute or Codelist tab
620 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve | New Code List proposed | Valve Control & Automatic Control | Refer to New attribute or Codelist tab
621 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. | Sector Discussion | see 00620 | 2.5.3 Valve | New Code List proposed | Valve Power | Refer to New attribute or Codelist tab
622 | No Action Required | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
623 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve | More information required for a decision |  | Closed
624 | Included | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | No action
625 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection | Refer to New attribute or Codelist tab
626 | No Action Required | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve | No action
627 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Incoming Pressure | Refer to New attribute or Codelist tab
628 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Outgoing Pressure | Refer to New attribute or Codelist tab
629 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Headloss | Refer to New attribute or Codelist tab
630 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE l. Valve mechanism code list should be similar to: BFL Butterfly DIA Diaphragm SLC Sluice GAT Gate BAL Ball KNF Knifegate DAV Double air FLP Flap gate NED Needle SAV Single air SND Solenoid WSC Check PRV Pressure reducing RLV Pressure relief | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Mechanism Butterfly Diaphragm Sluice Gate Ball Knifegate Double air Flap gate Needle Single air Solenoid Check Pressure reducing Pressure relief | Refer to New attribute or Codelist tab | Incorporated into the existing code list 'Valve Type'
631 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow | Refer to New attribute or Codelist tab | Created new attribute field and associated code list 'Valve Purpose'
632 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Include attribute fields describing how the pump is powered - electrical, diesel, petrol. | Sector Discussion | Does this relate to the motor or the pump? To be compared to the attributes of the motor | 2.5.2 Pump | More information required for a decision |  |  |  | Closed | Following response from Tauranga
633 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump | New attribute proposed | Pump oreintation |  |  | Refer to New attribute or Codelist tab
634 | No Action Required | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP c. “Actual pump rate” will at times be meaningless because of Variable Speed Drive (VSD) pumps, that can run at different speeds. This field is therefore either irrelevant for VSD, although it may be an eventual ‘input’ of actual data from control systems. | Noted: no action required | Reviewed and Noted only | 2.5.2 Pump | No action
635 | Completed | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty end date, Purchase date to be reviewed. | 2.5.1 Equipment | More information required for a decision |  | Refer to New attribute or Codelist tab | Warranty end date already included Created 'Purchase Date' as an optional field
636 | Included | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT b. Include Capitalized cost as well as purchase cost | Included | ODRC / ORC / RC are included | 2.5.1 Equipment | No action
637 | No Action Required | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT c. The abbreviated and full attribute names contained in this table are not related to each other (this is possible a typographical error). | Noted: no action required | Resolved in updated version | 2.5.1 Equipment | No action
638 | No Action Required | Potable water | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. An attribute field with an ability to include a SCADA reference should be included. | Noted: no action required | Refer to Telemetry | 2.5.1 Equipment | No action
639 | Completed | Potable water | Vol 1 | Asset Class: Electrical Asset - CABLING a. Ductwork poses a tricky question because it is separate from cabling. Ductwork can be a part of the structure, and can carry many cables. If it is going to be recorded, Ductwork needs to be an asset class in its own right. | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision |  |  |  | New asset class created 'Conduit'
640 | Completed | Potable water | Vol 1 | Asset Class: Instrumentation - INSTRUMENTS a. SCADA and RTU (controllers) are not instruments, because they do not measure variables. Include them under electrical equipment. | Included | Reviewed and Noted for Inclusion | 2.7.1 Instruments | Change made document updated
641 | Completed | Wastewater | Vol 1 | All Asset Classes a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | Included | Will ensure that they are applied. | General | Change made document updated
642 | Completed | Wastewater | Vol 1 | All Asset Classes b. Missing asset classes: There are a number of missing asset classes in the Wastewater Standard – including “Containment Structures” and “Tunnels”. Wellington Water has 23 containment structures for Wastewater, which is material in terms of asset renewal. | Sector Discussion | Additional Assets and attributes will be added to final version | General | More information required for a decision |  | Closed | Duplicate
643 | No Action Required | Wastewater | Vol 1 | All Asset Classes c. It was uncertain how the ‘crossover’ between the Wastewater and Stormwater network is managed within the Standard (including weirs). | Noted: no action required | Otherwise please be specific about the uncertainty. | General | No action
644 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER a. A definition may be required in relation to “relative level”. Relationship of ladders to access chamber; H&S attributes may be required, as ladders need to be certified. Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. This should be considered for inclusion in Volume 2. | Included | Include H&S Attributes | 2.3.1 Access Chamber | Haydn |  | Closed
645 | No Action Required | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS a. Vegetation should not form part of this asset class data attribute for the Wastewater network! | Sector Discussion | to be discussed with the TWG | 2.3.2 Channel | More information required for a decision |  | Closed
646 | No Action Required | Wastewater | Vol 1 | Asset Class: Reticulation Structures  CHANNELS b. Is this really an ‘asset class’ for Wastewater (open sewers?) | Noted: no action required | If they do not exist then this asset class will not be used | 2.3.2 Channel | No action
647 | No Action Required | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES a. Generally felt to be a ‘solid’ set of data attributes related to pipes. | Noted: no action required | Reviewed and Noted only | 2.3.4 Pipe | No action
648 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES b. Is there scope for a new field called “expected remaining life” based on observations? | Included | Remaining life is 'expected', observed or otherwise (e.g. calculated) - related to intervention type | 2.3.4 Pipe | Haydn |  | Closed
649 | Completed | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES c. How are ‘pipe supports’ treated within the Standard? | Sector Discussion | Please provide examples of the types of supports that are used | 2.3.4 Pipe | More information required for a decision |  | Closed
650 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES d. The “Material Description “ field contents need to be set at the correct level – a significant impact on design life results between different materials such as uPVC, mPVC and oPVC, MDPE, HDPE and HPPE | Included | Material is a mandatory attribute | 2.3.4 Pipe | No action
651 | Completed | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES e. Soil Type should also be captured as part of this Standard (impacts design life) and used to inform a wider geospatial dataset. We need to remember that a pipe may cross several soil types. | Sector Discussion | Was previously discussed and rejected by the TWG | 2.3.4 Pipe | Change made document updated External data set
652 | Completed | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES f. Surface Material should be recorded as part of this Standard – impacts structural composition. We need to remember that this field must be an updatable attribute based on non-3W observations. Pipes will also cross several different surface material | Included | Add Surface Material | 2.3.4 Pipe | New attribute & associated Code List proposed | Surface Material Surface Material Type | Refer to New attribute or Codelist tab
653 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PIPES An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. | Included | This is a geospatial layer and can attribute accordingly | 2.3.4 Pipe | No action
654 | No Action Required | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION a. In general, the focus group thought this was a well thought out set of attributes associated with Pump Stations. | Noted: no action required | Reviewed and Noted only | 2.3.5 Pump Station | No action
655 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION b. Attributes related to power supply are important; elements of the “electrical” asset class are related to the pump station (see comments in section 2.9 related to the parent-child relationship inherent in pump stations). Attributes include (at least) an ICP number. | Included | Already included. | 2.3.5 Pump Station | No action
656 | No Action Required | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION c. The Standard is silent on elements related to “Access” and/or “Easements” for this asset class. | Noted: no action required | Correct. Volume 1 focusses on recording asset data at practical completion | 2.3.5 Pump Station | No action
657 | Completed | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station | More information required for a decision |  | Refer to New attribute or Codelist tab | Created new attribute field 'Overflow'
658 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION e. The cost attribute is associated with a particular construction date – ie, the pump station is assumed to be ‘static’. This is not likely. (again – may relate to parent-child relationship of pump station to assets it contains). | Included | ODRC / ORC / RC are included | 2.3.5 Pump Station | No action
659 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION f. Safe working limits are a legal requirement  does this form part of the building standard? | Included | Depth is recorded | 2.3.5 Pump Station | No action
660 | Included | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION g. “Building Owner” could be split between multiple owners | Included | Owner vs manager fields available in the draft standard Catenate multiple owners in field Buildings are separate assets, see buildings | 2.3.5 Pump Station | More information required for a decision |  | Closed | Buildings are separate assets, see buildings
661 | Excluded | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP a. Elements of a pump may be regarded as a distinct asset – such as motors, impellors, control system, cabling. The attributes of a pump relate to the pump type – this field may need further expansion and/or definition. | Excluded | Detailed drawing and component information is provided in manuals on handover - a reference attribute is included | 2.4.2 Pump | No action
662 | Completed | Wastewater | Vol 1 | Asset Class: Mechanical Asset - PUMP b. The line between a pump asset and maintenance is not discussed within the Standard – even though this could change the asset function. | Sector Discussion | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | 2.4.2 Pump | Change made document updated |  | Closed
663 | Included | Wastewater | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. The data attributes within this section seem to relate entirely to Electrical Equipment; this does not make sense for this asset class. For example, the “Serial #” field has a description related to “protective material”. | Included | To be resolved in all 3W tables. | 2.4.1 Equipment | More information required for a decision |  | Closed | Change made document updated
664 | No Action Required | Wastewater | Vol 1 | Asset Class: Electrical asset - EQUIPMENT a. “Risk” should be a key field – with a strong relationship to a relevant Volume 2 table. Safety in Design elements (and residual risk) should form part of this also. | Noted: no action required | Links are not within the remit of these standards - this is an analytical element | 2.4.1 Equipment | No action
665 | No Action Required | 3-Waters | Vol 2 | Data Relationships: Linkages shown in charts between Schema are inconsistent. For example, the “Repairs & Maintenance” schema is shown as interfacing to “As-constructed” and “Condition” schemas. But other Schemas have “Repairs & Maintenance” as an interface. For example, “Financial Performance” and “Demand” both have “Repairs & Maintenance” as an interface. If interlinkages are not shown to be consistent then the validity of the Standard can be questioned. This aligns with the overall statement made in section 1.9 of this document. | Sector Discussion | Relationships are explained in depth in Vol 2 | No Specific Reference | No action
666 | No Action Required | 3-Waters | Vol 2 | 2. Project Area: The project area artefact could apply to any business project over the 3 waters and not simply a new subdivision reticulation e.g. new facility or augmentation of WW or WS plant, refurbishment of upgrading of network etc. Understanding how projects/investments are delivered and perform is an important AM capability. The metadata schema should not constrain how assets are managed to meet desired outcomes. | Noted: no action required | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | No Specific Reference | No action
667 | No Action Required | 3-Waters | Vol 2 | 3. Delivery Risk: In order to generate valid information and outcomes the recording of data in a schema for national reporting will require consistency both within an organisation and between organisations over time. This should be recognised as a risk to the successful delivery of benefits by the Data Standard. | Noted: no action required | Delivery risk is a risk for Volume 3 - Methodology | 1.4.2 Intervention Methodologies (Volume 3) | No action
668 | Included | 3-Waters | Vol 2 | 4. Units of measure in asset management would include flow, pressure, time - these are not in the Code list 1, but these and other units are referenced throughout the schemas. Note that different flow and pressure measurement units will apply to different assets or uses. | Included | Amended Code list | Table 2: Water Supply Service Attributes | No action
669 | Completed | 3-Waters | Vol 2 | 5. Date Range & Traceability: Similar to the comments made in section 2.1 related to Volume 1, key fields in Volume 2 should be auditable, giving the ability to track when changes are made, why and by whom. While a function of an information system, the requirement for such should be included in a metadata standard. | Sector Discussion | More information is required tofully iundertstand this feedback, but systems business rules (e.g. date ranges) are the place for defining extents, not these standards Assessors are included Data Table 1: Condition Attributes Assessor_N Assessor Name text | No Specific Reference | More information required for a decision |  |  | This is a systems requirement - not an element for the NZAMS as per our discussions in the workshops | Closed
670 | Included | 3-Waters | Vol 2 | 6. Code lists provided for Volume 2 generally require more work to develop consistent, full and meaningful references for use. We note that code lists have not been provided for Volume 1. | Included | Code lists have been updated for comment. | List of Code Lists | No action
671 | No Action Required | 3-Waters | Vol 2 | 7. Depreciation Data: Depreciation is an indicator of loss of service potential. Replacement value must reflect the true value of replacement in the current environment – which may be different to the environment at original installation. Changes to value and the rate of deterioration may be due to specific changes to asset attributes and environment over time. There must be fields to link changes to time and place. | Noted: no action required | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Code List 47: Financial Performance Metrics | No action
672 | No Action Required | 3-Waters | Vol 2 | 8. Lack of observation schema: As noted in section 4.4(a), the lack of an “Observations” schema hampers the ability for observation to inform multiple data schemas – such as condition or updates of asset attributes in the as-built schema. | Noted: no action required | Statement noted. Observations will feed into the attributes. | Data Table 1: Condition Attributes | No action
673 | Included | 3-Waters | Vol 2 | 9. H&S Data: Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. | Included | Now included in Risk attributes Con_Rat_HS Consequence Rating Health and Safety | Table 7: Risk Attributes | More information required for a decision |  | Closed
674 | Included | 3-Waters | Vol 2 | Condition a. Condition data is relevant for a range of decisions and processes in the asset lifecycle, most particularly around renewals, risk and valuations. The following comments consider these aspects but also apply to many of the other processes in some degree. | Included | Statement noted. | 2.2 Condition Schema |  |  | Closed
675 | Completed | 3-Waters | Vol 2 | Condition b. The inclusion of a calculated remaining useful life within the condition schema is fundamentally flawed because it does not account for other relevant asset life determining factors. Examples of such include criticality, demand, performance, optimisation and the asset’s operating environment. By linking condition grade directly to remaining useful life, the schema pre-supposes an end of life or replacement date decision. These conclusions should only be made while considering the wider factors as above. Noting this, Code List 6 linking condition grade to remaining useful life should be removed. | Sector Discussion | Let's discuss - these standards are not about decision-making - they are elements for decisionmaking - these standards define each of these elements. We are not suggesting you should make a decision on condition alone. But if your note is about definition of remaining useful life then let’s chat. | 2.2 Condition Schema | More information required for a decision |  | Closed | Condition is only one decision element. The standards expect critical assets have an influence on the timing of replacement. Interoperability analytics allows you to consider criticality alongside condition (in the example). Unfortunately, currently there is no quantitative analysis between these elements. If the pipe up to the hospital is condition 4 (still has a reasonable expected life, maintenance is within normal levels), then you still might chose to replace it because it's the pipe up to the hospital and do not want to take the risk.
676 | No Action Required | 3-Waters | Vol 2 | Condition c. It is recommended that the schema be modified to take into account the level of confidence in condition grades. There is little or no recognition of the probabilistic nature of condition assessments and hence the confidence limits which apply to the grades. Any condition grade is made within a band of confidence at a point in time. The confidence level is relative to whether it is being applied to a subject asset or extrapolated to an asset group, and whether it is applied at the time of assessment or projected forward. | Noted: no action required | This is a calculable field, for example, stochasticity | No Specific Reference | No action
677 | No Action Required | 3-Waters | Vol 2 | Condition d. The basis of the interfaces with other schema (Table 5) is unclear and the linkages shown do not acknowledge the relationships between condition data and all other schema. Eg: i. Criticality determines priorities for condition data collection ii. Repairs and maintenance activities are a key potential source of condition data iii. Condition is indicative of likelihood of failure and hence helps determine risk iv. Service and financial performance are impacted by condition v. Demand and utilisation inform the criticality of an asset and hence priority for condition data collection. | Noted: no action required | These are analytical outputs of specific problems being solved. We can discuss | No Specific Reference | No action
678 | Completed | 3-Waters | Vol 2 | Condition e. Items included in the condition data attributes (Table 2) appear to be a mix of data at different levels of detail; some being at the assessment level and others at the observation level. Any hierarchy or relationship between these is not implied or explained however. The potential one-to-many linkages from asset to assessments and further to observations are not apparent. Any data required must be clarified in terms of how it relates to other data to enable practical processes for capture and storage. | Sector Discussion | Action: To be discussed with Wellington Water. | Data Table 1: Condition Attributes | More information required for a decision |  |  | Condition can be determined a number of ways, the standards reflect this fact. | Closed
679 | Included | 3-Waters | Vol 2 | Condition f. The description of condition grades against physical deterioration (Code List 2) is a good approach however the terminology is inconsistent. Most descriptors but not all relate to asset failure. All should be described on the same basis to allow for consistent interpretation. “Asset failure” in this sense also requires definition and is unclear in the schema. | Included | Uniform terminology now applies | Code List 16: Condition Rating | No action
680 | Included | 3-Waters | Vol 2 | Condition g. The condition grade types (Code List 3) are unclear and do not give any sense of the distinctions or relationships between structural, service, mean, peak and overall grades. | Included | Condition code lists (e.g. structural, exterior, interior) are now included in Vol 2 | Code List 16: Condition Rating | No action
681 | Awaiting Implementation Phase | 3-Waters | Vol 2 | Condition h. The condition grade assessment methodologies (Code List 4) and assessment types (Code List 5) are extremely limited and do not capture many methodologies that are currently available and in use. Terminology is not consistent with the purpose of the list, ie; “Cut out” is a sampling methodology rather than an assessment type as listed. A cut out may be assessed visually, by destructive and/or non-destructive testing, or other means. Code lists 7 – 10 are similarly limited and the purpose and usage of which are unclear. | Sector Discussion | See code list | Code List 17: Condition Rating – Methodology | More information required for a decision |  |  | This is an issue for volume 3 | Closed | To be updated during and after implementation phase
682 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance a. The Proactive and Reactive Activity Type descriptions need additional clarification to minimise ambiguity. How should “impairment” be interpreted - breakdown, significant performance issue or just incipient failure only detectible with monitoring equipment (e.g. bearing vibration, thermographic image, etc)? Also “Scheduled” needs to exclude non-routine or one-off activities that are set to occur in the future. | Noted: no action required | See code list | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
683 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance b. The schema does not support optimisation of maintenance tasks through RCM analyses or other FMECA based approaches. An example would be the need for a clear and unambiguous definition of asset function. This is not well covered in Part 1 attributes. Comment should be requested from an RCM practitioner. | Noted: no action required | Statement noted. This is not a maintenance management system. | No Specific Reference | No action
684 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance c. Recording the “Image_ID” against activities does not cater for referencing other types of digital files. Suggest this optional attribute is made generic and capable of accepting hyperlinks to reference files in other systems. | Noted: no action required | This is an analytical requirement | No Specific Reference | No action
685 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance d. Fail_Mode and Cause_Iss is important but must be specific to each asset type rather than generic across all assets. It’s not clear if this is the intention. | Noted: no action required | This is an analytical requirement and is matched to other elements (e.g. AssetID) to determine response | No Specific Reference | No action
686 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance e. A key decision for every asset is to either run to failure or apply a scheduled maintenance/inspection plan. | Noted: no action required | This is an analytical requirement (i.e. both) | No Specific Reference | No action
687 | Included | 3-Waters | Vol 2 | Repairs and Maintenance f. In Part 1 Condition Assessment Type is an asset attribute, but Condition is part of a different schema. Shouldn’t these go together to reflect the fact that the condition assessment approach may change over time? | Included | Yes, but in the analytical phase. | No Specific Reference | No action
688 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance g. It isn’t clear how maintenance strategies are to be handled (i.e. managing maintenance work that has weekly/monthly/annual/ etc activities). AMIS functional requirements should be considered before fields like Recur and Recur_Cyc are established. | Noted: no action required | Standard is not intended to populate a maintenance plan. Code Lists are included to handle this requirement e.g. Recurrence Cycle | Code List 5: Recurrence Cycle Unit | No action
689 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance h. Need quantity as well as cost information to be able to analyse trends and predict future costs. Need to record all resources – not restricted. | Noted: no action required | Code lists for quanitifying repairs included | Code List 6: Bases of Cost | New Code List from Working Group |  | Refer to New attribute or Codelist tab
690 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance i. The combination of Activity Type, start date/time, end date/time does not appear to meet the requirements for DIA non-financial reporting for urgent/non-urgent callouts (i.e. need to separately record time to reach site and time to resolve issue). | Noted: no action required | Type of maintenance activity is included | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
691 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance j. There needs to be a new Event Type similar to “Upgrade/Improvement”. Irrespective of the funding source (capital vs operational) assets need to have a full history of events recorded against them. If we exclude upgrades and rely solely on project registers to capture this information we make lifecycle management significantly more difficult. | Noted: no action required | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Code List 49: Description of Financial Performance Element | No action
692 | Included | 3-Waters | Vol 2 | Repairs and Maintenance k. Why record overflows etc. in repairs and maintenance schema and not in the level of service? Overflows are recorded per financial year, different organisations have different financial years, is history recorded i.e. over time. Should other compliance activities i.e. RON and CDEM should also be coded. | Included | One is a record of the type event One is a record a service level e.g. overflows per year and an analytic | Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | No action
693 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance l. Asset versus component issue can give rise to different design criteria and system performance i.e. a pump has a l/s design while a filer has (say) minimum pressure drop, but it is performing of the pumping station that is the issue. | Noted: no action required | Statement noted | No Specific Reference | No action
694 | Included | 3-Waters | Vol 2 | Repairs and Maintenance m. Does not appear to allow for other investigation methods e.g. vibration analysis, DCVG results, thermal imaging, usage data analytics for identifying if an intervention is required. | Included | Code lists to be discussed against current code lists e.g. Condition (This is really a Volume 3 question) | Code List 17: Condition Rating – Methodology | No action
695 | Included | 3-Waters | Vol 2 | Repairs and Maintenance n. As found and as left condition or status is useful for items like valves, could also apply to depth of cover, locks etc. | Included | Statement Noted: No action required. | No Specific Reference | No action
696 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance o. Asset performance does not clearly link to key result areas or key performance indications set by organisations in the management of assets or demanded by consumers. | Sector Discussion | This is an anlytical question - discuss with sector | No Specific Reference | More information required for a decision |  | Closed |  | Closed
697 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance p. Asset or service performance - it is not clear what is referred to or if this is consistent. | Sector Discussion | Section updated in Volume 2 | 5.4 Service Performance Schema | More information required for a decision |  | Closed |  | Closed
698 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance q. How are components and soft parts etc linked to assets, is the lifecycle of O&M supported by this? | Noted: no action required | Component type is an attribute in the repair schema and captured under each asset. | 2.3.4 Components of Repairs, Maintenance and Operations | No action
699 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance r. Benchmarking - same as identified in service levels schema, consistency is required for valid and useful outputs to be obtained. | Noted: no action required | Statement noted and agreed. | No Specific Reference | No action
700 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance s. Outage duration - mandatory for all actions but what if no outage? Also what if the customers are reinstated over time ie 95% connected in 1 hour while the rest are out for days? Outage is linked to ' number of people' - this can be impossible to measure depending on each connection (as in an apartment block), would customer or property be a better measure. | Noted: no action required | Agreed. Then outage duration = 0. | No Specific Reference | No action
701 | Included | 3-Waters | Vol 2 | Repairs and Maintenance t. Third party damage excluded from outage definition but included in repair schema as cause. | Included | Third Party attribute included | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
702 | No Action Required | 3-Waters | Vol 2 | Repairs and Maintenance u. Maintenance planning - focused on time based maintenance (elapsed), but could encompass operating hours or CBRM. A MMS would do a better job, would it be better not to specify these matters in the schema and just have an objective for an outcome based system in place. This could be applied throughout the data standard noting the issues with consistently in benchmarking. | Sector Discussion | Analytical elements included in standards to schieve this analytic | No Specific Reference | More information required for a decision |  |  |  | Closed | Out of scope
703 | Included | 3-Waters | Vol 2 | Repairs and Maintenance v. It would be desirable to have costs for maintenance collected on an area/project basis for performance analysis. | Included | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | No Specific Reference | No action
704 | Included | 3-Waters | Vol 2 | Repairs and Maintenance w. Should complaints be linked to an issue or root cause rather than an address or asset - this would enable better linking and development of appropriate solutions and priority setting than a collection of disparate reports. Also need to know the outcome of the assessment of a compliant ie internal plumbing, no issue found etc before an organisation make decisions on number of complaints. Option of an outcome based CRM system rather than data standard? | Included | Linking CRM information to asset information is not in scope These root cause examples in the code list are asset related interrogations for asset management purposes. | No Specific Reference | No action
705 | Included | 3-Waters | Vol 2 | Utilisation a. Asset utilisation needs to consider the level of redundancy in the network or asset system required to achieve the desired overall level of risk. The proposed calculation of utilisation could work for an individual pump, but would be of little/no value for a trunk main network. It could easily be misinterpreted. | Included | Redundancy is include in the codelists in Vol 2 as an analytical attribute (see vulnerability). | Code List 43: Global Resilience Rating Elements | No action
706 | No Action Required | 3-Waters | Vol 2 | Utilisation b. Until the intervention methodologies are proposed for each of the 3 waters we find it difficult to understand what fields may or may not be wanted for this schema. | Noted: no action required | Statement noted. | 3.2.5 Code Lists |  |  | Closed
707 | Included | 3-Waters | Vol 2 | Demand a. Demand applies to collections of assets. Why would you want to record demand against an individual asset such as a pipe or valve? | Included | This is an analytics requirement, but may no be required agaist all asset components. | No Specific Reference |  |  | Closed
708 | No Action Required | 3-Waters | Vol 2 | Demand b. The fields offered are very limiting in this schema and the use of demand needs to be thought through in more depth. | Noted: no action required | Demand Section has been updated in Volume 2 | 3.3 Demand Schema |  |  | Closed
709 | No Action Required | 3-Waters | Vol 2 | Demand c. Peak demand at a system level is not the sum of zone demands due to the diversity/averaging effect as the study area increases in size. Average demand at a system level is the sum of the zone demands. The schema does not seem to recognise this. | Noted: no action required | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler | Data Table 4: Demand Attributes | No action
710 | No Action Required | 3-Waters | Vol 2 | Demand d. What analytics would this schema (as is) be used to support? | Noted: no action required | Future connections on flow (population demand) | Code List 33: Demand – Measure | No action
711 | No Action Required | 3-Waters | Vol 2 | Demand e. Should this schema exist in an AMIS? | Noted: no action required | Yes | 3.3 Demand Schema | No action
712 | No Action Required | 3-Waters | Vol 2 | Criticality a. Criticality is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | No change | 4.3 Criticality Schema | No action
713 | No Action Required | 3-Waters | Vol 2 | Criticality b. The current approach to criticality from Wellington Water uses criticality as an equivalent to consequence in the evaluation of risk. To this effect the criteria for criticality that we have developed uses cumulative weighted impacts in combination with importance (exposure) factors to derive risk. My view is that the criticality descriptors offered in the standards are only one component of the consequence variable in the risk equation ie the exposure factor. To this extent it is puzzling to identify how criticality as described could be used in the evaluation of risk – given the subsequent content of the risk schema. | Noted: no action required | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | 4.3 Criticality Schema | No action
714 | No Action Required | 3-Waters | Vol 2 | Criticality c. For example if the renewal of a pipe was being considered wrt risk of failure – condition is an indicator of probability, the potential impacts could be social, environmental or financial loss and the exposure is measured by the number of people or the importance of the facility affected by the loss of service. | Noted: no action required | These are analytical inferences which are attributed in code in algorithms by attributes these standards define | No Specific Reference | No action
715 | No Action Required | 3-Waters | Vol 2 | Criticality d. Until worked examples are provided as to how the consultants perceive criticality being used for different decisions we struggle to see how the schema as offered would be useful or at best would have limited value. | Noted: no action required | Explanation found in criticality schema | 4.3 Criticality Schema | No action
716 | No Action Required | 3-Waters | Vol 2 | Criticality e. The code list 27,28,29 tables have some potential flaws in our view. i. Special facilities is too vague as a term for Code 5. Few utilities would have munition storage or critical data centres and in most cases data centres would have back up. How is this derived for example if it was potential damage from blowing up a munitions store, how would compare to an LPG centre or holding tanks containing solvents ii. For a water utility is a hospital really less critical than a data centre? iii. What happens when an asset services 3 or 4 hospitals iv. Where is economic loss factored into these tables – they seem to be very “government” centric v. We struggle to think that decision making using criticality for small towns of less than 5000 people would only ever have code 3 assets as their most important asset. Risk is about context and the context must consider the community and the economic scale of their investment. We do not believe one size fits all. | Noted: no action required | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. | No Specific Reference | No action
717 | No Action Required | 3-Waters | Vol 2 | Risk a. Risk is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Noted: no action required | Statement noted. | No Specific Reference | No action
718 | No Action Required | 3-Waters | Vol 2 | Risk b. We assume that the risk schema is intended to facilitate risk management within water utilities. | Noted: no action required | Yes, and for buildings per the Biulding Standard | 4.4 Risk Schema | No action
719 | No Action Required | 3-Waters | Vol 2 | Risk c. We have reviewed this schema with respect to the principles of risk management as outlined in Section 3 of the guideline document for AS/NZS 31000:2009 | Noted: no action required | Noted | 4.4 Risk Schema | No action
720 | No Action Required | 3-Waters | Vol 2 | Risk d. In particular the schema as drafted inhibits the following principles: | Noted: no action required | Noted | 4.4 Risk Schema | No action
721 | No Action Required | 3-Waters | Vol 2 | Risk e. 3(g) Risk management is aligned with the organisations external and internal context and risk profile | Sector Discussion | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  |  |  | Closed
722 | No Action Required | 3-Waters | Vol 2 | Risk f. 3(h) Risk management recognises the capabilities, perceptions, and intentions of external and internal people that can facilitate or hinder the achievement of the organisations objectives | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | Closed
723 | No Action Required | 3-Waters | Vol 2 | Risk g. 3(j) Risk management continually senses and responds to change. As external and internal events occur, context and knowledge change, monitoring and review of risks takes place, new risks emerge, some change, others disappear | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | Closed
724 | No Action Required | 3-Waters | Vol 2 | Risk h. To propose a specific risk matrix into a national standard seems to conflict with these basic principles | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct And any organisation can taylor the analysis to the local context | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | Closed
725 | No Action Required | 3-Waters | Vol 2 | Risk i. Although interdependencies between other schemas are stated it is difficult to extract how they would be used together. Risk, criticality and condition must be interconnected but there is no indication as to how the application of these schemas would allow this | Noted: no action required | This would depend on the problem being solved and the analytical approach in doing so | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | Closed
726 | No Action Required | 3-Waters | Vol 2 | Risk j. The suggestion that probability scales for different events and water types are the same is unhelpful in the absence of worked examples. Are there examples to demonstrate a sensible cross relationship for the use of probability scales in water supply and stormwater? | Noted: no action required | Unclear of what this means, but the scales are adaptive to event type, but specifiuc to asset type | 4.4 Risk Schema | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | Closed
727 | Completed | 3-Waters | Vol 2 | Risk k. Other than flood risk, how do you assess time based probabilities? The use of the word “time to time” or “in your career” will lead to subjective assessments that will simply promote inconsistent investment decisions rather than secure them. | Noted: no action required | Code list updated | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
728 | No Action Required | 3-Waters | Vol 2 | Risk l. We believe the contents of the fields that describe 1- 5 consequences should be omitted. A decision to occupy these fields for a national risk schema to derive nationally consistent approaches to risk will do exactly the opposite – it promotes subjective assessment and also directly contravenes the principles of risk management as described in AS/NZS 31000. | Noted: no action required | To discuss, see code lists | Code List 41: Consequence Rating | More information required for a decision |  | Closed
729 | Included | 3-Waters | Vol 2 | Resilience NO schema offered However, we urge you to consider a fundamental question when addressing resilience for water utilities. Is the assessment of an assets’ resilience important or is it more important to assess the resilience of the service provided to customers on a national scale? We would suggest the latter, and therefore question the merits of offering a schema for asset resilience. If it is the latter, we also suggest that resilience is better attributed to customers rather than assets. | Included | Schema updated | 4.5 Resilience Schema | No action
730 | No Action Required | 3-Waters | Vol 2 | Design Performance This schema is not required. We don’t need evaluative criteria here. Attributes should be in the as built schema and actual performance should be in service performance. Table 12 in all volume 2 documents (sections 9.3) refer to the linkages with the resilience schema not the design performance | Noted: no action required | Let's discuss this is important. Design performance is different than Service Performance | 5.2 Design Performance Schema | More information required for a decision |  | Closed
731 | No Action Required | 3-Waters | Vol 2 | Financial Performance a. General comment – It would be interesting to know what is determined to be core data requirements with regards to the attributes. There is a large set of attributes to collect a large number would only be relevant to a small number of organisations. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | 5.3 Financial Performance Schema | No action
732 | No Action Required | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
733 | No Action Required | 3-Waters | Vol 2 | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema | No action
734 | No Action Required | 3-Waters | Vol 2 | Financial Performance c. Valuation date doesn’t seem to appear anywhere. | Noted: no action required | Included in standards | Data Table 10c: Valuation Attributes Details (Collected Level Indicated) | No action
735 | No Action Required | 3-Waters | Vol 2 | Financial Performance d. Linking the financial information e.g. revised asset lives with condition data. | Noted: no action required | Attributes included in standards, this is an analytical exercise | No Specific Reference | No action
736 | No Action Required | 3-Waters | Vol 2 | Financial Performance e. Terminology is not consistent with the Repairs and Maintenance schema e.g. reactive/planned/etc. | Noted: no action required | Now consistently applied | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
737 | No Action Required | 3-Waters | Vol 2 | Service Performance Level of service is recorded against individual assets, this may cause issues where service level is required from a network, facility, project, contract or organisational levels. These levels of service may not directly relate to asset parameters or the level of service at an asset may relate to another asset upstream (e.g. minimum pressure at a downstream point relates to the upstream network and pumps/regulators etc). Also levels of service are not static and these may change (this change may be the result of internal or external drivers). | Noted: no action required | These are analytical constructs from an individual assetID dataset. How consolidated into geographic units os for the specific analysis, e.g. network, zone, catchement etc. | No Specific Reference | No action
738 | No Action Required | 3-Waters | Vol 2 | Service Performance a. Benchmarking relies on the consistency of inputs. In order to generate valid information and outcomes the recording of data in a scheme for national reporting will require consistency in an organisation, between organisations and over time. Other national standards have shown there are issues with this approach, will the benefits of a metadata standard be realised (what are the risks and assumptions to the achievement of this benefit)? | Noted: no action required | This is a reference to standardised analytical approaches | No Specific Reference | No action
739 | No Action Required | 3-Waters | Vol 2 | Service Performance b. Residential demand figure, valid for industrial or commercial areas, how updated and how is history against assets recorded? | Noted: no action required | This is a reference to an analytical approach. E.g. ParcelID District Plan Zone type and connection demand (or Level of Service). | No Specific Reference | No action
740 | No Action Required | 3-Waters | Vol 2 | Service Performance c. Is it feasible that the same assessor (individual) is used for all items in each asset i.e. cultural significance and technical design and financial measures? | Noted: no action required | The same or multiple | No Specific Reference | No action
741 | No Action Required | 3-Waters | Vol 2 | Service Performance d. Consents compliance is linked to an asset when consents are typically given on an activity/facility - correct linkages and business processes will need to be established and implemented to ensure that compliance is achieved in light of asset changes. | Noted: no action required | Consent attributes are captured at property level which is not inconsistent with reporting at network/zone level - i.e. it is a spatial query between the two data sets. The attributes are specified for capturing asset detail in the standards | No Specific Reference | No action
742 | No Action Required | 3-Waters | Vol 2 | Service Performance e. Third party damage is excluded from service measures (interruptions) for water supply. This is a valid facet of AM, and the scheme has this included in repair and maintenance for WW assets. | Noted: no action required | Included in the Standards | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | No action
743 | No Action Required | 3-Waters | Vol 2 | Service Performance f. MoH grading should be linked to a time the grade was awarded, and possibly should be greater than just a single field i.e. who assessed etc. We question the merit of this as a valid asset performance measure as it is always system based. | Noted: no action required | Included in the Standards | Data Table 11: Service Performance Attributes – Functional | No action
744 | No Action Required | 3-Waters | Vol 2 | Service Performance g. The fact a health and safety assessment has been carried out is interesting, but it is the results that are important (have the risks been addressed or are there outstanding issues etc) and there is no mention of this. | Noted: no action required | Included in the Standards | Table 2: Water Supply Service Attributes & Code List 41: Consequence Rating | No action
745 | Included | 3-Waters | Vol 2 | Maintenance Planning i. Will the scheme provide an effective (and efficient) link to maintenance management systems that are in use currently? | Included | Yes that is the intention for the future. | No Specific Reference | No action
746 | Included | 3-Waters | Vol 2 | Maintenance Planning ii. Are all costs collected at an asset level, won't different treatments give rise to different outcomes, ie, where are staff or contractor costs added to a facility, item or asset. Is maintenance carried out on assets as they exist or on notional assets? | Included | Application of costs will be at the discretion of the rganisation, but likely to be applied to a cohort of assets when being maintained | No Specific Reference | No action
747 | Included | 3-Waters | Vol 2 | Operational Performance i. Actual performance should also be recorded as well as consent compliance - is water quality improving over time or always just inside the limit? | Included | Action: add in to schema (design performance? Service performance) | Data Table 9: Design Performance Attributes | No action
748 | No Action Required | 3-Waters | Vol 2 | Operational Performance ii. There is reference to LAWA framework – is this commonly used throughout the country? Would it be better to refer to the National Policy Statement or specific Regional rules as applicable for the authority? | Noted: no action required | All regional councils use LAWA | No Specific Reference | No action
749 | No Action Required | 3-Waters | Vol 2 | Valuation and depreciation Asset life versus economic/accounting life, does asset structure match the chart of accounts used by all organisations and applied in all business models i.e. contracted services? | Noted: no action required | Yes - there are appropriate fields for ODRC, ORC, RC and Forecast, Actual and Budget financial information in Finance Performance sections | Code List 47: Financial Performance Metrics | No action
750 | Completed | 3-Waters | Vol 2 | Planning for growth or decline i. Assets will need lifecycle stages not just in service ie proposed (linked to project), out of service, in store, abandoned, leased for F/O etc (assets can provide other services, not just those implicit in the standard) | Included | Discuss with Sector - to consider schema | No Specific Reference | Create a code list of service types as suggested here? |  | Refer to New attribute or Codelist tab
751 | No Action Required | 3-Waters | Vol 2 | Planning for growth or decline ii. Levels of service can change over time on different assets, this will need to be understood/recorded | Noted: no action required | Atributes to do this are included in the standards | No Specific Reference | No action
752 | No Action Required | Wastewater | Vol 1 | In talking about As Managed, I assume this is for how the councils handle data rather than how the data supplied by survey from the field, as these are two different worlds? | Sector Discussion | This is a discussion in the development of Volume 3 | No Specific Reference | No action |  |  | OUT OF SCOPE - VOLUME 5
753 | Completed | Wastewater | Vol 1 | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this | Included | Reviewed and Noted for Inclusion Included as part of the Project Attributes table Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | More information required for a decision |  |  |  | Refer to new attribute or Codelist tab
754 | Included | Wastewater | Vol 1 | There is increased risk to data accuracy in companies that are not working all the time with software projection transformations. As the client, I would always want to receive the data in it original projection and transfer it myself | Included | The requirement is for each company to deliver the data in the final projection and datum | 1.5 Deliverables | No action
755 | No Action Required | Wastewater | Vol 1 | Why is this BIM Enabled? Should this not be BIM Enabled/Geospatial Representation as these still hold and display 3d information. | Noted: no action required | Update, asset management and facility management systems do…. | 1.9 Data Principles | No action
756 | No Action Required | Wastewater | Vol 1 | This surely should be "current parcel" boundaries. Not sure as to what a title/property boundary is, as what is the definition of property (residence, address, rating unit, parcel(s))? Also, is this relevant?You want the assets to be shown in true survey location even if this shows them being constructed illegally through private property. | Sector Discussion | For analytical purposes Have added 'geographical units' code list | 2.1 Technical Reference Information | More information required for a decision
757 | No Action Required | Wastewater | Vol 1 | I believe this is how data should be stored, but supply of data should be as captured. By forcing this to the supplier you are increasing the risk of error, with groups that will only project data occasionally more likely to make mistakes | Noted: no action required | The intent of this is to educate the indutsry in what capability it will need | 2.1.2 Projections and Datums | No action
758 | No Action Required | Wastewater | Vol 1 | Why would you develop a new specification and then allow for it to be supplied in a historic format such as shapefile. This also means that the defined "text" geometry type cannot be supplied and instead would need to be changed to a point | Noted: no action required | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF | 2.1.7 Metadata Definitions | No action
759 | No Action Required | Wastewater | Vol 1 | Is this cost of the asset or cost of the asset plus installation? Is this standard cost of the recommended price of the asset, rather than any discounts were achieved? | Noted: no action required | All replacement costs include installation | 2.1.10 Common Attributes | No action
760 | Completed | Wastewater | Vol 1 | Is the central location the centre of access (i.e. manhole lid)or the centre of the structure? | Included | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. | 2.3.1 Access Chamber | Change made document updated
761 | No Action Required | Wastewater | Vol 1 | Pipe length shown here is neither the length of the digital pipe feature or the length of the real world feature, as you are not taking into account the "faux" pipe connectors angle. The middle pipe length here is very confusing! | Sector Discussion | Need more information for a way forward | 2.3.1 Access Chamber | More information required for a decision |  | Closed
762 | No Action Required | Wastewater | Vol 1 | Does this mean covered by dirt and not readily accessible or below ground level? | Noted: no action required | Below ground level | 2.3.3 Fitting | No action
763 | No Action Required | Wastewater | Vol 1 | What happens when two separate pipes are installed between access points (e.g. different material etc). Also there are examples were pipes may not have access chambers (as defined by this document). While that may be not best practice, it does occur. | Noted: no action required | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists | 2.3.4 Pipe | No action
764 | Included | Wastewater | Vol 1 | Is this the digital length or the real world length? | Included | This is the real world length as described in the QA validation field. | 2.3.4 Pipe | No action
765 | Completed | Wastewater | Vol 1 | What does this mean? What level of accuracy is defined as a discrepancy? | Included | Changes made to wording to reflect tolerances used in practice ('field') | 2.7.2 Matching to Existing Infrastructure | Change made document updated
766 | Completed | Potable water | Vol 1 | Asset Group: To be consistent with Section 1.8 Should this heading be changed to "Asset Category" ? (Or in section 1.8 change "Asset Category" to "Asset Group" | Included | Changed to Asset Group for consistency. | 1.7 Heirarchy | Change made document updated
767 | Completed | Potable water | Vol 1 | Asset Type: To be consistent with Section 1.8, should this be changed to "Asset Class" | Included | Changed to Asset Class. | 1.7 Heirarchy | Change made document updated
768 | Completed | Potable water | Vol 1 | The paragraph refers to "Asset Types", yet table 1.8 does not reference "Asset Types", only "Asset Class". If these are not interchange in relation to meaning, then I suggest a explanation of "Asset Type" and "Asset Class" be documented within the document somewhere. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
769 | Completed | Potable water | Vol 1 | My personal preference is to utilize "Asset Class" as standard terminology, and replace any instances of "Asset Type" within the document if they are inferring the same meaning. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
770 | Completed | Potable water | Vol 1 | My personal preference is to utilize "Asset Category" as standard terminology, and replace any instances of "Asset Group" within document. | Included | Changed to Asset Class. | 1.8 Theme Structure | Change made document updated
771 | Completed | Potable water | Vol 1 | Conflicts with section 2.3.4 states that a well is to be represented as a polygon | Included | Changed to Polygon | 1.8 Theme Structure | Change made document updated
772 | Awaiting Implementation Phase | Potable water | Vol 1 | Listed here as a guide, but each definition of the asset class states the required spatial representation. ie 2.3.1 states polygon feature. Therefore for clarity, should this table also list the requirement of the standard for each asset class? | Sector Discussion | More information is needed for a way forward | 1.9 Data Principles | More information required for a decision |  |  | The standard allows for representing any component / asset / asset class / group of assets etc in any way organisations like. I'm not sure we need to do this for all, as it will be different in different circumstances | Closed | To be resolved during implementation
773 | Included | Potable water | Vol 1 | I am assuming this only for Geo-spatial attributes? (As there may be different sources utilized across multiple attributes.) If this is correct, can this be added for clarity in the contents column. | Included | Defined by organisation | 2.1.10 Common Attributes | No action
774 | No Action Required | Potable water | Vol 1 | If the data source changes, is there a need to keep a date history of the changes. | Noted: no action required | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. | 2.1.10 Common Attributes | No action
775 | Completed | Potable water | Vol 1 | Common Attributes for your consideration: (We currently have the following 3 attributes fields across all our assets) - Manufacturer (of asset) - Supplier (of asset) - Installed By (Contractor who installed asset) Fields to be utilized to identify failing assets due to manufacturer/supplier and potential faulty installation by a contractor. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | change made document updated | Incorporated where relevant
776 | Completed | Potable water | Vol 1 | This field should be allowed to be empty. What if there is no photographic references available. Flows through to Asset Class definitions | Sector Discussion | consider N/A as an appropriate response. | 2.1.10 Common Attributes | More information required for a decision |  | change made document updated | Modified attribute General Validation Rule to also include that the field is 'Optional'
777 | Included | Potable water | Vol 1 | Define "Asset Classes" and "Asset Types" | Included | Asset Classifications have been defined in the Standards | 2.2 Asset Categories | No action
778 | Completed | Potable water | Vol 1 | RL: Add a definition of RL in the "Glossary of Terms and Definitions" in the document (Reduced Level) "RL" acronym used in multiple places in the document. | Included | Included in Glossary | 2.3.2 Embankment, Glossary | Change made document updated
779 | Completed | Potable water | Vol 1 | No Type field for Wells. ie Type_Well Is this an oversight or genuinely not needed? | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision |  |  |  | Closed
780 | Completed | Potable water | Vol 1 | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) | Sector Discussion | to be discussed with the TWG | 2.3.4 Well | More information required for a decision |  | Refer to New attribute or Codelist tab | Created attribute field 'Construction Method' and associated code list
781 | Completed | Potable water | Vol 1 | Seem to be missing Chamber Diameter, for circular access chambers. (As it states that AC_Length and AC_width only to be used if chamber is non circular) | Sector Discussion | Needs some rework and clarifiation. | 2.4.1 Access Chamber | More information required for a decision |  | Change made document updated
782 | Completed | Potable water | Vol 1 | Potential Attribute: Manufacturer of Fitting | Included | Already identified and will be refered to TWG. | 2.4.3 Fitting | New attribute proposed | Manufacturer | Refer to New attribute or Codelist tab
783 | No Action Required | Potable water | Vol 1 | Water flow direction is not absolute. I am assuming this is for a network operating under "normal" conditions. | Included | Correct. For a network operating under 'normal' conditions. | 2.4.5 Pipe | No action
784 | Completed | Potable water | Vol 1 | For clarity, perhaps include a diagram showing an irregular access chamber. Refer to page 20 in Vol 1 of the waster water meta-data standard (V1.2 DRAFT A - 14 July 2016) | Sector Discussion | Completed | 2.4.6 Pump Station | Change made document updated
785 | Completed | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrectly matched. EG Serial_No => Protective Material This is carried through to the Waste Water and Storm Water manuals. | Included | Resolved in current version. | 2.5.1 Equipment | Change made document updated
786 | Completed | Potable water | Vol 1 | Abbreviated and Full descriptions are incorrect matched. | Included | Resolved in current version | 2.5.1 Equipment | Change made document updated
787 | Completed | Potable water | Vol 1 | In our AMIS we are planning to utilize two fields to describe valves. Valve Type: Eg Isolation, Scour, Toby, Pressure Reducing, etc .. Valve Mechanism: Eg Gate, Knife, Ball, Air Release, etc.. Rather than combine function and mechanism into one attribute field. | Sector Discussion | to be discussed with the TWG refer to 630, 631 | 2.5.3 Valve | More information required for a decision |  | Refer to New attribute or Codelist tab (same as ID630/631)
788 | No Action Required | Potable water | Vol 1 | Where are readings recorded? Should there not be an attribute for the latest meter reading and date it was recorded. | Noted: no action required | As Constructed' data not operational data. | 2.7.1 Instruments | No action
789 | Completed | Potable water | Vol 1 | Incorrect reference: Should be 1.8 | Included | Resolved in current version. | 2.8.2 Matching to Existing Infrastructure | Change made document updated
790 | No Action Required | Potable water | Vol 2 | Terminology Constancy: In Vol 1, Section 1.8, a lot of the elements below are referred to as "Asset Classes" They are also referred to "Asset Classes" in the attribute and validation file format. Suggest change "Categories" to "Classes" | Noted: no action required | Standards updated to a consistent approach | Table 3: Asset Hierarchy Framework | No action
791 | No Action Required | Potable water | Vol 2 | I am unsure what this means. Can there be more explanation of the content in the Rules column. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
792 | No Action Required | Potable water | Vol 2 | What is Rule 2? Ensure on what this means. | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions | No action
793 | No Action Required | Potable water | Vol 2 | How are these levels recorded in the date table 7? (ie Network, facility) Table 7 only links back to an individual asset level (Unique_ID) There does seem to be merit to applying Risk to a network level, sub-network level or at a facility level? Could also apply this thinking to Criticality definition? | Sector Discussion | Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance or criticality | No Specific Reference | More information required for a decision |  | Closed |  | Closed
794 | No Action Required | Potable water | Vol 1 | All three standards use this sentence correct for all 3 waters | Sector Discussion | Please provide further information. | Executive Summary | More information required for a decision |  |  |  | Closed
795 | Completed | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.7 Heirarchy | Change made document updated
796 | No Action Required | Potable water | Vol 1 | Believe there should be a level between asset group and asset type (see my hierarchy tree). Also Asset Class & Asset Category is not specified in the hierarchy. | Sector Discussion | Please provide further information relating to your hierachy. | 1.7 Heirarchy | More information required for a decision |  | Closed
797 | Completed | Potable water | Vol 1 | Defined as Asset Type on previous page | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
798 | Completed | Potable water | Vol 1 | Page numbering out of sequence | Included | Resolved in current version. | 1.8 Theme Structure | Change made document updated
799 | No Action Required | Potable water | Vol 1 | What information is required to determine if a tank/reservoir is a civil structure or not. i.e. How to determine if a tank/reservoir is a containment structure or a retaining structure. | Noted: no action required | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | 1.8 Theme Structure | No action
800 | No Action Required | Potable water | Vol 1 | Will there be reference documents for treatment plant assets? | Noted: no action required | Not at this point in time | 1.8.1 Other Asset Classes in the precinct of a Water Network | No action
801 | No Action Required | Potable water | Vol 1 | How would an asset that could be represented as more than one of these be represented. e.g. would a scour be a single asset (pipe) or two (pipe and fitting) or would that be up to the Client to determine | Sector Discussion | More information is required to inform a way forward | 1.9 Data Principles | More information required for a decision |  | Closed
802 | Completed | Potable water | Vol 1 | water | Included | changed to Water. | 2.1.1 Accuracy Requirements for Locating Assets | Change made document updated
803 | Completed | Potable water | Vol 1 | water code lists | Included | Section under review. | 2.1.5 Attribute Data Fields | Change made document updated
804 | Completed | Potable water | Vol 1 | Definition etc missing | Included | Section under review. | 2.1.6 Attribute Data Type Definitions | Change made document updated
805 | No Action Required | Potable water | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils/contractors to use an ESRI based product, or something else? if not suggest removing ESRI from this sentence. | Noted: no action required | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for | 2.1.7 Metadata Definitions | No action |  | No further action
806 | Completed | Potable water | Vol 1 | Section 2.1.4 | Included | Section under review. | 2.1.7 Metadata Definitions | Change made document updated
807 | Completed | Potable water | Vol 1 | Does this code list include options for multiple networks? or is each network to be recorded as an individual project? | Included | ProjectID already included Yes it does - added multiples in Project Table | 2.1.9 Project Attributes | Change made document updated
808 | Completed | Potable water | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
809 | Completed | Potable water | Vol 1 | See note regarding Design Company above. | Included | Should be A/N. | 2.1.9 Project Attributes | Change made document updated
810 | No Action Required | Potable water | Vol 1 | Should this not be a code list? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | Closed
811 | Included | Potable water | Vol 1 | What is the definition of cost for contractors? What is the value of capturing this when there are no controls around application of defining cost? | Included | Reviewed and Noted for Inclusion Financial code lists for ODRC, ORC and OC are included | 2.1.10 Common Attributes | haydn |  |  |  | Closed
812 | No Action Required | Potable water | Vol 1 | What exactly are the photographic references? This appears to be a 250 Char field so completely useless for using this data. Is this intended to be used in a similar way to 'Unique ID' as a reference number for the photo? | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | Closed
813 | No Action Required | Potable water | Vol 1 | Again using a 250 character field means the data could be all over the place. Example uses this field to record specific instructions to access the asset. To me that should be a separately labelled field. | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes | More information required for a decision |  | Closed
814 | Completed | Potable water | Vol 1 | See note regarding this field on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
815 | Completed | Potable water | Vol 1 | See not for Design Company on page 13 | Included | Should be A/N. | 2.2.1 Area of Work Extent | Change made document updated
816 | No Action Required | Potable water | Vol 1 | Would a T not be a fitting instead of a node? | Noted: no action required | T is a fitting but also an intersection so therefore a node. | 2.4.4 Node | No action
817 | No Action Required | Potable water | Vol 1 | Is there a particular reason that Valves etc do not 'break' pipes? When works are undertaken (renewals in particular) actual physical assets provide useful 'real world' demarcation points. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | 2.4.5 Pipe | No action
818 | Completed | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram |  | Closed
819 | Completed | Potable water | Vol 1 | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe | Modify Diagram |  | Closed
820 | Completed | Potable water | Vol 1 | What are the reasons for Internal Diameter, Nominal Diameter and Nominal Bore all being required? Are these all not essentially the same thing? | Sector Discussion | The range of diameter types are an analytical requirement for interogating assets through a range of lenses | 2.4.5 Pipe | More information required for a decision |  | Change made document updated
821 | Included | Potable water | Vol 1 | Would this class also cover assets that provide access but are not part of a dam or weir wall? Suggest that this be added to the wastewater specification as well. | Included | Agreed 9/3/2017 | 2.3.6 Tunnel | Comment clarifed in potable water document and tunnel asset class added to wastewater document |  | Change made document updated
822 | No Action Required | Potable water | Vol 1 | Should purchase date be included? Do some warranties apply from date of purchase? | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling | More information required for a decision |  | Closed
823 | Included | Potable water | Vol 2 | a' instead of 'the' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
824 | No Action Required | Potable water | Vol 2 | Why is infrastructure for collection and treatment not covered? These assets are integral to potable water supply and asset managers need quality information that they can use to make asset management decisions. Sentence also contradicts itself. "does not cover infrastructure...treatment of water, except in the case of..infrastructure to treat water". | Noted: no action required | There is a desire to create anoter standard which includes these assets, as there is in th ebuilding environment for Large Commercial Buildings and Industrial Buildings | No Specific Reference | No action
825 | No Action Required | Potable water | Vol 2 | Pressure is more of a Quality provision. Suggest moving this into Quality. | Noted: no action required | Pressure is a Design Attribute How it performs against that design is a Design Performance attribute | No Specific Reference | No action
826 | Included | Potable water | Vol 2 | Delete extra "that" | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
827 | Included | Potable water | Vol 2 | outlines' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
828 | Included | Potable water | Vol 2 | investment' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
829 | Included | Potable water | Vol 2 | replace' | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
830 | Included | Potable water | Vol 2 | Influences | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
831 | Included | Potable water | Vol 2 | Replication | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
832 | No Action Required | Potable water | Vol 2 | General comment - risk and criticality are closely linked. Are they really different things? Just use one term and get rid of the other. | Noted: no action required | No action required. Decision to separate two schemas taken at project management level | No Specific Reference | No action
833 | Included | Potable water | Vol 2 | Table is missing a 'comments' field | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
834 | Included | Potable water | Vol 2 | Inconsistent with the wastewater and stormwater measure headings (Rating). Suggest same terminology is used across all three waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
835 | Included | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
836 | Included | Potable water | Vol 2 | Switch could and would. "could" more appropriate for grade 2, "would" more appropriate for grade 3. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
837 | Included | Potable water | Vol 2 | Is this a different manual than the 3rd Edition New Zealand Pipe Inspection Manual? If not use full document name as used in the wastewater and stormwater documents. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
838 | No Action Required | Potable water | Vol 2 | Should this not be in line with the wastewater and stormwater measures? (IIMM 2015) | Noted: no action required | No action required. This is the same document | No Specific Reference | No action
839 | No Action Required | Potable water | Vol 2 | If this information is to be completed by field (maintenance and operations) staff they are unlikely to know if works have been deferred or will be deferred. | Noted: no action required | Not an attribute of these standards | No Specific Reference | No action
840 | Included | Potable water | Vol 2 | Replace "data" with "cost" | Included | Documents have undergone a full publishing edit | Haydn | No action
841 | No Action Required | Potable water | Vol 2 | Stormwater document includes complete code lists for these items. Water and wastewater do not. | Noted: no action required | Code lists updated | List of Code Lists | No action
842 | No Action Required | Potable water | Vol 2 | Not convinced that this is a useful or practical schema, at least for potable water assets. Perhaps don't bother with this and just use demand schema instead? They are similar. | Noted: no action required | Utilisation and Demand are different decision elements as explained in the standards. | 3.2 Utilisation Schema 3.3 Demand Schema | No action
843 | Included | Potable water | Vol 2 | Missing sentence from WW and SW Volume two further explaining the utilisation schema. " Utilisation is measured using time or other base unit measured against a known availability." | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
844 | Included | Potable water | Vol 2 | "Current Utilisation" at an asset by asset level would require an impractical amount of monitoring. i.e. are we really going to know average and peak flows through each and every length of water pipe? | Included | This is an analytical construct, and easily monitored in an analytical sense at whatever frequency required for intervention circumstances | 3.2 Utilisation Schema | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
845 | Included | Potable water | Vol 2 | Partly a function of the pressure in the pipe. Are we really going to know potential utilisation for each and every length of water pipe? | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
846 | Included | Potable water | Vol 2 | Don't think it's possible to determine this for each and every asset. At least for potable water assets. | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
847 | Included | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets without extensive modelling. Alternatively would require data from modelling software. | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
848 | Included | Potable water | Vol 2 | Difficult to determine on an asset by asset basis for water assets | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
849 | Included | Potable water | Vol 2 | This does not seem to be an relevant measure for water demand in a metropolitan situation. | Included | Completed - see Demand section | 3.3 Demand Schema | No action
850 | Included | Potable water | Vol 2 | Criticality varies across all three waters. While a data centre may have a higher water criticality than a hospital, the opposite would be true of wastewater. | Included | Correct, which is why each asst class is treated differently when an analysis of things like criticality are conducted across a network | No Specific Reference | No action
851 | No Action Required | Potable water | Vol 2 | Of risk & criticality, which are both similar schema, criticality is much quicker and easier to measure and much less subjective. I would be tempted to exclude risk or use it with caution in decision-making compared the use of other schema. | Noted: no action required | It will be required n some circumstances, and here it is defined when you do | No Specific Reference | No action
852 | Included | Potable water | Vol 2 | Ln only needs to be 1 due to 1,5 rule | Included | Completed | No Specific Reference | No action
853 | Completed | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
854 | Completed | Potable water | Vol 2 | Even at a score of 3 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
855 | Completed | Potable water | Vol 2 | Even at a score of 3 is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
856 | Completed | Potable water | Vol 2 | Even at a score of 4 this is a pretty major event. Are the scales correctly graduated? | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
857 | No Action Required | Potable water | Vol 2 | Not convinced there is much use in this table, at least for water assets. Most revenue is derived from consumption so would be associated with a meter and the usage of water. | Noted: no action required | No action required. Organisation can choose how revenue is recorded against an asset | No Specific Reference | No action
858 | Included | Potable water | Vol 2 | So this is theoretical revenue? Not actual revenue? | Included | Actual, Forecast and Budget included in financial code lists | Code List 6: Bases of Cost | No action
859 | Included | Potable water | Vol 2 | Delete this text. Captured in the field below. | Included | Completd | No Specific Reference | No action
860 | Included | Potable water | Vol 2 | This whole section is confusing. It's trying to do two things at once. Individual asset attributes and whole of network attributes should be separated out. | Included | Network analytics are completed on individual asset analytical interogations | No Specific Reference | No action
861 | Included | Potable water | Vol 2 | So its not intended to be used for decisions at an individual asset level? If not, strip out all the individual asset measures and move somewhere else. | Included | It is in some circumstances to be used on an individual assetID | No Specific Reference | No action
862 | Included | Potable water | Vol 2 | This table seems to be a jumble of attributes for individual assets and DIA measures which are taken for the network / organisation as a whole. I'm not really sure the whole of network / organisation attributes are metadata. Delete DIA whole of network / organisation attributes or move to a separate table. dlane: Some data items are network wide while others are asset specific. If data capture is required these should be split into separate network and asset tables. | Included | Volume 2 is completed in these draft standards. Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance | No Specific Reference | No action
863 | Included | Potable water | Vol 2 | How does this field work? Is it the duration of the most recent unplanned interruption, the the total duration of all unplanned interruptions (from field below) or the average unplanned interruption duration? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
864 | Included | Potable water | Vol 2 | How does this field work? Is it the connections affected in the most recent unplanned interruption, the total connections affected in all unplanned interruptions (from field below) or the average number of connections affected in unplanned an unplanned interruption? | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | No action
865 | Completed | Potable water | Vol 2 | Delete this field. It makes no sense and is confusing. Field Ref 11.04 does the job. | Included | Table updated | No Specific Reference | Change made document updated
866 | Completed | Potable water | Vol 2 | Need to include the units of measure. kPa,psi etc | Included | Tables updated in code lists of Vol 2 | Code List 44: Description of Design Performance – Engineering Unit of Measure | psi to be added |  | Refer to New attribute or Codelist tab
867 | Included | Potable water | Vol 2 | Surely this field would only be used for a reservoir asset. Not, say, a pipe supplied from the reservoir. Please clarify the use of this field. | Included | It can be both | No Specific Reference | No action
868 | No Action Required | Potable water | Vol 2 | Not sure it would come from Repairs and Maintenance Schema. | Noted: no action required | This MoH included in the Service Performance Attributes | Data Table 11: Service Performance Attributes – Functional | No action
869 | Included | Potable water | Vol 2 | Confusing to have it on this table. So this field is used at a facility level not an individual asset level? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
870 | Included | Potable water | Vol 2 | Confusing to have it in this table. So this field is used at an organisation level? The question of whether there is an adequate backflow prevention programme doesn't relate to individual assets? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
871 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
872 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
873 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
874 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
875 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
876 | No Action Required | Potable water | Vol 2 | This is not a demand attribute, its abstraction/take and is source based. as you've said that this is potable water assets only I don't think it's appropriate here. | Noted: no action required | A source is an asset (e.g. a reservoir), abstraction is the process, demand is the level of abstratcion on the asset - each are different and can apply to a pipe connection no less (e.g. a school) | No Specific Reference | No action
877 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
878 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
879 | Completed | Potable water | Vol 2 | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated?. | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | Change made document updated - to discuss change Minor 'Comments' |  | Closed
880 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. Move to financial schema? | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
881 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not and individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
882 | No Action Required | Potable water | Vol 2 | Differs from tables in the stormwater and wastewater specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Tables are very similar, with the asset specific elements being applied when required. Tables have been normalised where possible | No Specific Reference | No action
883 | Included | Potable water | Vol 2 | Whole of network / organisation measure, not an individual asset measure. | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
884 | Completed | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
885 | Completed | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
886 | Completed | Stormwater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
887 | Completed | Stormwater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Included | Reviewed and Noted for Inclusion | 2.1.7 Metadata Definitions | Change made document updated
888 | Completed | Stormwater | Vol 1 | 2.1.4 | Included | Reviewed and Noted for Inclusion | 2.1.6 Attribute Data Types Definitions 2.1.7 Metadata Definitions | Change made document updated
889 | No Action Required | Stormwater | Vol 1 | Does this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Noted: no action required | Either | 2.1.9 Project Attributes | No action
890 | Completed | Stormwater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
891 | Completed | Stormwater | Vol 1 | See note regarding Design Company above. | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | Change made document updated
892 | Included | Stormwater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision |  |  |  | No further action required
893 | Included | Stormwater | Vol 2 | Heading (see water and wastewater) | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
894 | Included | Stormwater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or at code should be a single character as per the water measures. Should be consistent across all 3 waters | Included | Consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
895 | No Action Required | Stormwater | Vol 2 | Differs from table in wastewater and water specs. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
896 | Completed | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | General | Change made document updated
897 | Completed | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.7 Heirarchy | Change made document updated
898 | Completed | Wastewater | Vol 1 | Page numbering out of sequence | Included | resolved in updated version | 1.8 Theme Structure | Change made document updated
899 | No Action Required | Wastewater | Vol 1 | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence | Noted: no action required | Not the intention. The intention is to outline why the field is structured in this way | 2.1.7 Metadata Definitions | No action
900 | Completed | Wastewater | Vol 1 | 2.1.4 | Included | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | 2.1.7 Metadata Definitions | Change made document updated
901 | No Action Required | Wastewater | Vol 1 | Doe this code list include options for multiple networks? Or is each network to be recorded as an individual project? | Sector Discussion | This is an operational question related to an organisations ability to import data into their asset management systems. For immature organisations likely to be project by project, for mature ones project agnostics | 2.1.9 Project Attributes | More information required for a decision |  | Closed
902 | Completed | Wastewater | Vol 1 | Some companies include a number in their name. Alpha/Numeric instead? | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
903 | Completed | Wastewater | Vol 1 | See note regarding Design Company above. | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | Change made document updated
904 | Included | Wastewater | Vol 1 | Should this not be a code list? | Included | More information is needed for a way forward | 2.1.10 Common Attributes | More information required for a decision |  |  |  | No further action required
905 | Included | Wastewater | Vol 2 | Not a valid measure for wastewater utilisation. | Included | Updated | No Specific Reference | No action
906 | No Action Required | Wastewater | Vol 2 | Criticality varies across all three waters. for example, for wastewater a hospital would have a higher value than a data centre. while water could score differently | Noted: no action required | No action required, based on the importance of the building as defined in the Buildings standard | Code List 13: Facility Importance Rating |  |  | Closed
907 | Included | Wastewater | Vol 2 | Heading is different from that used in water and stormwater documents. Suggest standardising for simplicity. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
908 | Included | Wastewater | Vol 2 | Length will not allow for KPa or l/s to be used. Either this should be extended or code should be a single character as per the water measures. should be consistent across all 3 waters. | Included | Documents have undergone a full publishing edit | No Specific Reference | No action
909 | No Action Required | Wastewater | Vol 2 | Differs from tables in the stormwater and wastewater spec. Most/all of these measures should be applicable across all three waters. | Noted: no action required | Consistent across all standards, documents have undergone a full publishing edit | No Specific Reference | No action
910 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | An obvious mistake in the Potable Water Metadata Std is that someone has put the Residential Executive Summary in it????. | Included | Included in the draft Standards | Executive Summary | Change made document updated |  | Change made document updated
911 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | You are asking for public to comment on missing attributes within meta data tables. Considering you have spent 12500 hours on this, could you please comment if all the attributes defined by Australian standard ADAC have been included? http://engicom.com.au/adac/government-organisations I appreciate your list of assets may be more comprehensive. If any of the asset attributes defined in ADAC are missing there are like to be areas where assets will miss vital information for future analysis. If you have used IPWEA in your decision making process it would be useful to include this information on your website so it doesn’t look like you are reinventing the wheel. Well done on sorting out the asset management data through the lifecycle of each asset. Local councils desperately need national standard for asset capture, storage and access to information. | Included | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. | General | No action
912 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | I’d like to provide feedback on the proposed standard. However I caveat this as coming from a hands on GIS Practitioner View, which may be different to my colleagues here at LINZ. I think it will be incredibly important to incorporate good practice guidance at some stage on how these standards are practically implemented. Ideally providing an empty or working dataset that a person can take, open with their system and populate. Generally when you go to create the schema in a system you’ll follow it and interpret changing the types, field lengths, column names etc. My request is based on recent experience. Often this step is left out, and implementation of the standard fails. This was my experience with the ANZLIC geospatial metadata standard, 10 years after its release 95% of GIS practitioners in New Zealand could still not easily implement the standard within the most common desktop GIS software. The Australian based tool provided did not support NZ requirements. We ended up shoving the required text into a single desc field in an inappropriate manner, ending up with a total mess. This may require getting software providers onboard with adding these into their pre-defined templates for users of the most common software providers. If you could imagine in the same way we create a LINZ letterhead letter in MS Word. My 2 cents from a GIS data capture perspective and I am happy to discuss this further if appropriate, otherwise happy to leave it as this. | Noted: no action required | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | N/A | No action
913 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | In each of these documents out for proposal, there is reference to standard codes for things like asset type and material (“the CODELIST”), but none of these are available yet – will this be available before consultation closes? | Included | Code lists are included Attributes to be discussed | General | Gauge input from next review |  | Gauge input from next review
914 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | This is a great initiative and will aid everybody involved in the area of Asset Management. I would ask is has there been any coordination with the Institute of Public Works Engineering Australasia as they have a system already in place called ADAC (http://www.engicom.com.au/adac). Could your framework be an extension to that so we can leverage what software companies have developed already to support that schema. It appears that a lot of the info you are capturing has already been covered, why reinvent the wheel? | Noted: no action required | IPEWA Australisia has representation around the table, and has had for 2 years | N/A | No action
915 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Structure of the standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes. Further to the split of water sectors there is an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group has specified that a single document that focusses on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. In terms of usability our end users are expecting a data framework that is easy to understand and use. In the proposed layout we are expecting the standards will be met with cost burdens. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
916 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | 2. Applicability of volumes 1 and 2 The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was about creating an as-built data set for industry that can be used to collect field data, most of the workshops evolved around this input. Volume 2 for derived data has had limited industry input and we do not believe it is ready to be published. Further work on this volume is therefore required. | Noted: no action required | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. | General | No action
917 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | 3. Data hierarchy The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. As presented at the workshops, an example of how this could be applied to the tables is outlined below: Level 0 (system/layout specific data – master data. Typically assigned by organisational systems and numbering or coding rules - contains the common data set) -Inventory identification number / -Functional location i.e. Network type (water, wastewater, stormwater) / -etc. Level 1: Data categories, in example: “Technical/physical” i.e. Containment structures (available technical core classes) (or) Operational data (or) Financial data etc. Level 2: (attributes) Minimum required attributes, in example: -Function / -Depth / -Material / -etc. Level 3: (attributes) Conditional attributes, in example: -Diameter if circular / -length and width if not circular / -Joint type (if the structure has joints) / -etc. Level 4: (attributes) Optional attributes, in example: -Manufacturer / -Model/part number / -etc. | Included | Asset Classifications have been defined in the Standards Tables are to be discussed at length | No Specific Reference | Sector discussion |  | Closed
918 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | 4. Terminologies and definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need to be agreed. | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | No action
919 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | 5. Graphical representation and its accuracy This subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. Graphical representation should be removed from the document; the purpose of this standard is collecting metadata of asset physical properties. Geospatial requirements are a standard in its own right and even providing these as guidelines does not seem appropriate. | Included | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH | General | No action
920 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | 6. General content 1.“Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. 2. The units of measure have not been covered during the workshops. Further input may be required before the draft is ready for public release. 3. Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and the implementation may not be practical. 4. Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. In many instances data will be collected in-house. 5. Australian examples and photos should be replaced by New Zealand examples. Word choice such as “savvy” (used often) is not the best choice. Some of the language used needs to be reviewed in order to retain the standard’s professionalism. | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included | General | No action
921 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | 7. Implementation The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate has not been considered where organisations may choose not to collect certain information for low risk assets. An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard | Noted: no action required | This is not within the scope of these standards | N/A | No action
922 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | We believe there is a reasonable amount of work that has not been completed, such as standard definitions, which may lead to inconsistencies between the water organisations. Without this work being completed the documentation that has been produced could only be used as a guideline or a code of practice. | Noted: no action required | All definitions have been standardised and normalised | No Specific Reference | No action
923 | Completed | 3-Waters | Vol 1 & Vol 2 | However, page 141 of Potable Water Volume 1 As-constructed/As-built references code lists for 3 waters assets that can be reviewed in a supplementary document called 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016 Is this document available for download or can it be emailed to me? I would like to cross-check what is in this code list against the attribute tables to assist with my review. | Included | Code lists are included | General | Change made document updated |  | Change made document updated
924 | No Action Required | 3-Waters | Vol 1 & Vol 2 | As-constructed schema should not be a separate document, and should recognize that many assets are created though term contracts not just greenfield build. We should not separate “as-constructed” from other elements of the standard because this perpetuates last century’s practice of asset management being about the asset whereas it is about the service enabled by the asset. We should modify the “as-constructed” schema to recognise that construction happens both in new builds and in renewal term contracts and the information should support both efficiently. I am not convinced of the value of separating the standards into two parts. While as constructed data is central to an asset information system there are few transactions that use it in practice. Most construction projects will use subsets of the inventory tables, performance based construction projects will also use the condition and performance tables, term PPP or BOOT contracts will use almost the entire standard. This means there is no one to one connection between projects and elements of the entire data schemas so the split of the source documents is artificial. I think there is a serious downside to separating the two documents that drives us towards a combined view. Asset management is all about delivering services that require significant assets. Separating as-constructed from performance data perpetuates past practice that asset management was about having assets in good condition, whereas it is about having assets in sufficient condition to deliver targeted services. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
925 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Another challenge with this proposed separation and the associated “constructor” reference fields is that for roads and 3 waters, though to a lesser extent buildings, much infrastructure is created through renewal or replacement programmes. For example for State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. This means that we need to think seriously about replacing the “constructor” record in the “as-constructed” table with a reference to an “Asset Intervention” record as described elsewhere in my comments. Unless this is done there will be not be normalisation of records relating responsibility for modification of inventory, a ridiculous amount of duplicate records created from term contracts where much inventory is created, and a mismatch between the constructor records in the “as-constructed” schema and those of the maintenance schema, when in term network management contracts these are the same constructor. The same duplication will occur when the same constructor creates many inventory records as occurs in term contracts | Noted: no action required | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | No Specific Reference | No action
926 | Included | 3-Waters | Vol 1 & Vol 2 | The categories of data type should be simple, exhaustive and mutually exclusive so should vulnerability and resilience stand alone? The proposed “global meta data schemata” classifies data into several categories. This is a necessary and good thing because it help users appreciate the scope of the data and find the elements they may be interested in. To do this well the elements must be simple, described in commonly understood language, cover the field of interest, i.e. be exhaustive, and be mutually exclusive, i.e. not have definitions that overlap or require subtle nuancing. | Included | Included in the draft Standards | General | No action
927 | Included | 3-Waters | Vol 1 & Vol 2 | Vulnerability - risk There is an open question in the document as to whether vulnerability should be drawn out as a standalone data category, when it influences risk. I do not think it should be standalone because this then makes “risk” become “risk other than vulnerability” and I think that is a bit silly. I certainly agree that vulnerability is important. I think it so important that we should draw it out in the risk or resilience categories. The high level approach to risk is to consider likelihood and consequence. Simplistically consequence conflates: • vulnerability of service, and • impact from reduction or loss of service and vulnerability of service conflates: • vulnerability of infrastructure (considering network effects), and • availability of alternate infrastructure or alternate services. I think we should draw out these or similar elements of risk for those elements of infrastructure type that potentially have a consequence greater than tolerable. This might mean (in the transport context) arterials and above in a transport world because of their importance to the economy and society. Effectively this creates a level of service gap around vulnerability, the very gap that rental companies advertise as being closed when they proclaim on their hoardings that a building to let is 85% EQ code compliant. | Included | Included in the draft Standards | 4.2 Vulnerability Schema | No action
928 | Included | 3-Waters | Vol 1 & Vol 2 | Resilience - performance Resilience is a service level, or a strategic goal. As a service level it should be within the performance elements of the data standard. I know that it has prominence because it is an important element of performance, but so too are accessibility and safety for transport, or availability of supply or health for water. As a strategic goal it is a driver of service levels. | Included | Resilience is a state and requires measurement The level of service is subject to the level of service any organisation seeks to apply, and an invetment plan to meet that level | 4.5 Resilience Schema | No action
929 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Utilisation is multifaceted and requires enhancement The definition of utilisation given in the draft standard is the proportion of an assets available capacity that is actually being used. I think that there will need to be some clever messaging to ensure that the unit of capacity chosen is understood for infrastructure in different circumstances. Using a transport example provides an illustration of this. Over 60% of New Zealand’s roads are classified as access or low volume access roads. This means that they have less than 1000 vehicles using them per day. A single lane has a capacity of about 1400 vehicles per hour, depending on its configuration, i.e. on the proposed definition of capacity most roads have a daily utilisation of about 1.5% yet these roads represent the last and/or first mile of most trips and so are critical to our economy and society. The level of utilisation will always be low simply because there are rural and urban areas with low population that are connected to market or work place. Even with planned intensification of central urban areas daily utilisation might only rise to 5%. This is analogous to the smallest element of supply or removal for potable or waste water. Also, where there is suppressed demand because demand exceeds supply, e.g. on congested transport networks (whether roads or busses), we may report 100% utilisation, but that is bad because the potential benefit of suppressed trips is being lost or costing more. In a water example we may constrain the development of business when supply is inadequate for development yet fully used by current development. Together these factors mean that we have to be careful about the utilisation measure and how we use it alongside other measures at a local and network level, a simplistic approach won’t do. I think this section of the draft standard needs work to draw out these issues. In addition we need to consider how utilisation and performance metrics are used to optimise asset investment decisions. | Noted: no action required | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | No Specific Reference | No action
930 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Inventory Interventions At the moment there are two types of works records, those recorded as maintenance and those associated with the as-constructed fields. I think we should consider what we want from the recording of “works” or inventory interventions because I expect that will lead to an improved data structure with one form of works interventions record. | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
931 | Included | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Planned, current, completed or abandoned works so we can fuel the nationwide forward and current works viewer enabling better coordination of works and reduced disruption of customers whether the works are construction, renewal or maintenance. Interventions on inventory are a process that creates or modifies inventory. Much information is required about the process as much as of the fact that it creates inventory. E.g. the forward works viewer being developed to display proposed and current works have time, duration, and place elements of information as well as descriptive information about the constructor and infrastructure being modified or created as reflected in the proposed “as-constructed” schema. | Included | Statement noted. Already done in Repairs and Maintenance schema. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
932 | No Action Required | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Responsibility for management of infrastructure, noting that ownership may pass to a client when inventory enters service, but responsibility for maintenance may extend beyond the transfer date | Noted: no action required | Noted | No Specific Reference | No action
933 | Included | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • A hierarchy of works and tasks that distinguish a term contract (or work) from a work task within it so that the work identifies responsibility, type of work, stage of work etc, and the task the date and type of work done linked to the infrastructure impacted. I think this allows better alignment with supplier’s management systems, responsibility for work done, and supports many forms of contract from term based contracts to single task contracts. This also enables security to be built into system for data exchange. This is important because for most infrastructure networks (buildings aside) most new infrastructure arises due to renewal works and not due to greenfield construction. | Included | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
934 | Included | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
935 | Included | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
936 | Included | 3-Waters | Vol 1 & Vol 2 | I think inventory intervention (or works most commonly) records should reflect or create: • Types of inventory intervention with appropriate records, including, but not limited to: o Physical works, probably the most common type o Waste or abandonment, associated with infrastructure being removed from the inventory and reflected in a valuation as a write-off o Inventory received from third parties, e.g. as a result of transfer from development of a new residential area to a council, or the transfer of responsibility of a road from a local authority to the Transport Agency as a State highway o Inventory transferred to third parties, e.g. the transfer of responsibility of a previous State highway to a local authority on completion of a State highway bypass. I acknowledge that “inventory interventions” is not the best term and that a better one should be found. | Included | Included in the draft Standards | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | No action
937 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Assessments There is an opportunity to introduce a concept of an intervention type of “Assessment”. This arises because there are many instances where responsibility for some parameter in many of the tables is explicitly referenced, yet is essentially the same information in each case. This information is who changed the parameter, when, why, as a result of what process…? This proposed approach will enable normalisation of data describing the assessment of condition or performance (whether current or forecast), valuation, risk or any other metric in a standard way. It will then identify the provenance and responsibility for each. This proposal is much the same as that for “inventory interventions” in that it suggests that the core information is about the process leading to the metric in the data and this should be recognised. | Noted: no action required | Assesments are (or interventions) are subject to the element being interrogated (e.g. condition). The standards have attributes which capture these. These will however be predominantly the focus of the work when develop-ing Volume 3 | Data Table 1: Condition Attributes & Code List 17: Condition Rating – Methodology | No action
938 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Supply of as constructed data I think that we shouldn’t mandate the form for the supply of as constructed (or other data) but rather the relevant metadata describing its provenance, quality etc. If the form is mandated then it would require an absurd level of record keeping and compliance from term contractors who create many new assets. E.g. for State highways we use term contractors who create the vast majority of new surface infrastructure each year. For State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. Suitably qualified and quality assured staff from contractors enter the as-constructed data directly into our inventory system, and this isn’t shown as an acceptable method of delivery yet it patently is. One of the purported benefits of meta-data standards is that it enables business to business transfer of data. Defining the transfer of data on a disc seems to fly in the face of these benefits and the advance of B2B technology. Similarly I would think that NIU doesn’t want to be involved in contractual requirements for each form of contract, rather whether information is being managed well and is fit for purpose. I think the supply of data section starting on page 1 of volume 1 needs review. | Noted: no action required | Data format (form here) is not within the scope of these standards | General | No action
939 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Asset management I think the sections of the standard on asset management need a revision to better reflect: 1. That customer service at least long term cost is the goal, and not maintenance of asset condition, noting that the two are related. 2. Investment decisions made in a customer service centric world. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
940 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Customer service focus The various diagrams, for example figure 3 on page 24 of volume 2 is written in very economic language around the return for investment of public funds. This is of course critical, but loses the narrative that relates providing customer service that is economic. | Noted: no action required | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. | No Specific Reference | No action
941 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Customer service focus: I think the steps in the above referenced diagram, and the description on the preceding pages are missing an element and that is what is being targeted in terms of service levels and how this target is established. Or alternatively (as a poor second best) are missing the inputs describing the economic and social benefits of different service levels experienced by customers. If these were present then the analytics could do the required work. This step is required to establish the performance targets referenced in the performance elements of the standard. Eg what is the optimal economic service level for service outages considering investment to reduce the frequency, duration and impact of service outages against the social and economic impacts of these. This step is difficult and complex but needed none the less. It requires decisions about the relative weight to be given to quasi commercial models or economic models. It requires significant analytics to be undertaken to determine the relationships between costs and benefits of different levels of service for different types of customers in different circumstances. Much of these analytics are represented in the economic evaluation manual used to determine the economic value of transport proposals in New Zealand. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | No action
942 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Customer service focus: The service led approach enables a more informed discussion with customers about expectations of service level and the cost of these than a black box economic model. It essentially proposes a three stage approach: (See figure in word document) This recognizes that information is never perfect to enable ideal one off analytics because customers’ needs, systems and contexts change so what might be optimum now likely won’t be at another time. The aspect of service level target should be reflected in the analytics framework. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. | No Specific Reference | No action
943 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world I think that section 1.8 needs some rework though many aspects are worth keeping. There is significant reliance on the metaphor that as assets deteriorate and consequently the maintenance expense to sustain targeted service levels increases there is a sweet spot between condition and maintenance cost. I think we need to recast that metaphor in a customer centric world and recognize that the sweet spot is tautological because the definition used for condition grade 5 is that it has failed or soon will so it is no coincidence that replacement is needed there. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
944 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world The proposed standard presents a theoretical approach to stochastic analysis. This style of analysis is becoming common place. The standard might reference the UK’s Highways Efficiency Maintenance Programme website, especially this url: http://www.highwaysefficiency.org.uk/efficiency-resources/asset-management/life-cycling-planning-toolkit.html That site includes standard tools for “stochastic analysis” of renewal programmes using the “5-step condition rating”. While the text is all about roads the processes are generic. With translation, or a babel fish (as Douglass Adams might say) they are as applicable to buildings as to roads. The tools on that site are of course single factor analyses as condition based analytics generally are. There is no single or multifactor customer service optimisation (e.g. skid resistance and ride comfort for roads) that assists planning in a constrained environment or in an environment where value for money matters, but it is a straight forward approach to estimating the works required to sustain performance. That reference, or a more applicable one, or a derivative of it, would go some way to making the theoretical text in the proposed standard tangible. | Noted: no action required | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
945 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If the text were recast to be more customer service centric it might use the following approach. The two most important decisions to intervene with some form of monitoring or works when managing a network to provide customer service are: 1. When delivered service levels have or will drop below the targeted level or there is too great a risk that they will 2. When, despite the targeted service level being met, it is cheaper in the long run to intervene, or there is an unacceptable risk that costs will rise unless an intervention is made Intervention decisions can initially lead to a monitor, maintenance, renewal or improvement interventions, whichever is part of the least long term cost intervention strategy. A more colloquial way of putting this is only intervene if its broken, or cheaper in the long run. | Noted: no action required | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
946 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world Transport examples of the two decision types are: Ensuring the service is delivered to target. • Replacing the tires on your car when the tread depth has reduced and become unsafe, or ahead of winter when risk is greatest when tread depth has almost become unsafe • Continuing to monitor the change in direction of a river beside a roadway that may ultimately risk scouring of the road formation in order that preventive works can be taken when necessary and most cost effectively to preserve the transport route • Water cutting the excess bitumen off a road to restore the prominence of the chips so tyres grip these rather than “float” on the water film when the road is wet in order to restore the skid resistance of the road surface. • Resurfacing a road when the skid resistance of a road is falling and is either unsafe or will become unsafe before the next opportunity to intervene because the stones have polished Ensuring that delivery of the service is at the least possible long term cost. • Replacing the oil in your car engine even though it is performing well in order to forestall engine damage • Monitoring the condition and maintenance expenditure on deteriorating roads so that and expected renewal works can be designed and timed to be cost effective long term • Sealing cracks in an asphaltic concrete road surface to reduce water ingress to the pavement which would cause the pavement to deteriorate rapidly and require more expensive repairs • Rebuilding or replacing the structural layers in a pavement when this is the cheapest long term cost because deterioration in pavement strength is leading to the need for significant and increasingly frequent and costly repairs and resurfacing treatments to maintain service levels | Noted: no action required | And, is the intention of the analytical foundations set down for Volume 4. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
947 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Investment decisions in a customer centric world If discussion of the type inferred in the above table were included then the standard would be more tangible to users and better focussed on customer service, the goal of asset management. I think it worth the discussion including reference to or guidance on the economic decision to continue to maintain infrastructure or to renew or replace it on a site specific basis. The IIMM might be suitably referenced. When funds can be used on other investments outside asset management of the infrastructure in question then we look for the sweet spot where the net present value of the renewal plus reduced subsequent maintenance stream is better than the present value of the continued and increasingly expensive maintenance stream. This should be included because it can be implemented site by site for significant investment, and needn’t rely on sophisticated network level analytics and data, though it requires some to describe the relationship between condition, time and maintenance cost. This analysis that maintenance costs typically increase as condition worsens is shown in the following indicative diagram as indicated in the draft standard metaphorical diagrams. This shows there isn’t a sweet spot from this relationship alone. Another factor is required for optimisation and that is the present value of the replacement cost option on a site specific basis, or long term budget on a network basis. (see figures in word document) | Noted: no action required | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
948 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Global Schemata The global asset metadata schemata diagram on page 16 of volume 2 appears out of place with the prosaic listing of detailed data requirements. If it were fully developed as an idea in the text you would expect it to tell a story about why certain data elements are required. No such story is conveyed, so the inference is that whatever data is in the standard will enable such analysis, if that were true then the benefit of the advanced analytics would be small. That seems odd. Does this description add value? | Noted: no action required | The diagram provides context for the detail that follows There are some who are already applying this level of complexity to decision-making. | 1.4 Context of Asset Data and Analytics | No action
949 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Network level performance targets The standard for service performance p101 vol 2 as proposed enables the measurement of performance against a target. This is good. However there is no reference to what good looks like so the measurements are just that. It may be useful to add records that: • Enables the categorisation of target service levels • Set service targets for each performance aspect for each category This would provide the data required to enable reporting of whether the service provided was good enough or not, in a situation where targets differ by category. The One Network Road Classification framework developed by REG for transport classifies roads into 8 categories and sets targets for each. | Noted: no action required | Levels of service are policy decisions, and are not within the scope of these standards However, where organisatoins provide these levels, these standards will attribute them and analyse them for decision-making purposes | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
950 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Financial Performance The standard has sections on p88 vol2 and succeeding pages. It would be beneficial to review common good practice to understand what data elements should be here. The Australian Infrastructure Financial Management Guide is one such reference. Here as elsewhere the tables can be normalised by reference to an assessment record as proposed above, the type here being valuation. In addition I would have thought there would be considerable opportunity to normalise valuation approaches by assigning each asset a valuation type, and that type record containing the depreciation rates etc. applicable to it. I am not sure that the valuation section has been fully developed yet because some thought must be given to valuation components being different to asset register components. There is no need for them to be the same as they have different drivers. This sections contains data about construction cost that will be transferred to the “as constructed” tables. It asks that the cost of an asset be supplied and that supply is mandatory. However there is a challenge with this because almost all construction contacts cost elements at a higher level of aggregation than each asset. E.g.the construction of a sewage treatment plant does not lead to an estimated cost per inventory item created. Contracts with lump sum maintenance items likewise have no costs per maintenance work task. Therefore a review is required of how costs are acquired and stored and at what level. I suspect that it will be best to capture financial information at the financial/contractual transaction level and activity at the inventory affected level. The concept proposed above for having transactional records for works and tasks enables costs to be collected at that level. | Noted: no action required | There is an opportuity to reflect on the tables and code lists provided in the standards. There are some analytical assumptions being addressed here, which are for the analytics in which will be unpacked in more detail in Volume 4. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups |  | Closed
951 | No Action Required | 3-Waters | Vol 1 & Vol 2 | Information required to manage well varies by criticality of network and context I expect that, as with roads, the information needs of managing a water network in a simple undemanding context differ from those of a demanding context. While the performance metrics around health and availability may be common the needs for sophisticated infrastructure and condition metrics would differ. Similarly the information needs for the critical elements in a complex network would be greater than for other elements. This would lead to a hierarchy of mandatory fields based on context. I think this should be considered. | Sector Discussion | To discuss | 5.4 Service Performance Schema | No action
952 | Included | 3-Waters | Vol 1 | pg 3: Validating the data submission: is this to go against each asset or an organisational process requirement? | Included | Against each asset and against each attribute | General | No action
953 | No Action Required | 3-Waters | Vol 1 | 1.8 They are requesting that “each asset type must be delivered on a separate level/layer and the files must be clearly labelled…” If this is in a CAD format this makes perfect sense, but then the attribute information that is being requesting won’t be able to put against the individual asset (when last I tried this, it can only be done with blocks, and blocks can be tricky to convert to a shape file). But if in a shape file format, it is a bit of an overkill, it is structuring back to the way we used to have it. And we will need to combine the information in order to import into Assetfinda. it is also implying that information from contractors will be to a High enough standard that we can suck it into our GIS and all points and lines will meet perfectly. In a perfect world that would be great, but from having a draughing background. I can guarantee you are going to get hydrants, valves etc. not matching perfectly with your pipes (this comes from the skill of the person doing the as built) and greater maintenance issues later. We would be relying on the project managers to insist on high quality as built. This then brings up the issue of disposals of existing infrastructure. Or the assigning of asset id numbers that have intelligence. | Noted: no action required | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | 1.8 Theme Structure | No action
954 | No Action Required | 3-Waters | Vol 1 | 1.11 Projects will need to be on board with this. | Noted: no action required | Noted, but out of scope. | 1.11 Acceptance Testing | No action
955 | Included | 3-Waters | Vol 1 | 2.1.1 Precision needs to be clarified on what is acceptable. | Included | Precision is defined in the standards | 2.1.1 Accuracy Requirements for Locating Assets | No action
956 | No Action Required | 3-Waters | Vol 1 | 2.1.5 In the proposed structure, the data Code list fields will be limited to 10 characters, this is not going to allow us to use unabbreviated materials e.g.: uPVC instead of PVC Unplasticised. We need to decide on this now as it affects the look up tables and associated finance. | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the Full Name once the asset data is provided. | 2.1.5 Attribute Data Fields | No action
957 | Awaiting Implementation Phase | 3-Waters | Vol 1 | 2.1.8 The attribute fields they are suggesting may impact on Assetfinda fields e.g.: they are the same but have different criteria. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
958 | No Action Required | 3-Waters | Vol 1 | 2.4.1 For Access chamber of valves they are requesting one location point, which is what we have and one polygon of the same area representing a plan view of the valve pit. We have over 2000 valves, that is a lot of additional files, and I feel a duplication of work, as the plan view can already been seen as a schematic when viewing the reticulation. - The same as above goes for Storm water | Sector Discussion | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | General for Access Chambers and Valves | More information required for a decision |  | Closed | Large assets like the ones being described here ought to use drawings and operations manuals (referenced). Much like pump stations we collect a certain amount of information, after that, it is agreed we go to the original data source.
959 | No Action Required | 3-Waters | Vol 1 | 2.4.7 Says that pump stations should be a polygon feature and all attributes are to be attached to this polygon. Then in 2.5.2 which refers to Pumps it requires pumps to be a point feature with all attribute information attached to this point. So which is it. The Pump station, the pump, or both? - The same as above goes for Storm water | Noted: no action required | The pump station refers to site specific information. The pump is the asset specific information. | General for Pump and Pump Station | No action
960 | No Action Required | 3-Waters | Vol 1 | 2.6.2 Cathodic Protection- I don’t know what that is. | Noted: no action required | This refers to systems installed to protect water mains from corrosion. | 2.6.2 Cathodic Protection | No action
961 | No Action Required | 3-Waters | Vol 1 | 2.8.2 This puts all the responsibility on the contractor to provide all the specified information in the way the document wants it, with us only needing to import it. - The same as above goes for Storm water | Noted: no action required | It also puts the responsibility on the asset owner to specify it properly | General | No action
962 | No Action Required | 3-Waters | Vol 1 | All the attributes that are being requested of us seems to me to be a lot more information than will ever be needed or used, but if supplied by a contractor as suggested, is achievable. | Noted: no action required | Noted, for analytical purposes | General | No action
963 | No Action Required | 3-Waters | Vol 1 | Waste Water seems to be a repeat of the above. | Noted: no action required | Repeat | General | No action
964 | Completed | Potable water | Vol 1 | In Summary The main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed potable water assets as defined by asset managers in New Zealand. While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant. It’s not clear who is meant by consultants here. | Included | Note added in glossary 9/3/2017 | In Summary | Change made document updated
965 | Completed | Potable water | Vol 1 | The objective of the specification in Volume 1 is to provide geospatially savvy potable water asset “As Manufactured” and “As-constructed / As-built” digital data. The objective of the specification in Volume 2 is to provide geospatially savvy potable water asset “As Managed” digital data. I don’t like the use of the word savvy | Included | Reviewed and removed | General | Change made document updated
966 | Completed | Potable water | Vol 1 | Table 1.8 doesn’t appear to include an allowed category or descriptor for “back-flow preventer” | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | 1.8 Theme Structure | New Code List Entry proposed | Back-Flow Preventer | Refer to New attribute or Codelist tab | Include 'Backflow preventer' as valve type Is there a difference btn backflow preventer and a non retrn valve - AWAITING FURTHER INFORMATION TO CLOSE OFF
967 | No Action Required | Potable water | Vol 1 | I presume in Table 1.9 that “N” stands for No. I’m sure there will be some exceptions to the rule per asset | Noted: no action required | Reviewed and Noted only | 1.9 Data Principles | No action
968 | No Action Required | Potable water | Vol 1 | 2.1.1 The explanations on pages 6 and 7 between absolute accuracy, relative accuracy and spatial precision are useful; however I think the sector needs to derive one preferred conceptual practice i.e. is absolute accuracy more important than relative accuracy? Whose data set has primacy? E.g. LINZ spatial data with asset data associated by relative accuracy? | Noted: no action required | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | 2.1.1 Accuracy Requirements for Locating Assets | No action
969 | No Action Required | Potable water | Vol 1 | I agree with the QA Validation field being a mandatory attribute in Table 2.1.5 | Noted: no action required | Reviewed and Noted only | 2.1.5 Attribute Data Fields | No action
970 | No Action Required | Potable water | Vol 1 | Not all fields in the project attribute table in 2.1.7 are practical. What about a project that is geographically separated (relining different pipes) or across different asset classes? (e.g. water mains and sewers) | Noted: no action required | Reviewed and Noted only | 2.1.9 Project Attributes | No action
971 | No Action Required | Potable water | Vol 1 | 2.1.1 Pg 17 . Ditto for “Area of Work” extent. | Noted: no action required | Reviewed and Noted only | 2.2.1 Area of Work Extent | No action
972 | No Action Required | Potable water | Vol 1 | 2.3.1 How will an open civil structure be represented? E.g. a settlement pond | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | 2.3.1 Containment Structure | More information required for a decision |  | Closed
973 | Completed | Potable water | Vol 1 | The repetitive use of the generic term “Health & Safety Issues” in the respective attribute tables should be revised to documented Health & Safety Risks. Or similar | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure trigger there are 'special circumstances'. A code list is proposed | General | More information required for a decision | Health & Safety Type | Closed
974 | No Action Required | Potable water | Vol 1 | I’m unsure what the use of a “Resilience field (as an open text field?) is in these tables. Too much variability and not enough guidance around what data and format to enter. This is an AM (Vol 2) derivation anyway and not an “As-Built” attribute in my view. Whereas “Design Life” is. | Noted: no action required | Resilience Rating is a measured a6ttribute | 4.5 Resilience Schema | No action
975 | Completed | Potable water | Vol 1 | 2.3.4 The term Well should be changed to “Bore” | Sector Discussion | Commented on this previoulsy | 2.3.4 Well | More information required for a decision |  | Closed
976 | No Action Required | Potable water | Vol 1 | 2.4.3 The point feature is to be “snapped” to the pipe asset it is associated with. Does the spatial representation snapped to the polyline create a node? If not then this creates problems when modelling. | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed | 2.5.3 Valve | No action
977 | Completed | Potable water | Vol 1 | 2.4.5 How is a locator cable or Intrinsic Protection (IP) cable for anti-corrosion ruining with a pipe (e.g. taped to the pipe) to be represented? Why in the table do we have to submit pipe diameter, nominal diameter, external diameter and nominal bore? This is overkill and one wrong piece of information will lead to confusion i.e. which one is the correct one? | Sector Discussion | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | 2.4.5 Pipe & 2.6.2 Cathodic Protection | More information required for a decision |  | Closed
978 | No Action Required | Potable water | Vol 1 | 2.4.7 Should the spatial representation include and ancillary works e.g. dry wells, wet wells, filters, air scrubbers or bio-filters (more applicable to wastewater PS I realise) | Noted: no action required | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. | 2.4.6 Pump Station | No action
979 | No Action Required | Potable water | Vol 1 | 2.5.2 Pumps, can take many types and forms. I trust the fields in the table are flexible enough to accommodate the variety to be expected. | Noted: no action required | We hope so. This will be tested during the pilot phase | 2.5.2 Pump | No action
980 | Completed | Potable water | Vol 1 | Is a backflow preventer to be considered a mechanical equipment asset or a valve? | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | 2.5.1 Equipment & 2.5.3 Valve | More information required for a decision | Back-Flow Preventer |  |  | Closed | Included as a Valve
981 | Awaiting Implementation Phase | Potable water | Vol 1 | 2.6.1 Electrical asset – table doesn’t look accommodating enough for the variety of electrical fittings and assets to be expected | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | 2.6.1 Cabling | More information required for a decision |  |  |  | Closed | To be resolved during implementation
982 | No Action Required | Potable water | Vol 1 | 2.6.2 Good to see Cathodic Protection systems included. | Noted: no action required | Reviewed and Noted only | 2.6.2 Cathodic Protection | No action
983 | No Action Required | Potable water | Vol 1 | 2.8.2 reporting Mismatches could be problematic depending upon the spatial base used – see 2.1.1 above. | Noted: no action required | Reviewed and Noted only | 2.8.2 Matching to Existing Infrastructure | No action
984 | No Action Required | Potable water | Vol 1 | There are a heap more Definitions that could be added to the Glossary e.g. “trunk main” for starters. | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Glossary | More information required for a decision |  | Closed
985 | Completed | Potable water | Vol 1 | Request for code lists: On page 158 of volume 1 of the potable water standard there is mention of supplementary document 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016. Even though this document is in draft, I’d really like to take a look at it. Can it be made available for download, or am I to a copy emailed to me? | Sector Discussion | Code lists now incorporated into document | General | Change made document updated |  |  |  | Closed
986 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | We appreciate the work put in by your team and the various working groups in developing these documents. The process of evaluating the standards has also been useful for Education as an agency, in promoting a review of our data collection processes and considering how these align with a potential implementation of the standards. Our comments on the standards focus at the strategic level. For our organization, with over 30,000 buildings, the cost of changing data collection are high. We therefore need to consider very carefully what information we capture, what decisions we will need to take with information, how we control the quality of information and how it is updated. For that reason it is important to us that we understand the proposed benefits and implementation uses of the standards before taking firm decisions on data collection for their use. We look forward to further discussion on implementation. Your presentation at the last governance group was a helpful insight into your team’s thinking: we want to ensure that agencies understand each other before committing to implementation or advancing a business case with Ministers. For that reason our comments are interim, subject to these further discussions. | Noted: no action required | Statement noted. | General | No action
987 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Overview of the Metadata Standards Education recognises the importance of asset information in protecting New Zealand’s ability to provide services in a fast-changing national economy. We also endorse a commitment to standardising and sharing information between public agencies. However, we have concerns about the detail and structure of the data proposed in the metadata standards. A challenge in commenting on the proposed metadata standards is understanding the objectives of the data collection process. It remains unclear how this information will be used, what elements of the process will be compulsory and how the comparison between agencies will work. Education is concerned that the costs of collecting the information outlined in the metadata standards will exceed the benefits. Understanding the benefits derived from these comparisons is critical to determining what data should be collected and how it should be categorised. For instance, the data that is needed to promote All-of-Government procurement is very different from the data needed to identify major network risks within New Zealand | Noted: no action required | Statement noted. Business case. | General | No action
988 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Education is also concerned that the focus on the physical condition of the assets may be poorly targeted. Rapid changes in demographics profiles, technology and consumer preferences will also have a major impact on the ability of the current asset networks to meet the future needs of communities. We think that the metadata project should place as much emphasis on the ‘fitness for purpose’, as it does to the physical condition. | Noted: no action required | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | General | No action
989 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | In addition, the metadata standards assume that decisions on asset maintenance are made centrally. Where maintenance decisions are made is a policy choice that is influenced by broader factors than asset management. In the case of Education, asset maintenance decisions are largely managed at a school level. This is a fundamental premise of how the management of schools is devolved to local communities. This is more responsive to the needs of local communities, as well as meaning minor maintenance decisions can be made in the context of education delivery. However, this also means that, while we fund schools for maintenance, we do not specifically control how that funding is spent. This limits the extent to which Education is able to track maintenance expenditure. | Noted: no action required | This standard does not assume where or how decisions are made, it is a set of metadata standards that define decision elements for analytics to support those decisions - in a standard way | No Specific Reference | No action
990 | No Action Required | 3-Waters & Buildings | Vol 1 | Broad strategic issues: Education’s documentation for new construction includes much of the data outlined in the Metadata standards. However, while we collect and hold this information for each project, we do not capture this data into a central database. The nature of this information is useful when looking at the details of potential redevelopment of an asset but not for evaluation at a portfolio level. As with our response to the overall project, Education believes that clearly articulating the benefits of the process will better inform how and what information needs to be collected. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
991 | Included | 3-Waters & Buildings | Vol 1 | Broad strategic issues: We are aware that much of the information for as-built projects will be provided by the contractor. However, we have concerns that the rigorous specification of data may limit the pool of contractors to larger firms with the resources to provide information in a metadata standard. There is a risk that this reduces competition in the industry, and creates price increases especially in provincial centres where Education operates. Education’s exposure to price increases with small building firms is more pronounced than other government agencies who may build a smaller number of more complex facilities (e.g. Courts, Corrections, Defence). | Included | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | N/A | No action
992 | No Action Required | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General | No action
993 | No Action Required | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. | Noted: no action required | Repeat | N/A | No action
994 | No Action Required | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education’s ability to maintain the quality of data is also limited by the devolution of maintenance and minor capital works to schools. Most of the subsequent alterations to buildings are controlled by the schools. Reconfiguring teaching spaces is a regular occurrence across the portfolio but it is unlikely that these changes will be updated in as-built records. | Noted: no action required | Implementation considerations are out of scope | General | No action
995 | No Action Required | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The detail of components specified in the metadata standards appear to be very granular for many of Education’s buildings – for instance there are about 200 fields to describe a building ceiling. The majority of Education’s building will be a simple domestic-scale or light industrial structures, where there is little benefit in collecting this level of detailed information. | Noted: no action required | Implementation considerations are out of scope | General | No action
996 | No Action Required | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: Education would recommend that different levels of information are collected for different types of assets. For instance, complex multi-storey buildings with lifts, fire protection and science laboratories, would require more extensive data to be collected than single-storey wooden-structure school buildings. | Noted: no action required | Implementation considerations are out of scope | General | No action
997 | Included | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The information Education collects on underground services varies greatly depending on the scale and nature of the development. Many of Education’s developments are additions or small schools in provincial locations, with work undertaken by local building firms. The ability of small contracting firms to record in detail where underground services are located is poor, and records are unlikely to be available in an electronic format. Detailed collection of this data may be appropriate for major assets. However, we recommend that collection of geospatial information on underground services is restricted to the larger or more complex developments. | Included | Implementation considerations are out of scope | N/A | No action
998 | No Action Required | 3-Waters & Buildings | Vol 1 | Detailed data collection issues: The risk assessment analysis in the proposed standards is difficult to interpret and evaluate especially for the type of assets being developed by Education. The scale of Ministry buildings tends to be domestic or light industrial in scale. The risk implications for different components of the assets (such as the roof) cannot be easily separated from the risk profile of other components of the building. We recommend this aspect of the risk criteria of the Metadata standards be critically reviewed. | Sector Discussion | The standards make the separation of components and the analysis of risk at a component level of granularity possible. There will be a further discussion about this level of recording with the technial working group. | No Specific Reference | More information required for a decision |  |  |  | Closed
999 | No Action Required | 3-Waters & Buildings | Vol 2 | Broad comments The focus of the data collection is around the building envelope (walls, roof) with significantly less focus on the interior assets. However, building interiors represent a large component of the total cost of providing assets and are the components with the shortest life expectancy. The interior configuration has a major influence on the ability of school buildings to generate positive educational and social outcomes. For these reasons, Education believes the metadata standards should have a greater focus on the interior assets and configuration. | Noted: no action required | All components are collected, including interior components | No Specific Reference | No action
1000 | No Action Required | 3-Waters & Buildings | Vol 2 | Broad comments As well as the definition of the data held, the metadata schema will need to outline the data structure and hierarchy. If information is not collected at a consistent level in the asset hierarchy it makes comparisons between entities difficult. For instance, it is difficult to compare what proportion of the portfolio has fitted wall insulation, if one agency collects the information by building and another by facility. This aspect of the standards should be reviewed. | Noted: no action required | Data Classification, Heirarchy and Structure are all outlined in the Draft Standards | No Specific Reference | No action
1001 | No Action Required | 3-Waters & Buildings | Vol 2 | Broad comments The amount of information collected about the assessor for each data category is unnecessary. It is always useful to know who undertook the assessment but the collection of qualification and experience against each asset is excessive. This detail should be replaced with a measure of confidence around the measures, such as whether it was the result of an exhaustive analysis or a desk-top assessment. | Noted: no action required | Each organisation will decide at what level of granularity (detail) it collects tdata to manage its assets. | No Specific Reference | No action
1002 | No Action Required | 3-Waters & Buildings | Vol 2 | Detailed comments on categories of data The metadata standard outlines the format and categorisation of data on the assets. The following considers each of the categories individually. It discusses these in broad terms and then outlines how Education collates and reports of these asset categories. | Noted: no action required | Statement noted, no action required. | No Specific Reference | No action
1003 | No Action Required | 3-Waters & Buildings | Vol 2 | Condition: The metadata standards propose that condition measures categorise assets by: structure; external; interior; services; and fittings. Separating external cladding and structure is a useful differentiation for some of the housing and light commercial categories. The detail captured on the interior is overly simplistic. The proposed metadata standards focus on cosmetic issues such as the quality of the paint finish, rather than configuration and functionality which is of greater importance for Education. As noted above, interior components represent around one-third of the total building cost and have the highest depreciation rates/shortest lives. Ministry measures: The broad asset categories used by Education are: external; interior; services; and roof. More detailed condition data is held for individual schools but the revaluation and portfolio reporting for Education uses these four categories. Education is currently reviewing options to measure how different building design and fabric choices impact on the light, air quality, temperature and noise levels in teaching spaces. | Noted: no action required | Condition Elements are covered in detail in the standards They do not differentiate buildings by type, beyond the Building Code definition of Facility Importance (which is not building type) These are asset metadata standards, not portfolio form / function and mix standards | 2.2 Condition Schema Code List 13: Facility Importance Rating | No action
1004 | Included | 3-Waters & Buildings | Vol 2 | Repairs and Maintenance The definitions of repairs and maintenance defined in the metadata standards are reasonable and workable. 1. However, collecting data on deferred maintenance items is too complex and unproductive. Part of the issue is that subsequent work may override the maintenance items, but be difficult to identify and measure. Under-maintaining an asset may be best reflected in the condition assessment process. 2. Ministry measures: Education currently identifies programme maintenance items to be undertaken on a building, including recurrence timeframes. Education also categorises the reason for maintenance according to priority (i.e. health and safety, protection of building etc). While Education has a good knowledge of the budgeting for repairs and maintenance, it does not track specific expenditure, accountability for which has been devolved to schools. This means that the explicit scope of work that has been undertaken is not available in Education’s information systems. | Included | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | No action
1005 | No Action Required | 3-Waters & Buildings | Vol 2 | Utilisation: The utilisation measures by nature need to be specific to the industry in which the agency operates and would tend to be for internal reporting only. There is limited advantage in establishing utilisation standards for comparison between entities with very different objectives. This is more appropriately a component of the annual reporting to stakeholders rather than a metadata measure. Ministry measures: Currently Education has a formula for entitlement of classrooms and other space based on school enrolments. Education measures schools’ provision of space compared to entitlement with an optimal target range of 85% to 105%. | Noted: no action required | Agreed, but the standards apply across all Sectoirs (e.g. Housing Providers) | 3.2 Utilisation | No action
1006 | No Action Required | 3-Waters & Buildings | Vol 2 | Demand There are several problems attempting to identify demand for an asset. These are compounded for school assets, which provide free and compulsory services. Commonly residential and light commercial facilities have a variety of different demand parameters. For instance a school hall will support school assemblies, indoor sports activities and community events. Each of these demands has different physical requirements. Measures of demand are therefore difficult to establish. Ministry measures: Education regularly needs to address circumstances where the demand for a school exceeds its capacity. This would commonly be dealt with by strategies such as the application of enrolment zones. Education uses local and regional demographic trends amongst other inputs to identify demand for additional learning spaces and/or new schools. | Noted: no action required | Demand Section has been updated in Volume 2 And, there are many examples of useful demand analytics for schools | 3.3 Demand Schema | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1007 | No Action Required | 3-Waters & Buildings | Vol 2 | Criticality Applying criticality to residential and light commercial buildings is more difficult than with infrastructure. The metadata approach to defining communities being serviced by public sector buildings is not viable. Communities which use public sector buildings tend to be complex and overlapping and criticality dependent on other assets within the network. The definitions of criticality should therefore be limited to explicit requirements in supporting post-disaster response or recovery i.e. identifying assets which have an explicit function defined by Ministry of Civil Defence and Emergency Management plans. Ministry measures: The criticality for the school as a civil defence centre is an agreement between Civil Defence and the Board of Trustees. This will partially be dependent on other community infrastructure in the location. Schools which are Civil Defence centres are not identified within Education’s central information systems. | Noted: no action required | Critciality will be closely linked to Faclity Importance per the Building Code | Code List 13: Facility Importance Rating | No action
1008 | Included | 3-Waters & Buildings | Vol 2 | Risk The metadata schema for risk measurement works to associate risks with asset components. For most of the risks (e.g. earthquake, flooding) it is more appropriate to associate the risk with a building or site, rather than individual component (e.g. roof). Ministry measures: Education has risk registers at a portfolio level and each school has a risk register. Some of the risks associated with the assets relate to the use of materials (e.g. asbestos). These are also logged on the school risk register but not captured centrally. | Included | Risk can be applied at any level of granularity Analytics enable Portfolio level of risk to be established | 4.4 Risk Schema | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1009 | Included | 3-Waters & Buildings | Vol 2 | Resilience The resilience measures have yet to be developed within the metadata standards. The focus of the resilience measures appears to be around major civil defence and emergency events, such as earthquakes. It will be useful to identify the ‘Importance Level’ as defined in building legislation. A sole focus of the civil defence component of resilience is too narrow. We believe the issues should also encompass the ability to change the use of assets or to reconfigure them for different demand or purposes such Ministry measures: When Education developed the business plan for transportable modular classrooms it aimed for these to constitute a proportion of the network to allow flexibility to respond to demographic changes. | Included | Resilience has been updated in the standards | 4.5 Resilience Schema | No action
1010 | Included | 3-Waters & Buildings | Vol 2 | Design Performance The majority of the design performance schema appears to relate to items of equipment, such as pumps and piping. This represents a relatively small proportion of the assets within Education’s network. The majority of the network is relatively uncomplicated, one and two storey buildings, with limited HVAC or specialist facilities. Collecting design performance at the level of individual items is therefore of limited value. Ministry Measures There are some specialised assets within Education’s portfolio, such as lifts in multi-storey buildings. However, these are few in number and are managed under a national contract. Details on the design performance of smaller components, such as heat pumps are typically held by the school. | Included | There are also mant examples of building design perfomance (Earthquake Rating, Energy Rating etc.) | Table 14: Design Performance Examples | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1011 | No Action Required | 3-Waters & Buildings | Vol 2 | Financial Performance There has been significant effort to develop measures for financial performance within the standards. The proposed standards outline a detailed basis for the collection of valuation, depreciation, time of payment information. Rather than replicate data held elsewhere, it would be more useful to ensure that there are linkages with the agency’s broader financial system. This has the advantage of enabling association of asset measures with other agency performance measures, for instance measuring the asset cost per visitor or student. Ministry Measures Education has recently established a new asset management system (Tribal K2) which tracks budgeting for maintenance and other property costs. The system links to Ministry’s property data warehouse system. This allows analysis and development of a broad range of performance measures. The result is the ability to compare asset performance measures to aspects such as student numbers (e.g. the percentage of students learning in buildings that fall into each asset condition category). | Noted: no action required | Organisation specific financial analytics will be supported by attribution within this standard. | 5.3 Financial Performance Schema | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1012 | No Action Required | 3-Waters & Buildings | Vol 2 | Service Performance The service performance schema appears to be a raft of unrelated criteria, which individually may be critical to the functionality of the asset, but do not belong in the same category. The result is measures which relate to different levels of assets from components (e.g. disabled access) through to facilities (e.g. iwi interest). A number of the proximity measures, such as kilometres to communities are difficult to establish without further definitions of community. The result is a wide range of criteria which does not allow comparison between different agencies. Similarly, the raft of measures around district plan criteria, such as provision of car parks, is difficult to update. For many public service assets the land will be designated so underlying zonings will be poor indicators of the use of the site. Some aspects of the data, such as iwi values, heritage considerations or community interests, cannot be easily summarised into a data base. It would be better to include an identifier which would highlight whether more detailed analysis is available on file. Overall Education would advocate for service performance to be restructured into a number of separate themes. Ministry measures Education has a basis for evaluating the service levels called the Innovative Learning Environment (ILE) assessment tool. The information is currently collected at a building level and is a requirement of the five yearly capital and maintenance planning process. Education is evaluating ways of standardising the capture of the information. The ILE assessment tool also has facility to include a range of qualitative measures such as ‘how well the design reflects the needs of the local community’ which may be developed in future. | Noted: no action required | No action required with regards to comment son the business case. The standard is intended to system and organisation agnostic. | 5.4 Service Performance Schema | No action
1013 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Introduction The Auckland Council family fully supports of the intention behind this standard and has actively contributed in the working groups for roads, residential housing and light commercial buildings and the three waters. The Auckland Council family welcomes the opportunity to provide feedback at this time, and the opportunity to participate in the further development of the standard. The metadata standard is a great opportunity to gain national consensus of what minimum level of data capture is required. This initiative will enable us to ensure that data can be applied in a consistent and repeatable way to make good asset management decisions based on acceptable levels of service, replacement and growth strategies. | Noted: no action required | Statement noted. | General | No action
1014 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Summary Feedback is currently sought with specific regards to the three waters and the residential housing and light commercial buildings standards. We have found it difficult to provide meaningful feedback in the absence of a clear strategic message, an understanding of which is shared by all reviewers. That message needs to link the standards to the business case and to recently held discussions with the Minister of Finance. A further opportunity to work on and develop the standard from the ground up, in the way that the transport group has developed the roads standard, would also help the Auckland Council family to feel more confident about the result. To that end we suggest that it would be useful to incorporate such an opportunity into the process from here. We would like: • To present our feedback to the combined governance group • The working groups to review and address all feedback on the standards • The resulting outputs to be made available for consideration by the governance group prior to any public release of the standards | Noted: no action required | Discussions will continue across the Infrastructure Sectors (Core and Social) | No Specific Reference | No action
1015 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 | Volume 1 – As-built metadata standard What we like: • Provides reasonable coverage of possible data fields • As a collection of possible attributes it will help to drive a culture of good practice to capture metadata • It brings attention to the need for good base data What we consider could be further developed: • In its current format the standard is not adoptable due to the constraints it will place on systems and business processes this needs to be addressed before it can be adopted. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed
1016 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • The layout should be modified to clarify the distinctions between master data and metadata. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
1017 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 | What we consider could be further developed: • A number of elements have been included but are not complete, and an understanding of industry definitions, hierarchies and processes is required to complete this volume. We would welcome the opportunity to assist with this. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
1018 | No Action Required | 3-Waters & Buildings | Vol 2 | Volume 2 – Asset management performance standard What we like: • Recognition of the notion that data is only useful if it is used • An approach that recognises the value of rigorous analysis to inform decision making What we consider could be further developed: • In general, we consider that this volume is under developed with inconsistencies and cross-overs to Volume 1. We would welcome an opportunity to further input into its development, as we recognise that it can provide a useful tool, particularly for organisations with limited capability in this area. | Noted: no action required | Volume 2 is now a comprehensive document | No Specific Reference | No action
1019 | No Action Required | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • This volume assumes generalist practices that are inadequate for non-linear assets and includes operational and derived data that is not suitable for inclusion in an AMIS system. | Noted: no action required | This volume is spatially aware, and will attribute point, line, ployline and 3D objects. It is also agnostic to any AMIS and GIS system | No Specific Reference | This will be discussed at the technical workshops |  |  |  | Closed
1020 | No Action Required | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Needs to be carefully framed for the asset types that it relates to. | Noted: no action required | Asset types are specifically defined within the standards - See Volume 1 of each Group of Assets | No Specific Reference | No action
1021 | Included | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Replacement trigger points should be broadened from reliance on subjective visual condition to incorporate best practice for optimal replacement, that is, based on objective measurement and sound engineering judgement. | Included | Visual inspections are only one type of condition assessment to trigger an interventi. Capacity could be another (at Very High > 95%) | Code List 31: Demand – Capacity Unit of Measure | No action
1022 | Included | 3-Waters & Buildings | Vol 2 | What we consider could be further developed: • Reference should also be made to failure mode effects analysis (FMEA/FMECA) as a means to support optimal replacement points. Our feedback does not further consider this volume due to the large disparity with practice and limited workshops to fully capture industry needs. | Included | The standards do not preclude failure mode analysis of any type. The standard captures some of the attributes for this analysis. | 2.3.5 Code Lists | This will be discussed at the technical workshops - mor ework is required here with the sector |  |  |  | Closed
1023 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 1. Create a separate volume that covers strategic fit and business needs across all asset categories. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1024 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 2. Focus on a business standard for assets including improving the hierarchy to cover both asset and data hierarchies and outline the relationship between them. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | No Specific Reference | No action
1025 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 3. Review publishing formats to maximise the impact of the standard. | Included | The drafts have now had a full publishing edit | General | No action
1026 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations: 4. Remove content that is not related to the business standard including those referring to implementation paths, delivery mechanisms and quality control rules. | Sector Discussion | To discuss - for example? | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
1027 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The Workshops The working groups were presented with A-Spec as a straw-man and tasked to focus on the possible data that could be captured for individual asset types. The working groups started with limited traction and concern was raised early on as to the purpose of the workshops in diving into attribute detail that is quite easily obtainable from various sources. A basic data hierarchy was established that allowed the attributes to be tackled in a constructive manner. In hindsight, it would have been useful to consider other industry standards as part of the process. We feel that such consideration could still be undertaken as part of the follow on from this feedback. Despite the concerns mentioned above, the workshop groups generally worked well and came to agreement on the things that were required. It would be extremely useful for the working groups to go over the feedback and address it as appropriate. Strategic, governance and procedural feedback should also be reviewed by the governance groups. | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | General | No action
1028 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Definitions of industry terminologies and attributes. | Sector Discussion | Examples required | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
1029 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Identification of business needs. | Noted: no action required | Business case will outline / describe benefits | N/A | No action
1030 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • An assessment of “fit for purpose” data capture. A matrix and understanding of the minimum data capture required based on organisational needs. | Noted: no action required | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | N/A | No action
1031 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Exploring the origin of the data and identifying whether it belongs to volume one (As constructed) of these standards or is better suited with other data sources, for example geotechnical data. | Noted: no action required | These data sets are what are required for asset management purposes | General | No action
1032 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Validation of the Codes list or optional pick lists. | Noted: no action required | Reviewed and implemented | General | No action
1033 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • The standard is required to be system agnostic. Identifying how the standard will be implemented has an effect on the data capture requirements. To enable this we need to understand what the systems and processes look like. The standard needs to be reconciled with these systems and processes at organisation level. | Noted: no action required | Updated | General | No action
1034 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | The following work that is fundamental to the success of the standard: • Comparison to international practice and other complimentary standards. | Sector Discussion | Information to be provided for discussion | General | More information required for a decision |  |  |  | Closed | There has been a number of reviews against international standards. These (eg OGC) have been aligned to the standards. We will continue to review the standards throughout the pilot for application, due to the variable nature of these standards
1035 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • There is a logical split between roads, buildings and three waters; however there is less logic to further splitting up the three waters when the majority of the components and attributes are the same. It would be sensible to consider consolidating these. | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | No action
1036 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Rather than repeating the introductory statements in both volumes of each version of the standard a covering or base document (as seen in most other standards) should be considered, as the principles of data collection are the same. This would also have the advantage of slimming the volumes down. | Noted: no action required | Format based on technical differentiation | General | No action
1037 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • Common data sets are repeated at every asset class adding unnecessary volume. | Noted: no action required | Action on data scientists. | General | No action
1038 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Format of the standard and target audience • The standard seems to reference the manner in which data will be collected. This is the responsibility of the various organisations and should not form part of the standard. | Noted: no action required | This is not within the scope of these standards | General | No action
1039 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The document will benefit from a better structure around the rationale, strategic drivers and added benefits, of the standard. Some of this information is scattered across the introduction section but it could be strengthened and focused on the purpose of the standard, which is about agreeing on common classifications and definitions. We think there is general agreement that data standards are needed and this doesn’t need to be emphasised. | Noted: no action required | This is not a policy report, an asset management plan, nor a 30 Year Infratsructure Plan (where you would find this requirement). This is a metadata standard for assets at an assetID level of granularity. It does however capture the context of the analytics which inform these types of documents which support organisations asset management | No Specific Reference | No action
1040 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • We believe that the key purpose of this standard should be to outline data requirements that enable organisations to compare their performance and share asset lifecycle knowledge while continuing to measure their performance in a meaningful and cost effective manner in the context of their strategic objectives. | Noted: no action required | Statement noted. | General | No action
1041 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The intention of this standard development was to produce a metadata capture culture and identify the appropriate level of capture. This intention has been somewhat obscured by the very much “field-base” information that is supplied by suppliers and contractors on the physical attributes of assets. We believe that it would be useful to reconsider the audience of this standard and review it to ensure that the audience is appropriately targeted. In that way the business strategy can direct appropriate attribute fields, which will then be common sense as long as common definitions are understood. | Noted: no action required | This observation describes on audience, this is not the only audience, for example design engineers. | General | No action
1042 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Data capture, as acknowledged in the standard is but one component of good asset management and the ways in which this initiative will support organisational challenges such as achieving ISO 55001 accreditation could be made clearer within it. | Noted: no action required | This is not within the scope of these standards | N/A | No action
1043 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The standard strategic goal is to enable organisations and the country “to collect locally and use globally”. It is unclear how this standard compares and incorporates international best practice. There are examples of other international metadata standards however only A-Spec was examined. | Noted: no action required | A number of other standards have been investigated. (Uniclass, Cbi, Omniclass, Master Spec etc. etc.) The strategic goal is to enable organisations and the country “to collect locally and use nationally” | No Specific Reference | No action
1044 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • The way in which the standard is currently written presents the data capture requirements in a set manner and format thereby requiring business needs to be moulded for the data specific needs. These limitations are likely to prevent users from taking opportunities in system and process advances that may become available. Some of these initiatives already exist such as open data sources from product suppliers. We expect these advances to become more readily available in the future. It is not clear how the static two-dimensional model presented by this standard will allow business to incorporate these changes. | Noted: no action required | The standard does exactly the opposite to what this is suggesting. The question is not so much about how it is collected but how the data is manipulated into a common format when it is (see FME) | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1045 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • Existing systems have been heavily invested in and are very diverse, even in the Auckland council family, to tailor for specific needs. With the possibility of the standard purely becoming a mapping exercise; it then does not support the need to prescribe data fields to intricate detail. The level of data capture required to complete the national level analytics is not identified. Anything else is considered optional and does not support the reason for capturing data at every level. | Noted: no action required | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. But Note use of tools like FME. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1046 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Strategic fit of the standard • In order to address the matters referred to in the point above, the standard could be reconfigured to provide the required performance outcome and guidance on how these requirements may be met, while allowing flexibility in means and methods of demonstrating compliance. | Noted: no action required | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. And, there are many analytcal options on the same data sets depending upon he problem being solved. | No Specific Reference | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  | Closed
1047 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • As has been mentioned previously, the document uses terminology and jargon that is not consistent with those used in NZ. This is an easy fix, and appropriate language is a great factor in the ease of adopting new things. | Included | The drafts have now had a full publishing edit | General | More information required for a decision
1048 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • There are plenty of NZ examples of assets of each class and type, and we will be happy to provide some if required. Using Australian examples in a NZ standard is not appropriate where there is a suitable local example available. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed
1049 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • It is also important that the examples used are relevant to the asset type contemplated in the standard. Building examples for the residential housing and light commercial standard will make the logic of the approach more apparent. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision |  |  |  | Closed | Diagrams reviewed and updated
1050 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Language and definitions • Most of the terminology used in the attribute fields is not defined. Without these definitions data cannot be accurately mapped and the data collector will be left to assumptions that will compromise data integrity. | Included | A full publishers edit has been completed on the standards | General | More information required for a decision |  |  |  | Closed
1051 | No Action Required | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • At the beginning of the working group workshops we agreed that these are business standards – hence system agnostic; this is even mentioned in the document. At the same time the proposed standard – language, data formats and terminology – has been prepared for an easy input to a functional specification for a GIS application. It is evident that the asset classification and the attributes were “flattened” to fit this particular implementation. This has detrimentally affected the business value of the standard – we have a number of attributes that do not belong to the asset class they are listed against. An example: in stormwater, swale only attributes are elevated at channel level, at which level they are meaningless. | Sector Discussion | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | General | More information required for a decision |  | No further action |  | Closed
1052 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The current format of data requirements as a mix of business standard and specification is of particular concern. On one hand it makes the business part of the standard logic hard to follow, while on the other hand the document is not sufficiently detailed to be effective as a functional specification. As a consequence standard does not show the business what it needs to collect and the application vendors will not understand what they need to build. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
1053 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • The asset data hierarchy needs to be completed. Most importantly the way assets have been grouped for data capture needs to be reconsidered in order to represent the business asset hierarchy. Business hierarchy is of great importance for FMEA, operation and maintenance of complex assets, for example. The exclusion of business hierarchies from the standard will require every organisation to create another set of rules outside of the standard in order to maintain these relationships. | Sector Discussion | The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers that in turn will provide consistency to the asset owners. As each organisation has their own hierachy it is expected that they will categorise the data being provided according to their needs | General | More information required for a decision |  |  |  | Closed | To be resolved during implementation
1054 | Included | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • We strongly recommend that all implementation related fields be removed from the document, as outlined below: o Attribute abbreviations – these are in many cases system related setup and for instance instrumentation may be adopted by numbering systems such as ISA55 that is international practice. The purpose of these abbreviations is not clear. o Character length – This serves no purpose and is not supportive of being system agnostic. By providing full and proper definitions to the attribute field data may be mapped correctly, regardless of character lengths. o Comments – This filed has no purpose that cannot be fulfilled by either the unit filed or description fields o QA validation – These are rules set by business and specific software systems. It also does not serve any purpose to identify minimum capture level. This could be done in a better way through a developed hierarchy that identifies, master data from metadata and compulsory fields from conditional or optional fields | Included | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | General | No action
1055 | Included | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • To date geometrical and topology rules have not been discussed. Currently there are different requirements governing the way geospatial data is captured. As with the asset management systems, investment has been made in maintaining systems to these rules. From an analytics point this does not seem to have any impact on the analytic output. Development of such a standard is considered to be a separate endeavour in its own right and has the potential for having great cost impacts to organisations. In the same way one could argue other data sets must then be prescribed – such as geotechnical information, drawings and so on. Flexibility is key, as planning for known technology, given the pace of technological change, will mean that the standard is out of date before it is published. | Included | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | General | No action
1056 | Included | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • Attribute sets are not normalised across the asset classes. An example of this is the repetitive material types in the codes lists. (Note. Watercare, Wellington Water and Christchurch City Council were the only parties to receive the codes lists later on request. This was never published. | Included | It is acknowledged that codelists will need to be dynamic in nature and will be open to continued contribution from the sector. The code lists are now incorporated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | General | No action
1057 | Completed | 3-Waters & Buildings | Vol 1 | Scope and content of Volume 1 • As-built data versus operational data versus derived data is crossed over between the volumes. Separation is required through the data hierarchy. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Change made document updated
1058 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 1. Create a separate volume for strategic fit and business needs | Noted: no action required | To discuss | No Specific Reference | More information required for a decision |  |  |  | Closed
1059 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Improve the Asset Hierarchy section to cover both asset and data hierarchy and to outline the relationship between them. | Included | Asset Classifications have been defined in the Standards | General | No action
1060 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and simplify attributes specifications; all attributes that do not belong to the As Built standard, such as demand, repair and maintenance, health and safety issues, service and financial performance should be removed. These are time related measures and events that are covered by other parts of the standard. Connecting these events and measures to assets is the subject of asset analytics, not the as built standard. | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' | No Specific Reference | No action
1061 | Completed | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Review and clean the attribute tables – remove all values that are included as they are not relevant. | Sector Discussion | The standards have harmonised and standardised data and hierarchies across the standards | General | More information required for a decision |  |  | An addition of explanation has been added to standards - completed | Closed
1062 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Clean the relationship between asset classes, attributes and values. One asset class has to belong to one asset category. | Included | Asset Classifications have been defined in the Standards | General | More information required for a decision |  |  |  | Closed | Change made document updated
1063 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Outline a list of core asset characteristics – the whole concept of the standard as vehicle for comparability becomes meaningless if we don’t agree on a few critically important attributes that must be collected. | Noted: no action required | Mandatory, Optimal, Optional will be discussed with the sectors | No Specific Reference | More information required for a decision |  |  |  | Closed
1064 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 2. Focus on business standard for assets: • Our recommendation is to add a section on asset geometry and topology for water networks – but not one that could be mistaken for a specification for GIS applications. This section needs to address the core rules for creating geometric networks and outline the participation of all assets in these networks. | Included | Included in the draft Standards | General | No action
1065 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Since all standards are related and are part of the same suite of documents it would make sense for them to be published as related volumes (chapters?) rather than independent books. | Included | This has been reviewed, and a decision to keep as separate documents made - at this time (the documents would be 300+ pages if combined | No Specific Reference | No action
1066 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Another approach to publishing standards which would be effective is by using links to look up the list of attribute values. | Included | Other access toolss will be reviewed before release in July 2017 | No Specific Reference | No action
1067 | Included | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 3. Review publishing formats: • Think about publishing the data tables in a data view in addition to the document | Included | Included in the draft Standards | General | More information required for a decision |  |  |  | Closed | Attributes held within Metaconnect
1068 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | Recommendations 4. Remove content that is not related to the business asset data standard: • We strongly recommend that all references to implementation paths, delivery mechanisms and quality control rules be removed from this document. This should be a subject to a separate project/ research due to the variety of business models that can be applied. Unless there is a directive for a centralised implementation of these standards, they remain the responsibility of each organisation and have to be adapted to the particular technology platform. | Noted: no action required | Unclear of where there are examples of this | No Specific Reference | No action
1069 | No Action Required | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  |  |  | Closed
1070 | No Action Required | 3-Waters | Vol 1 | Asset class definitions needed: Need clear definition of asset classes. Channels are particularly bad examples; they cover a range of assets with various function and purpose - and badly. Under current structure there is no way to describe sw treatment devices. | Sector Discussion | Classifications and types defined in the standards Refer to code lists | General | More information required for a decision |  | Closed
1071 | No Action Required | 3-Waters | Vol 1 | Attribute definitions needed: Many definitions are unclear or missing. Some appear to be database oriented - need to be business meaningful. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Closed
1072 | No Action Required | 3-Waters | Vol 1 | Standard is about structured data, not any information about assets: This standard should cover the data that needs to be captured in as structured way for further analytical and reporting use. Hence all data that has no such value needs to be removed. In complex assets most of the asset specific data is kept in operation manuals and other operation related documentation. | Noted: no action required | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | General | No action
1073 | No Action Required | 3-Waters | Vol 1 | This is volume one - as constructed assets. Remove all data that is not relevant to as constructed - there are other volumes that this data is described | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Closed
1074 | No Action Required | 3-Waters | Vol 1 | Huge number of attributes that are not relevant and not agreed. Need to go back to the workshop discussions and agree how feedback following working sessions will be captured - cannot afford to continue like that. | Sector Discussion | More information is required to inform a way forward | General | More information required for a decision |  | Closed |  | Closed
1075 | Included | 3-Waters | Vol 1 | Renewal material in pipes. This should be relabeled to say lining material. | Included | Attributes included, lining material included in standards see code lists | General for Pipes | No action
1076 | Completed | 3-Waters | Vol 1 | Missing attributes. Lining material installation data is critical | Sector Discussion | More information is required to inform a way forward | General for Pipes | More information required for a decision |  | No further action | Modified General Validation Rule for Material, Renewal Method and Renewal Material to also include that the fields are 'Conditional'
1077 | No Action Required | 3-Waters | Vol 1 | See excel sheet with specific feedback. | Noted: no action required | Information to be provided for discussion refer to ID1069 | General | More information required for a decision |  |  |  | Closed
NEW001 | Completed | 3-Waters | Vol 2 | Code List 9 - people with a spade won't understand the difference between these codes, as they are all the same thing to the person on the ground | Sector Discussion |  |  | Codelist 21 on page 45 |  |  |  | Closed | Duplicate
NEW002 | Awaiting Implementation Phase | 3-Waters & Buildings | Vol 1 & Vol 2 | In volume 2 there is a space to define mandatory - but there isn't the same in volume 1. what's going on? | Sector Discussion |  | General |  |  |  |  | No further action required | Mandatory removed from volume 2 Understanding the importance of data, and what is essential v optional, will be determined during initial implementation
NEW003 | No Action Required | 3-Waters & Buildings | Vol 2 | Need to include an attribute where something hasn't been assessed yet | Sector Discussion |  | General |  |  |  |  | No further action required | go with having a blank field as this is the equivalent of no record adjust QA that field can be empty
NEW004 | No Action Required | 3-Waters & Buildings | Vol 1 & Vol 2 | There are potentially occurances where the standards include code lists, where not enough information is known to make the code lists finite - suggestion that these code lists are flagged as being examples etc | Sector Discussion |  | General |  |  |  |  | No further action required | Completed Added to standard
NEW005 | No Action Required | 3-Waters & Buildings | Vol 2 | Table 2 - looks more transactional than elemental, why connected to an 'event' rather than directly to the 'table'? | Sector Discussion |  | General |  |  |  |  | No further action required | Multivatiate analysis

## New attributes or Codelist
ID of Action items | Standard | Volume | Feedback | Status | Final Comments for Publication | Section Reference in Final Version - per Contents page | Additional Work | Proposed Codelists / Attributes | Additonal Comments | Attribute Name - Abbreviated | Attribute Name - Full | Data Type | Units of Measure | Max Length | Comments | Contents | Example | General Validation Rule | Specific Validation Rule | CODELIST Reference | Legend Physical - P Metadata - M Asset Management - AMS | Codelist Name | Codes
| wastewater | Vol 1 | Feedback from Vicki - Jeff Booth Consulting The table needs to be matched with the stormwater one. |  |  | 2.4.4 Pipe |  |  | The pipe table is to be replaced with the pipe table from the SW document This is due to the pipe table being the same as PW which does not suit.
48 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Sector Discussion | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General | New Code List proposed | Health & Safety Type |  | Hlth_Sfty | Health And Safety Issues | Alpha / Numeric |  | 10 chars | No commas included | Health and safety Issues that need to be known | Specific instruction to access the asset | Field cannot be empty | Entry must be from CODELIST | Health and Safety Issues | M | Health and Safety Issues | CONFINED - Confined Spaces ENERG_SRC - Energy Sources EXCAVATION - Excavation and Trenching FORKLIFTS - Forklifts Operating HAZ_SUB - Hazardous Substances HEIGHT - Working At Height HIGH_VOLT - High Voltage LIFT_EQUIP - Cranes and Lifting Equipment NIL - No Requirement PLANT - Mobile Plant POWER_EQ - Powered Plant and Equipment TRAFFIC - Live Traffic VEHICLES - Driving Motor Vehicles
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute Weight Add to Mechanical Equipment Asset Class Electrical Equipment Asset Class |  | Weight | Weight | Integer | Kilograms | n/a | Whole number | Weight of asset in kg | 5 | Field cannot be empty | Default = -9999 |  | P
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute Current Maximum Rating Add to Mechanical Equipment Asset Class Electrical Equipment Asset Class Instrument Asset Class |  | Current Maximum Rating | Integer | Ampere (Amp) |  | n/a | Whole number | The Current maximum rating |  | Field cannot be empty | Default = -9999 |  | M
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute Output Rating Add to Mechanical Equipment Asset Class Electrical Equipment Asset Class |  | Out_Rate | Output Rating | Integer | Kilo-volt ampere (kVA) | n/a | Whole number | Output Rating in kVA |  | Field cannot be empty | Default = -9999 |  | M
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute Power Rating Add to Mechanical Equipment Asset Class Electrical Equipment Asset Class |  | Power_Rate | Power Rating | Integer | Kilowatt (kW) | n/a | Whole number | The power rating of the asset |  | Field cannot be empty | Default = -9999 |  | M
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute IP Rating Add to Mechanical Equipment Asset Class Electrical Equipment Asset Class Instrument Asset Class |  | IP_Rating | Ingress Protection Rating | Integer |  | n/a | Whole number | Ingress Protection rating recorded to IEC 60034-5 standard IP67 to be recorded as 67 |  | Field cannot be empty | Must be 2 digits long. Default = -9999 |  | M
57 | 3-Waters | Vol 1 & Vol 2 | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments | New attribute proposed | New attribute Capacity Time Instrument Asset Class |  | Capacity_T | Capacity Time | Decimal | Time |  | 2 decimal places | The Capacity of the asset in time as ampere hours |  | Field cannot be empty | Default = -9999.99 |  | M
63 | 3-Waters | Vol 1 & Vol 2 | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA) |  | OMA | Operational Management Area | Alpha / Numeric |  | 10 chars | No commas included | The specific management area that is applicable to this asset |  | Field cannot be empty | Entry must be from CODELIST | Operational Management Area | M | Operational Management Area | CMA - Catchment DMA - Demand Management Area
65 | Stormwater | Vol 1 | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. | Sector Discussion | Add Rigid and Flexible to code list | 2.3.4 Pipe | New attribute proposed | Rigid or Flexible as option |  | Rig_Flex | Rigid or Flexible | Alpha |  | 1 char | Rigid or Flexible field | Indicates whether the pipe is Rigid or Flexible |  | Field cannot be empty | Valid input: R, F |  | P
66 | Stormwater | Vol 1 | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. | Sector Discussion | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | More information required for a decision |  |  | Test_Type | Testing Type | Alpha / Numeric |  | 10 chars | No commas included | The type of testing carried out on the asset |  | Field cannot be empty | Entry must be from CODELIST | Testing Type | M | Testing Type | Deflect - Deflection Compact - Compaction
68 | Stormwater | Vol 1 | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... | Included | AddCCTV & Laser Profiling testing to code list testing type | General | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling | [13 empty] | Condition Assessment Type | CCTV Laser Profiling
69 | Stormwater | Vol 1 | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" | Sector Discussion | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | New attribute proposed | Installer of Asset |  | Installer | Installer | Alpha / Numeric |  | 100 chars | No commas included | Name of the individual or company who installed the asset |  | Field cannot be empty | Default = N/A |  | M
69 | Stormwater | Vol 1 |  |  |  | 2.7.1 Instruments |  |  | To be included along with Installer | Inst_W | Installer Warranty | Date | Time | n/a | dd/mm/yyyy | Installer's warranty end date |  | Field cannot be empty | Default = 31/12/9999 |  | M
69 | Stormwater | Vol 1 |  |  |  | 2.7.1 Instruments |  |  | To be included along with Manufacturer | Manu_W | Manufacturers Warranty | Date | Time | n/a | dd/mm/yyyy | Manufacturer's warranty end date |  | Field cannot be empty | Default = 31/12/9999 |  | M
76 | Stormwater | Vol 1 | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) | Safety access included as part of H&S codelist | Frame_Cl | Frame Class | Alpha / Numeric |  | 10 chars | No commas included | The class of the frame |  | Optional Field cannot be empty | Entry must be from CODELIST | Frame Class | P | Frame Class | TBD from SME contribution
76 | Stormwater | Vol 1 |  |  |  | 2.4.1 Access Chamber |  |  |  | Frame_Std | Frame Standard built to | Alpha / Numeric |  | 30 chars | No commas included | The NZ standard used at time of construction |  | Optional Field cannot be empty
76 | Stormwater | Vol 1 |  |  |  | 2.4.1 Access Chamber |  |  |  | Cover_Cl | Cover Class | Alpha / Numeric |  | 10 chars | No commas included | The class of the cover |  | Optional Field cannot be empty | Entry must be from CODELIST | Cover Class | P | Cover Class | A - Footpaths and Areas only accesible by pedestrians and pedal cyclists B - Footpaths that may be lounted by a vehicle or livestock and light tracker paths C - Malls and pedestrian areas open to slow moving commercial vehicles D - Carriageways of roads and areas open to commercial vehicles E - General docks and aircraft pavements
76 | Stormwater | Vol 1 |  |  |  | 2.4.1 Access Chamber |  |  |  | Cover_Std | Cover Standard built to | Alpha / Numeric |  | 30 chars | No commas included | The NZ standard used at time of construction |  | Optional Field cannot be empty
76 | Stormwater | Vol 1 |  |  |  | 2.4.1 Access Chamber |  |  |  | Seal_Type | Seal Type | Alpha / Numeric |  | 10 chars | No commas included | The seal type on the cover |  | Optional Field cannot be empty | Entry must be from CODELIST | Seal Type | P | Seal Type | BOLT - Security Bolt-Down BOLTWATER - Bolted and Water tight DOUBLE - Double Sealed WM - Welded Metal
78 | Stormwater | Vol 1 | Manufacturer Manufacturing Standard Third Party QA Accreditation | Sector Discussion | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion |  | Manu | Manufacturer | Alpha / Numeric |  | 100 chars | No commas included | Manufacturer of the asset |  | Field cannot be empty | Default = NA |  | M
78 | Stormwater | Vol 1 |  |  |  | 2.4.3 Fitting |  |  | added to partner manufacturer field | Manu_W | Manufacturers Warranty | Date | Time | n/a | dd/mm/yyyy | Manufacturer's warranty end date |  | Field cannot be empty | Default = 31/12/9999 |  | M
78 | Stormwater | Vol 1 |  |  |  | 2.4.3 Fitting |  |  |  | Manu_Std | Manufacturing Standard | Alpha / Numeric |  | 30 chars | No commas included | The NZ standard used at time of construction |  | Optional Field cannot be empty | Default = NA |  | M
78 | Stormwater | Vol 1 |  |  |  | 2.4.3 Fitting |  |  |  | TP_QA | Third Party Quaslity Assurance | Alpha / Numeric |  | 100 chars | No commas included | The name of the party that issued the Quality Assurance |  | Optional Field cannot be empty | Default = NA |  | M
83 | Stormwater | Vol 1 | Rigid material standard and QA Separate Flexible material standard and it's QA | Sector Discussion | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA |  | RM_Std | Rigid Material Standard | Alpha / Numeric |  | 30 chars | No commas included | The NZ standard used at time of construction |  | Optional Field cannot be empty | Default = NA |  | M
83 | Stormwater | Vol 1 |  |  |  | 2.4.4 Pipe |  |  |  | RM_QA | Rigid Material Qualirty Accreditation | Alpha / Numeric |  | 100 chars | No commas included | The name of the party that issued the Quality Assurance |  | Optional Field cannot be empty | Default = NA |  | M
83 | Stormwater | Vol 1 |  |  |  | 2.4.4 Pipe |  |  |  | FM_Std | Flexible Material Standard | Alpha / Numeric |  | 30 chars | No commas included | The NZ standard used at time of construction |  | Optional Field cannot be empty | Default = NA |  | M
83 | Stormwater | Vol 1 |  |  |  | 2.4.4 Pipe |  |  |  | FM_QA | Flexible Material Qualirty Accreditation | Alpha / Numeric |  | 100 chars | No commas included | The name of the party that issued the Quality Assurance |  | Optional Field cannot be empty | Default = NA |  | M
85 | Stormwater | Vol 1 | Compaction strength per NZS4566.2 | Sector Discussion |  | 2.4.4 Pipe |  |  | Create an observation field for results | Observed | Observation | Alpha / Numeric |  | 250 chars | No commas included | Observations at time of construction. May include results from testing of asset eg compaction tests etc |  | Optional Field cannot be empty | Default = NA |  | M
125 | Buildings | Vol 1 | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 | More information required for a decision |  |  | Build_Code | Building Code | Alpha / Numeric |  | 100 chars | No commas included | The relevant NZ Building Code at time of construction |  | Field cannot be empty |  |  | M
506 | Potable water | Vol 1 | how is a locator or IP cable taped to the pipe represented? | Sector Discussion |  | 2.4.5 Pipe |  |  |  | L_or_IP | Locator or IP Cable | Alpha |  | 1 char | Yes or No field | Is there a locator or IP cable taped to the pipe along this section? |  | Optional Field cannot be empty | Valid input Y or N |  | P
541 | Stormwater | Vol 1 | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! | Sector Discussion |  | 2.3.4 Wing Wall |  | Apron |  | Apron | Apron | Alpha |  | 1 char | Yes or No field | Indicates if an Apron exists as part of the structure |  | Field cannot be empty | Valid Input: Y,N |  | P
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion |  | 2.3.2 Embankment |  |  |  | Over_RL | Overflow Level | Decimal | Metres | n/a | 2 decimal places | Indicates the Reduced Level of the point where the overflow occurs |  | Optional Field cannot be empty | Default = -9999.99 |  | P
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion |  | 2.3.2 Embankment |  |  |  | Easting | Easting coordinate | Decimal | Metres | n/a | 3 decimal places | Indicates the easting coordinate of the of the point where the overflow occurs |  | Optional Field cannot be empty | Default = -9999.999 |  | M
543 | Stormwater | Vol 1 | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. | Sector Discussion |  | 2.3.2 Embankment |  |  |  | Northing | Northing coordinate | Decimal | Metres | n/a | 3 decimal places | Indicates the northing coordinate of the point where the overflow occurs |  | Optional Field cannot be empty | Default = -9999.999 |  | M
549 | Stormwater | Vol 1 | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. | Sector Discussion |  | 2.4.1 Access Chamber |  |  | instead of depth field | RL | Reduced Level | Decimal | Metres | n/a | 2 decimal places | Reduced Level at the bottom of the chamber |  | Field cannot be empty | Default = -9999.99 |  | P
583 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure | New Code List proposed | Burial Status Above ground Below ground Partially buried |  | Buried | Burial State | Alpha / Numeric |  | 10 chars | No commas included | The burial state of the asset |  | Optional Field cannot be empty | Entry must be from CODELIST | Burial State | P | Burial State | ABG - Above Ground BLG - Below Ground PART - Partially Buried
586 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  |  | Inlet_Prot | Inlet Protection Type | Alpha / Numeric |  | 10 chars | No commas included | The type of inlet protection on this asset |  | Conditional Field cannot be empty | Entry must be from CODELIST | Inlet Protection Type | P | Inlet Protection Type | NRV- Non Return Valve ASV - Automatic Shutoff Valve
587 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  |  | Inlet_Feed | Inlet Feed Type | Alpha |  | 1 char | Top of Bottom field | Indicates from where the asset is being filled |  | Field cannot be empty | Valid input T or B |  | P
588 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  |  | Out_Shut | Outlet Shut Off Valve | Alpha |  | 1 char | Yes or No field | Indicates whether there is an outlet shut off valve
589 | Potable water | Vol 1 | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  |  | Partition | Partitioned | Alpha |  | 1 char | Yes or No field | Indicates if the asset is partitioned |  | Field cannot be empty | Valid input Y or N |  | P
590 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber |  |  | Converted to codelist | Acc_Rest | Access Restriction | Alpha / Numeric |  | 10 chars | No commas included | The type of access restriction to the asset |  | Field cannot be empty | Entry must be from CODELIST If there is a Restriction populate the Health & Safety field | Access Resrtiction | P | Access Restriction | CONFINED - Confined Space NONE - No Restriction RESTRICT - Restricted Access
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting |  |  |  | Link_Feat2 | Link Feature | Alpha / Numeric |  | 10 chars | No commas included | Type of the second feature to which the asset is attached |  | Field cannot be empty | Entry must be from CODELIST | Feature Type | M
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. |  |  | 2.4.3 Fitting |  |  |  | Link_ID2 | Link Identifier | Alpha / Numeric |  | 20 chars | No commas included | Unique ID of the second asset its associated with |  | Field cannot be empty | Default = N/A |  | M
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. |  |  | 2.4.3 Fitting |  |  |  | Link_Feat3 | Link Feature | Alpha / Numeric |  | 10 chars | No commas included | Type of third feature to which the asset is attached |  | Field cannot be empty | Entry must be from CODELIST | Feature Type | M
596 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. |  |  | 2.4.3 Fitting |  |  |  | Link_ID3 | Link Identifier | Alpha / Numeric |  | 20 chars | No commas included | Unique ID of the third asset its associated with |  | Field cannot be empty | Default = N/A |  | M
597 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed | Manufacturer |  | Manu | Manufacturer | Alpha / Numeric |  | 100 chars | No commas included | Manufacturer of the asset |  | Field cannot be empty | Default = NA |  | M
597 | Potable water | Vol 1 | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting | New attribute proposed |  | added to partner manufacturer field | Manu_W | Manufacturers Warranty | Date | Time | n/a | dd/mm/yyyy | Manufacturer's warranty end date |  | Field cannot be empty | Default = 31/12/9999 |  | M
614 | Potable water | Vol 1 | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber | More information required for a decision | 0 |  | Sealed | Sealed | Alpha |  | 1 char | Yes or No field | Indicates if the asset has been sealed |  | Field cannot be empty | Valid input Y or N |  | P
617 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station | New attribute proposed | Portable generator (Y/N) | Will use Power backup as this currently exists as an attribute field with an associated code list | Power_back | Power Backup | Alpha / Numeric |  | 10 chars | No commas included | Indicates the type of backup this unit has should there be a power outage | UPS, Generator, Battery | Conditional Field cannot be empty | Entry must be from CODELIST | Backup Power Type | P
618 | Potable water | Vol 1 | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station |  |  |  | Seismic | Seismic Performance Status | Integer | Percentage | n/a | Whole number | The Seismic Performance status of the asset as defined by the relevant NZ standard at time of capture represented as an accurate measure of %NBS (New Building Standard) |  | Field cannot be empty | Default = -9999 |  | M
618 | Potable water | Vol 1 |  | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station |  |  |  | Seis_Std | Seismic Standard | Alpha / Numeric |  | 30 chars | No commas included | The NZ standard used to define Seismic Performance | NZS 3106-2009 | Field cannot be empty | Default = N/A |  | M
618 | Potable water | Vol 1 |  | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | New attribute proposed | Calculation |  | Seis_Calc | Seismic Calculation | Alpha / Numeric |  | 100 chars | No commas included | The calculation used to qualify the Performance Status |  | Field cannot be empty | Default = N/A |  | M
619 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve | New OPTIONAL attribute | Valve Power Manual power mains power battery power pneumatic hydraulic spring |  | Valve_P | Valve Powered By | Alpha / Numeric |  | 10 chars | No commas included | How the asset is powered | Hydraulic | Optional Field cannot be empty | Entry must be from CODELIST | Valve Power | P | Valve Power | MANUAL - Manual MAINS - Mains Electriciy BATTERY - Battery PNEUMATIC - Pneumatic HYDRAULIC - Hydraulic SPRING - Spring
620 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve | New Code List proposed | Valve Control & Automatic Control |  | Op_Mode | Mode | Alpha / Numeric |  | 10 chars | No commas included | What activates the valve control | Manual | Field cannot be empty | Entry must be from CODELIST | Valve Control | M
621 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. | Sector Discussion | see 0619 | 2.5.3 Valve |  | Valve Power |  | Valve_P | Valve Powered By | Alpha / Numeric |  | 10 chars | No commas included | How the asset is powered | Hydraulic | Optional Field cannot be empty | Entry must be from CODELIST | Valve Power | P
625 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection |  | Valv_Con | Valve Configuration | Alpha / Numeric |  | 10 chars | No commas included | Configuration of the asset |  | Field cannot be empty | Entry must be from CODELIST | Valve Configuration | M | Valve Configuration | Inline - I Bypass - B Cross-Connection - C
627 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Incoming Pressure |  | Press_In | Incoming Pressure | Integer | Kilopascals (kPa) | n/a | Whole number | Incoming pressure of the valve during normal operation in kilopascals |  | Field cannot be empty | Default = -9999.99 |  | M
628 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Outgoing Pressure |  | Press_Out | Outgoing Pressure | Integer | Kilopascals (kPa) | n/a | Whole number | Ougoing pressure of the valve during normal operation in kilopascals |  | Field cannot be empty | Default = -9999.99 |  | M
629 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | New attribute proposed | Headloss |  | Head_Loss | Head Loss | Integer | Kilopascals (kPa) | n/a | Whole number | Pressure head loss through the valve at peak flow in kilopascals. Please note – not when the valve is shut |  | Field cannot be empty | Default = -9999.99 |  | M
631 | Potable water | Vol 1 | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow |  | Purpose | Purpose | Alpha / Numeric |  | 10 chars | No commas included | The purpose of the asset | Sample | Field cannot be empty | Entry must be from CODELIST | Valve Purpose | M | Purpose | AIRIN - Air In AIROUT - Air Out AIRINOUT - Air In & Out PRES BDY - Boundary Press. Zone CTRLFLOW - Control - Flow CTRLPRESS - Control - Pressure CTRLFLPR - Control Flow & Press SERV - Customer Service FIREFIGHT - Fire fighting FIRE - Fire Service Connection PRESREDU - Pressure Reducing PRESRG - Pressure Regulating PRESRELF - Pressure Relief SAMPLE - Sampling Point SCOUR - Scour BYPASS - Facilate main valve operation DMA BDY - DMA boundary isolation NRV - Non- return/backflow
633 | Potable water | Vol 1 | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump | New attribute proposed | Pump oreintation |  | P_Orient | Pump Orientation | Alpha |  | 1 char | Horizontal or Vertical field | Is the pump oriented horizontally or Vertically? |  | Field cannot be empty | Valid input: H,V |  | P
635 | Potable water | Vol 1 | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty end date, Purchase date to be reviewed. | 2.5.1 Equipment |  |  |  | Purch_Date | Purchase Date | Date | Time | n/a | dd/mm/yyyy | The date the item was purchased |  | Field cannot be empty | Default = 31/12/9999 |  | M
657 | Wastewater | Vol 1 | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station |  |  |  | Overflow | Overflow | Alpha |  | 1 char | Yes or No field | Indicates if the asset has an overflow |  | Field cannot be empty | Valid input Y or N |  | P
753 | Wastewater | Vol 1 | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this | Included | Reviewed and Noted for Inclusion Included as part of the Project Attributes table Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | More information required for a decision | 0 |  | Surveyed | Surveyed Date | Date | Time |  | dd/mm/yyyy | Indicates the date of a survey before or after an event (e.g. earthquake) |  | Field cannot be empty | Default = N/A |  | M
780 | Potable water | Vol 1 | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) | Sector Discussion | to be discussed with the TWG | 2.3.4 Well |  |  |  | Con_Mtd | Construction Method | Alpha / Numeric |  | 10 chars | No commas included | Construction Method. | Insitu | Field cannot be empty | Entry must be from CODELIST | Well Construction Method | P | Well Construction Method | DRILLED - Drilled DRIVEN - Driven DUG - Dug

## Sheet1 (2) (hidden)
NZAMS - Sector Feedback - Final Version | [23 empty] | 358 | 10 | 179 | 522 | 0 | 0 | 0 |  | 599 | 241 | 231 | 0 | 50 | [18 empty] | 1069
ID | Respondent | Organisation | Standard | Volume | Section nr. V6 | Page number V6 | Paragraph / table V6 | Section nr. V8 | Page number V8 | Paragraph/table V8 | Feedback | Topic | OPUS Comments | Volume | Review Haydn Vol 1 | Review Haydn Vol 1 & 2 | Review Haydn Vol 2 | Review GISSA | Response (GISSA response date) | Status Included, Excluded, Sector discussion, Noted: no action required | Status Included, Excluded, Sector discussion, Noted: no action required from GISSA sheet 11-2 | Final Comments for Publication | Section Reference in Final Version - per Contents page | Included | Excluded | Sector discussion | Noted: no action required | HAYDN | GEORGE | GEORGE & HAYDN |  | Vol 1 | Vol 1 & 2 | Vol 2 |  | Haydn | question for haydn | Haydn Action | action for gissa | gissa comment | pw V1 | ww V1 | sw V1 | Build V1 | pw V2 | ww V2 | sw V2 | Build V2 | follow up action by gissa | Additional Work | Proposed Codelists / Attributes | MW_edits_V2 | HR_edits_V15 | HR_edits_V15 Notes for George
1 | Nic Donnelly | LINZ | Potable water | Vol 2 | Use of spec | III | 3 |  |  |  | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | NA | Statement noted, no action required. | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
2 | Nic Donnelly | LINZ | Potable water | Vol 2 | 3.4 | 43 | Data table 3 / 3.10 |  |  |  | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Normalisation | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
3 | Nic Donnelly | LINZ | Potable water | Vol 2 | 3.5 | 47 | Code list 13 / A |  |  |  | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Normalisation | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
4 | Nic Donnelly | LINZ | Buildings | Vol 2 | Use of spec | III | 3 |  |  |  | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Data | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [8 empty] | n/a | n/a | n/a | NO ACTION | [5 empty] | No action |  | N/A
5 | Nic Donnelly | LINZ | Stormwater | Vol 2 | Use of spec | III | 3 |  |  |  | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Normalisation | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
6 | Nic Donnelly | LINZ | Stormwater | Vol 2 | 3.5 | 50 | Code list 13 / A |  |  |  | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Spatial | Users to decide most appropriate system. | Vol 2 |  |  | George |  |  | Included | Noted: no action required | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  | there is a difference when working with accuracies of 0.00-0.20m suggest this adopt LINZ suggestion possible sector review | [9 empty] | No action |  |  | y | completed | 1 | 1
7 | Nic Donnelly | LINZ | Wastewater | Vol 2 | Use of spec | III | 3 |  |  |  | Should be "coordinate reference system" as in ISO 19111 | Spatial |  | Vol 2 |  |  | George |  |  | Included | Included | Standards are OGC spatial attribution compliant | Use of the Specification | 1 | [9 empty] | 1 |  |  | ok | [12 empty] | No action |  | N/A
8 | Nic Donnelly | LINZ | Wastewater | Vol 2 | 3.5 | 49 | Code list 13 / A |  |  |  | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Spatial | Users to decide most appropriate system | Vol 2 |  |  | George |  |  | Included | Noted: no action required | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  | change needed in Vol 2 specs | there is a difference when working with accuracies of 0.00-0.20m suggest this adopt LINZ suggestion possible sector review | [9 empty] | No action |  |  | y | completed | 1 | 1
9 | Nic Donnelly | LINZ | Potable water | Vol 1 | Use of spec | v | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | Noted | not required in this section, covered in later sections 28/2/2017 | Included | Included | not required in this section, covered in later sections 28/2/2017 | Use of the Specification | 1 | [7 empty] | 1 | [17 empty] | No action
10 | Nic Donnelly | LINZ | Potable water | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Horizontal Coordinate System" to distinguish it from the vertical |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed 28/2/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
11 | Nic Donnelly | LINZ | Potable water | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Vertical Datum" since datums can also be horizontal |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed 28/2/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
12 | Nic Donnelly | LINZ | Potable water | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | or vertical datum |  |  | Vol 1 |  |  |  | Under Review | further explanation required 28/2/2017 | Included | Sector Discussion | Updated in draft standards | 1.5 Deliverables |  |  | 1 | [5 empty] | 1 |  |  |  | 1 |  |  | change needed | sector discussion not needed response changed to Included | not needed | not needed | not needed | not needed | [5 empty] | Change made document updated
13 | Nic Donnelly | LINZ | Potable water | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | changed 28/2/2017 precision changed to 3 dec places, will need to ensure spec alignment with this | Included | Included | changed 28/2/2017 precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
14 | Nic Donnelly | LINZ | Buildings | Vol 1 | Use of spec | 4 | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | Included - addressed from previous comments | 2017-03-20 | Included | Included | Reviewed and Noted for Inclusion | Use of the Specification | 1 | [7 empty] | 1 | [6 empty] | check done |  | not needed | not needed | not needed | not needed | [5 empty] | No action
15 | Nic Donnelly | LINZ | Buildings | Vol 1 | 2.1.2 | 7 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | Included - addressed from previous comments | 2017-03-20 | Included | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 | [6 empty] | check done |  | n/a | n/a | n/a | done | [5 empty] | Change made document updated
16 | Nic Donnelly | LINZ | Stormwater | Vol 1 | Use of spec | v | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | Use of the Specification | 1 | [7 empty] | 1 | [6 empty] | check done |  | not needed | not needed | not needed | not needed | [5 empty] | No action
17 | Nic Donnelly | LINZ | Stormwater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Horizontal Coordinate System" to distinguish it from the vertical |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | 1 | [7 empty] | 1 | [6 empty] | check done |  | done | done | done | done | [5 empty] | Change made document updated
18 | Nic Donnelly | LINZ | Stormwater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Vertical Datum" since datums can also be horizontal |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | check done |  | done | done | done | done | [5 empty] | Change made document updated
19 | Nic Donnelly | LINZ | Stormwater | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 | [6 empty] | check done |  | done | done | done | done | [5 empty] | Change made document updated
20 | Nic Donnelly | LINZ | Wastewater | Vol 1 | Use of spec | v | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | Use of the Specification | 1 | [7 empty] | 1 | [6 empty] | change needed |  | not needed | not needed | not needed | not needed | [5 empty] | No action
21 | Nic Donnelly | LINZ | Wastewater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Horizontal Coordinate System" to distinguish it from the vertical |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
22 | Nic Donnelly | LINZ | Wastewater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Vertical Datum" since datums can also be horizontal |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
23 | Nic Donnelly | LINZ | Wastewater | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
24 | Nic Donnelly | LINZ | Wastewater | Vol 1 | Glossary | 112 | Glossary table |  |  |  | Update to NZVD2016 |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | Glossary | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
25 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Metadata terminology | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action
26 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Implementation | Statement noted. It is suppose to be a standard and not a specification. Vol 1 to be reviewed. No action required for Volume 2. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action
27 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Mandatory Fields | Statement noted. To be considered in business case. No changes required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action |  |  |  |  | 1 | 1
28 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | QA | Agreed. Action: Quality assurance will be undertaken in following releases | Vol 1 - Vol 2 |  | The drafts have now had a full publishing edit |  |  |  | Included | Included | The drafts have now had a full publishing edit | General | 1 | [7 empty] | 1 | [17 empty] | Changes made documents updated |  | N/A
29 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Mandatory Fields | Action. Mandatory fields to captured at a minimum levels. Mandatory fields to be looked at to remove non-essential attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The adoption of extents of fields is determined ny each organisation | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  | change comment as this is not the intent to allow variations more importantly need to address level of attributes to be collected | [9 empty] | No action
30 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Mandatory Fields | Action. Mandatory fields to captured at a minimum levels. Mandatory fields to be looked at to remove non-essential attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  | change comment as this is not the intent to allow variations more importantly need to address level of attributes to be collected | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action |  |  | y | completed
31 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | General | Agreed. Rewrite "In Summary", to reflect public asset ownership. Action on volume 1. | Vol 1 - Vol 2 |  | George |  |  |  | Noted: no action required | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [13 empty] | No action
32 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | NA | No action required, refers to future volumes. Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Future work is yet to be determined | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
33 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | NA | Asset categories are defined in Volume 1, changes can be transferred to Vol 2 as required. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | The classification has been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  | is this meant to say defined in the standard? | Yes , and changed |  |  | done | done | done | done | [5 empty] | Change made document updated |  | N/A
34 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | NA | Asset categories are defined in Volume 1, changes can be transferred to Vol 2 as required. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | The classification has been defined in the Standards Code Lists included | General | 1 | [9 empty] | 1 |  |  | is this meant to say defined in the standard? |  |  |  | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action |  | N/A
35 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | NA | Asset group, class not mentioned in Vol 2. Asset class only mentioned in Chapter 1. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | The classification has been defined in the Standards | General | 1 | [9 empty] | 1 |  |  | is this meant to say defined in the standard? | [12 empty] | No action |  | N/A
36 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards Code Lists included | General | 1 | [9 empty] | 1 |  |  | ok |  |  |  | naming resolved & codelists added | naming resolved & codelists added | naming resolved & codelists added | naming resolved & codelists added | [5 empty] | No action |  | N/A
37 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | Noted: no action required | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy |  |  |  | 1 | [6 empty] | 1 |  |  | ok |  |  |  | no action | no action | no action | no action | [5 empty] | No action
38 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Spatial | Action on volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The adoption of extents of fields is determined by each organisation | General for Hierarchy |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
39 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Data | Agreed. Action: Include confidence level in each schema. | Vol 1 - Vol 2 |  | Data quality is an analytical output - see for example the Harmonic data maturity scale |  |  |  | Excluded | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference |  | 1 | [6 empty] | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
40 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Mandatory Fields | Statement noted. Out of scope. For asset owners to determine the amount of data they collate. | Vol 1 - Vol 2 |  | Data quality is an analytical output - see for example the Harmonic data maturity scale |  |  |  | Noted: no action required | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | research by GISSA for our info only |  | no action | no action | no action | no action | [5 empty] | No action |  |  |  |  | 1 | 1
41 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Financial Performance | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action |  |  |  |  | 1 | 1
42 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Spatial | Action for Volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | Noted: no action required | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums |  |  |  | 1 | [6 empty] | 1 |  |  | ok |  |  |  | no action | no action | no action | no action | [5 empty] | No action
44 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Data | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Suggestion to be adopted in all documents in all tables. 26/3/2017 | Included | Included | Adjustment will be made to standards | General | 1 | [9 empty] | 1 |  |  | ok |  | change needed in docs |  | done | done | done | done | [5 empty] | Change made document updated |  | N/A
45 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. |  |  |  | Noted: no action required | Noted: no action required | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
46 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | In this context the unique id is created by the consultant as an audit trail before and after incorporation into asset owners systems | no action | no action | no action | no action | [5 empty] | No action
47 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Mandatory Fields | Agreed. Action required in both volumes. | Vol 1 - Vol 2 |  | George |  | Under Review | To be discussed with the TWG 25/03/2017 | Included | Included | Photographic Evidence is an optional attribute | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  |  |  | noted | noted | noted | noted | [5 empty] | change made document updated |  | N/A
48 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Mandatory Fields | Agreed. Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | 2017-03-25 | Noted: no action required | Noted: no action required | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | what are you saying? | This a code list of its own e.g confined space certification, working at heights etc. | make mention of change request create codelist and change field to point to code list | create sample c odelist | [8 empty] | request documented | New Code List proposed | Health & Safety Type
49 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Mandatory Fields | Agreed. Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Clarification to be provided for all fields that have this requirement in all documents. 26/3/2017 | Included | Included | Adjustment will be made to standards | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | done | done | done | n/a | [5 empty] | Change made document updated |  | N/A
50 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Spatial | Action for Volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | The area of work boundary is submitted at practical completion. It is only intended to record the area where works have been completed and will hold the common information about the project the project | Included | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | 1 | [7 empty] | 1 |  |  |  |  | why added to Vol 2 ? | For analytical purposes Have added 'geographical units' code list | [11 empty] | No action |  | ?
51 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Spatial | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
52 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under review | Have the code lists been distributed? 26/3/2017 | Included | Included | Code lists included in standards | 2.3.3 Retaining Structure | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | NOTED codelist added | n/a | NOTED codelist added | n/a |  |  |  |  | gauge input from next review | No action |  | N/A
53 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Condition | 1. Data scientist feedback 2. agree, yes. Action on volume 1. 3. agree, we can have design life unit as a new field. Action on volume 1 and 2. | Vol 1 - Vol 2 |  | To discuss |  |  |  | Sector Discussion | Included | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | 1 | [7 empty] | 1 | [7 empty] | please review yur response | [9 empty] | No action |  | ? | y | completed
54 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under review | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | Sector Discussion | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
55 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Mandatory Fields | Action on volume 1. | Vol 1 - Vol 2 |  | These standards are not about Treatment Plants |  |  |  | Noted: no action required | Noted: no action required | These standards are not about Treatment Plants | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
56 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Have the code lists been distributed? Can be assigned as sector discussion This detail was identified at the previous workshops and determined to be appropriate . 26/3/2017 | Included | Included | Code lists included in standards | General Equipment | 1 | [7 empty] | 1 |  |  |  |  | previoulsy missed | Code lists included | change needed in docs |  | NOTED codelist added | NOTED codelist added | NOTED codelist added | NOTED codelist added |  |  |  |  | gauge input from next review | Gauge input from next review |  | N/A
57 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | To be reviewed by the TWG for consideration of inclusion. 26/03/2017 | Sector Discussion | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | N/A
58 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | Noted: no action required | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
59 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Granularity | Agreed. Repair lengths to be recorded. A quantification of repair required. This feedback was requested from TWG but was not returned. Granularity question. Access point issues action on volume 1 | Vol 1 - Vol 2 |  | George |  | Under Review | Have the code lists been distributed? Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. 26/3/2017 | Included | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | NOTED codelist added | NOTED codelist added | NOTED codelist added | n/a |  |  |  |  | gauge input from next review | Gauge input from next review |  | N/A
60 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Financial Performance | No action required. Put .00 if no decimal is required. | Vol 1 - Vol 2 |  | Unit rates are given as such by Valuation Reporting standards |  |  |  | Noted: no action required | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
61 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | QA | Agreed. Action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | 1 | [7 empty] | 1 | [7 empty] | check if done | [9 empty] | No action |  | ? | y | completed | 1 | 1
62 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | QA | Agreed. Action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | 1 | [7 empty] | 1 |  |  |  |  | previously missed | Code lists included |  | check if done | [9 empty] | No action |  | ? | y | This is tables you provided in the 'introduction'. | 1 | 1
63 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Demand | Statement noted. This is captured in "Demand" schema, Vol 2. Catchment area is more design information and not necessarily required. | Vol 1 - Vol 2 |  | to discuss - catchment name reference name? |  |  |  | Sector Discussion | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes |  |  | 1 | [5 empty] | 1 |  |  |  |  | will the contrator know this at time of capture? Possibly for capital projects but not likley for subdivision developments Council can add post supply of data | For analytical purposes Have added 'geographical units' code list updated comment not answered | change needed |  | n/a | n/a | n/a | n/a | [5 empty] | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA) | codelilsts added
64 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | noted | Resolved in new version. 26/3/2017 | Noted: no action required | Noted: no action required | resolved in updated version | 2.5.1 Equipment |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok |  | change needed in docs |  | done | done | done | n/a | [5 empty] | Change made document updated
65 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 2 | Global Asset Metadata Schemata |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. |  |  | Vol 1 | Add Rigid and Flexible to code list |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Rigid and Flexible to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | document request | Response changed to Sector Discussion | [8 empty] | document request | New attribute proposed | Rigid or Flexible as option
66 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 3 | Risk |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 | [13 empty] | More information required for a decision
67 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 3 | Design Performance |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | More information required for a decision
68 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 4 | Volume 3 - 1 |  |  |  | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... |  |  | Vol 1 | AddCCTV & Laser Profiling testing to code list testing type |  |  | Haydn | 2017-03-14 | Included | Included | AddCCTV & Laser Profiling testing to code list testing type | General | 1 | [7 empty] | 1 | [17 empty] | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
69 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | Sector Discussion | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | 1 | [7 empty] | 1 | [6 empty] | document request | Response changed to Sector Discussion | make mention of change request | make mention of change request | make mention of change request | [6 empty] | New attribute proposed | Installer of Asset
70 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Sector Discussion | Included | Reviewed and Noted for Inclusion | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | Vol2 ? | Haydn please review | [9 empty] | More information required for a decision |  |  | y | Updated comment
71 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. |  |  | Vol 1 | Add Table |  |  | Haydn | 2017-03-14 | Included | Included | Add Table | General | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | GISSA to ADD table | add table | add table | add table | ?? | [5 empty] | New Code List entry for Condition Assessment Type proposed | Deflection Test
72 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation Format Instructions |  |  |  | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. |  |  | Vol 1 | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) |  |  | Haydn | 2017-03-14 | Noted: no action required | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
73 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Con_Ass_T |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | 1 | [7 empty] | 1 | [16 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
74 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Photo_Ref |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | 1 | [7 empty] | 1 | [16 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
75 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.1 | 53 | Access Chamber Attribute & Validation File Format Instructions Photo_Ref |  |  |  | Deflection Test result |  |  | Vol 1 | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | 2017-03-14 | Included | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | 1 | [7 empty] | 1 | [17 empty] | New Code List entry for Condition Assessment Type proposed | Compaction Test
76 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.1 | 55 | Access Chamber Attribute & Validation File Format Instructions Cov_Type |  |  |  | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) |  |  | Vol 1 |  |  |  | George/Haydn | If we agree on these then recommend ratification after documents are distributed. 14/03/2017 | Sector Discussion | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 |  |  |  |  | do we need more information before including in standards? | Changed final comment | make mention of change request | [9 empty] | request documented | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not)
77 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.1 | 56 | Access Chamber Attribute & Validation File Format Instructions Cov_RL |  |  |  | Seal Access Safety |  |  | Vol 1 |  |  |  | George/Haydn | If we agree on these then recommend ratification after documents are distributed 14/03/2017 | Sector Discussion | Included | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 |  |  |  |  | do we need more information before including in standards? | cant this be part of the H&S coment? | make mention of change request | [9 empty] | request documented | New Code List & entries proposed | Health & Safety Type
78 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.3 | 69 | Fittings Attribute & Validation File Format Instructions Material |  |  |  | Manufacturer Manufacturing Standard Third Party QA Accreditation |  |  | Vol 1 | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | 1 | [7 empty] | 1 | [17 empty] | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
79 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 72 | Pipe Attribute & Validation File Format Instructions Des_Life |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. |  |  | Vol 1 | Add Rigid and Flexible to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | Add Rigid and Flexible to code list | 2.4.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Haydn please explain how these will be included changed to Sector Discussion | [8 empty] | request documented | New attribute proposed | Rigid or Flexible as option |  | y | These are a code we need to add in the 'materials section'
80 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 73 | Pipe Attribute & Validation File Format Instructions Photo_Ref |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing / Laser Profiling / Compaction results to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
81 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 75 | Pipe Attribute & Validation File Format Instructions Pshape |  |  |  | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test |  |  | Vol 1 | Add Deflection Testing / Laser Profiling / Compaction results to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | Additional entries included in Code list Condition Assessment Type |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
82 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 75 | Pipe Attribute & Validation File Format Instructions Pshape |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing / Laser Profiling / Compaction results to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
83 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 77 | Pipe Attribute & Validation File Format Instructions Instl_Mthd |  |  |  | Rigid material standard and QA Separate Flexible material standard and it's QA |  |  | Vol 1 | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Haydn please explain how these will be included changed to Sector Discussion | [8 empty] | request documented | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA |  | y | Code list to materials type
84 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 78 | Pipe Attribute & Validation File Format Instructions Haunching |  |  |  | Foundation strength pre-install Compaction strength per NZS4566.2 |  |  | Vol 1 | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Included | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
85 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 78 | Pipe Attribute & Validation File Format Instructions Backfill |  |  |  | Compaction strength per NZS4566.2 |  |  | Vol 1 | More information required for a way forward |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | More information required for a way forward | 2.4.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | More information required for a decision |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
86 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 78 | Pipe Attribute & Validation File Format Instructions Manu |  |  |  | Third Party QA for pipe material manufacturer |  |  | Vol 1 | Third Party QA Accreditation to code lists |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Third Party QA Accreditation to code lists | 2.4.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
87 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 2 | Global Asset Metadata Schemata |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. |  |  | Vol 1 |  |  |  | George/Haydn | I get what is being said and see this as a conversation for appropriate design and construction practice to mitigate risk. I also see this as education for the industry that could be provided by companies like Hynds. What if this was the start of an educational series of seminars/webinars etc ? 10/3/2017 | Included | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  |  | do you want us to include new attributes? Wouldn’t this be defined by the pipe material and then added as a code? | Yes no change to comment Pipe Material not defining attribute | same as 66 | same as 67 | same as 67 | same as 67 | same as 67 |  | n/a | n/a | n/a | n/a | Make sure request documented | New attribute proposed | Rigid or Flexible as option
88 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 3 | Risk |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection Testing to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
89 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 3 | Design Performance |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection Testing to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
90 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 4 | Volume 3 - 1 |  |  |  | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... |  |  | Vol 1 | Add CCTV & Laser Profiling testing to code list testing type |  |  | Haydn | 2017-03-10 | Included | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
91 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" |  |  | Vol 1 |  |  |  | George/Haydn | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | Included | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments |  |  | 1 | [5 empty] | 1 |  |  |  |  | is there any action on our part? | Yes build a code list | make mention of change request manufacr=turer exists designer ? Installer ? Installer warranty ? | [9 empty] | request documented | New attribute proposed | Installer of Asset
92 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing/Laser Profiling result to code list |  |  | Haydn | isnt this part of the construction phase and recorded? 10/3/2017 | Included | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
93 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. |  |  | Vol 1 | Add Table |  |  | Haydn | 2017-03-10 | Included | Included | Add Table | 1.7 Heirarchy | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | [9 empty] | Create tabel and add to codelist and pivot table | Create entries Desktop Visual cctv laser etc
94 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation Format Instructions Des_Life |  |  |  | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. |  |  | Vol 1 | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) |  |  | Haydn | 2017-03-10 | Noted: no action required | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
95 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Comments |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-10 | Included | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
96 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Photo_Ref |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-10 | Included | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
97 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 44 | Pipe Attribute & Validation File Format Instructions Des_life |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. |  |  | Vol 1 | Add Rigid and Flexible to code list |  |  | Haydn | 2017-03-10 | Sector Discussion | Included | Add Rigid and Flexible to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | make mention of change request | changed to sector discussion | [8 empty] | request documented | New attribute proposed | Rigid or Flexible as option
98 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 44 | Pipe Attribute & Validation File Format Instructions Photo_Ref |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing/Laser Profiling result to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
99 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 48 | Pipe Attribute & Validation File Format Instructions PShape |  |  |  | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test |  |  | Vol 1 | haydn |  |  | Haydn | 2017-03-10 | Sector Discussion | Included | More information is required to inform a way forward | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | More information required for a decision |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
100 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 48 | Pipe Attribute & Validation File Format Instructions PShape |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing/Laser Profiling result to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
101 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 52 | Pipe Attribute & Validation File Format Instructions Haunching |  |  |  | Foundation strength pre-install Compaction strength per NZS4566.2 |  |  | Vol 1 | Add Foundation strength pre-install and compaction strength per NZ4566.2 |  |  | Haydn | 2017-03-10 | Included | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | make mention of change request | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | New Code List entry for Condition Assessment Type | Compaction Test per NZ4566.2 Foundation strength pre-install |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
102 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 52 | Pipe Attribute & Validation File Format Instructions Backfill |  |  |  | Compaction strength per NZS4566.2 or NZS3725 |  |  | Vol 1 | More information required for a way forward |  |  | Haydn | 2017-03-10 | Sector Discussion | Included | More information required for a way forward | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | More information required for a decision |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
103 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 52 | Pipe Attribute & Validation File Format Instructions Manu |  |  |  | Third Party QA for pipe material manufacturer |  |  | Vol 1 | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists |  |  | Haydn | 2017-03-10 | Included | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | [9 empty] | request documented | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
104 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | General | [5 empty] | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. |  |  | Vol 1 | Me either |  |  | Haydn | Have not seen this pdf with the attributes proposed 14/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
105 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 1.8 | 1 | Channel |  |  |  | Spillway should be its own Asset Class |  |  | Vol 1 |  |  |  | Under review | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. 14/03/2017 | Sector Discussion | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure |  |  | 1 | [5 empty] | 1 | [7 empty] | Request for details to be captured currently spillway covered as an asset type within Channels Class | [9 empty] | More information required for a decision
106 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 1.9 | 4 | Stormwater Asset Class |  |  |  | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) |  |  | Vol 1 |  |  |  | Under review | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. 14/03/2017 | Sector Discussion | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles |  |  | 1 | [5 empty] | 1 | [7 empty] | what kind of watercourse? Forebay = retention Bridge - roading Maintemnance track - roading Fence - roading Viewing platform - not in scope erososion protection - more information neeeded | [9 empty] | More information required for a decision
107 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Format Instructions |  |  |  | Source for what? This should have more detail. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Clarified the purpose of this field | Included | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | 1 | [7 empty] | 1 | [6 empty] | change needed doc | change in pivot table | done | done | done | done | [5 empty] | Change made document updated
108 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.3.2 | 27 | 2 |  |  |  | Does this include forebay bunds and pond banks associated with ponds? |  |  | Vol 1 |  |  |  | Under review | Incorporate forebay bunds and pond banks as code list types 14/03/2017 | Sector Discussion | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment |  |  | 1 | [5 empty] | 1 | [6 empty] | changed mind these are embankment types | changed to Included | [9 empty] | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks
109 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.3.3 | 37 | Figure 17 |  |  |  | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? |  |  | Vol 1 |  |  |  | Under review | Review the requirements for capture 14/03/2017 | Sector Discussion | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure |  |  | 1 | [5 empty] | 1 | [6 empty] | change needed | make mention of change request OFFER SUGGESTION | [9 empty] | More information required for a decision
110 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.3.3 | 43 | Retaining Structure Attribute & Validation File Format Instructions Link_ID |  |  |  | Bathymetry Attribute? |  |  | Vol 1 |  |  |  | George/Haydn | please say more about this. In what context would this attribute be used? | Included | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | 1 | [8 empty] | 1 |  |  |  | ok |  |  | suggest change to EXCLUDED as out of scope | [9 empty] | Haydn suggest this is excluded as I think it can be sourced from LINZ |  |  | y | we manage water bodies as part of stormwater and water asstes - we should add this
111 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | General | [5 empty] | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable |  |  | Vol 1 |  |  |  | Noted | GISSA reference for review - Z:\Clients Projects\LINZ Meta-Data Standard Project\Buildings\Building Draft Standards\Distributed\Buildings New Format - V1 1 DRAFT - gissa v12 20160619 - Distributed Uncontrolled Copy 20/03/2017 | Noted: no action required | Noted: no action required | GISSA reference for review - Z:\Clients Projects\LINZ Meta-Data Standard Project\Buildings\Building Draft Standards\Distributed\Buildings New Format - V1 1 DRAFT - gissa v12 20160619 - Distributed Uncontrolled Copy | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
112 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 1.3 | 1 |  |  |  |  | The Hierarchy table works well |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
113 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Global Asset Metadata Schemata | 2 |  |  |  |  | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Noted: no action required | Reviewed and Noted only for discussion | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | possible sector discussion this is the mandatory vs optional conversation | n/a | n/a | n/a | possible sector discussion this is the mandatory vs optional conversation | [5 empty] | No action |  |  | y | Updated comment
114 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 1.5 Data Principles | 3 |  |  |  |  | Complex requirement for such a large property portfolio |  |  | Vol 1 |  |  |  | Haydn | Noted 20/03/2017 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
115 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 1.6 Graphical Data Construction Principles | 4 |  |  |  |  | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? |  |  | Vol 1 |  |  |  | Noted | Reference to "please use sound CAD practices.." refers to the construction of linework 20/03/2017 | Noted: no action required | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
116 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.1 Accuracy Requirement for Locating Asset | 5 |  |  |  |  | This is a huge task for as constructed / as built for a large portfolio |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
117 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Asset Management Frameworks | 5 |  |  |  |  | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
118 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Asset Management Frameworks | 5 |  |  |  |  | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below |  |  | Vol 1 |  |  |  | Noted | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. 20/03/2017 | Noted: no action required | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | review and see where N/A and unknown is appropriate | [9 empty] | No action
119 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 Common Attributes Across all Asset Classes | 11 |  |  |  |  | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | This is selected versus a blanket option | Included | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | 1 | [8 empty] | 1 |  |  |  | ok |  |  |  | COMMUNICATION | COMMUNICATION | COMMUNICATION | COMMUNICATION | [5 empty] | No action
120 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 Common Attributes Across all Asset Classes | 11 - 244 |  |  |  |  | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes |  |  | 1 | [5 empty] | 1 |  |  |  |  | what is to be included? |  |  | updated comment suggest remove that it is to be included | n/a | n/a | n/a | NOTED | [5 empty] | More information required for a decision |  |  | y | no change
121 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 11-251 |  |  |  |  | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Noted 20/03/2017 | Noted: no action required | Included | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General |  |  | 1 | [6 empty] | 1 |  |  |  | not saying its to be included However comparison needed to ensure these areas covered or not Will do after release of documents suggest change this to sector discussion |  | review against standard |  | n/a | n/a | n/a | NOTED | n/a | n/a | n/a |  |  | No action
122 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 12 |  |  |  |  | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available |  |  | Vol 1 |  |  |  | Noted | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. 20/03/2017 | Noted: no action required | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
123 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 13 |  |  |  |  | V_Proc  what is this and what is it to relate to? |  |  | Vol 1 |  |  |  | Noted | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. 20/03/2017 | Noted: no action required | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
124 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 13 |  |  |  |  | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Haydn please provide wording for how this will be applied/linked 20/03/2017 | Included | Included | Tables will be referenced in Final Versions | General | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | n/a | [5 empty] | No action
125 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 17 |  |  |  |  | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. |  |  | Vol 1 |  |  |  | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. 20/03/2017 | Sector Discussion | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 |  |  | 1 | [5 empty] | 1 | [11 empty] | NOTED | [5 empty] | More information required for a decision
126 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Reference unknown- cut off page | [5 empty] | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Sector Discussion | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof |  |  | 1 | [6 empty] | 1 |  |  |  | your suggested response does not answer the question of why was it included. A wind loading table is not required as this is a calculated value | For analytical purposes updated comment Not answered | [5 empty] | THIS IS NOT WIND ZONES THIS IS A VALUE CALCULATED FIOR EACH BUILDING | [5 empty] | More information required for a decision
127 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Reference unknown- cut off page | [5 empty] | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
128 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Reference unknown- cut off page | [5 empty] | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
129 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone |  |  | Vol 1 |  |  |  | Haydn | I think this detail is to be provided at the time it was built not at time of capture? - thoughts?? This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Noted: no action required | Noted: no action required | I think this detail is to be provided at the time it was built not at time of capture? - thoughts?? This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
130 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
131 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Sector Discussion | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint |  |  | 1 | [6 empty] | 1 |  |  |  | your suggested response does not answer the question of why was it included. | For analytical purposes Have added 'geographical units' code list updated comment Not answered |  |  | n/a | n/a | n/a | codelists added | [5 empty] | Change made document updated
132 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Graffiti  irrelevant |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
133 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Flood  applicable only in related areas, and this information is on local council records |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
134 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 18, 20-250 |  |  |  |  | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? |  |  | Vol 1 |  |  |  | Haydn | Please refer to Volume 2. 20/03/2017 | Noted: no action required | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
135 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 20 |  |  |  |  | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose |  |  | Vol 1 |  |  |  | Noted | Addressed from previous comments see ID 131. 20/03/2017 | Noted: no action required | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 |  |  |  |  | SEARCH ON GEOTECHNICAL QUESTION |  |  |  |  | PREVIOUSLY COVERED | [5 empty] | No action
136 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 20 |  |  |  |  | Design life how is this applied to existing property |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
137 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 23 |  |  |  |  | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials |  |  | Vol 1 |  |  |  | Noted | This standard will be applicable to both residential and light commercial buildings. 20/03/2017 | Noted: no action required | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
138 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 24-25 |  |  |  |  |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
139 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 25-28 |  |  |  |  | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
140 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 28 |  |  |  |  | Finish  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
141 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 29 |  |  |  |  | Finish condition assessment, condition and repairs  ✓ The rest is superfluous |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
142 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 30 -34 |  |  |  |  | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satify both facilities management and asset management. With respect to cu metre please provide more information. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satify both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
143 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 34 |  |  |  |  | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. |  |  | Vol 1 |  |  |  | Noted | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
144 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 35 |  |  |  |  | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
145 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 35 |  |  |  |  | Design life  If new = Ok |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Excluded | Reviewed and Noted only | 2.4.1 Ceiling |  | 1 | [8 empty] | 1 | [6 empty] | no action | no action | no action | NOTED | [5 empty] | No action
146 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 35 |  |  |  |  | Cost  Not needed? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Included | Reviewed and Noted only | 2.4.1 Ceiling | 1 | [9 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
147 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 36 |  |  |  |  | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Included | Reviewed and Noted only | 2.4.1 Ceiling | 1 | [9 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
148 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 37 |  |  |  |  | Too much detail required for ceilings. Condition, material, surface finish = Yes |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
149 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 37 |  |  |  |  | Risk, Resilience, and Financial performance  Too much detail |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Included | Reviewed and Noted only | 2.4.1 Ceiling | 1 | [9 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
150 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 37 |  |  |  |  | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
151 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 40 |  |  |  |  | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling |  |  | 1 | [7 empty] | 1 |  |  | review your response as not consistent with question | updated comment | [5 empty] | COMMUNICATION | [5 empty] | More information required for a decision
152 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 40 |  |  |  |  | Smoke_Barr  Smoke relevant to multiunit development only. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
153 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 41 |  |  |  |  | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling |  |  | 1 | [7 empty] | 1 |  |  | review your response as not consistent with question | updated comment not answered | [5 empty] | NOTED | [5 empty] | Change made document updated
154 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 41 |  |  |  |  | Des_Life - ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
155 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 41 |  |  |  |  | Cost ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
156 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 42 |  |  |  |  | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
157 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 43 |  |  |  |  | Whole page  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
158 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 47 |  |  |  |  | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
159 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 47 |  |  |  |  | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
160 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Live load rating of floor à too difficult to define |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
161 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
162 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Repairs and Maintenance à what’s the need for this? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema |  |  | 1 | [7 empty] | 1 |  |  | what is to be included? | updated comment | [5 empty] | NOTED | [5 empty] | No action
163 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference |  |  | 1 | [7 empty] | 1 |  |  | what is to be included? | updated comment | [5 empty] | NOTED | [5 empty] | No action |  |  |  |  | 1
164 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 49 |  |  |  |  | First 5 rows à Very detailed for residential use. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
165 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 50 |  |  |  |  | Bracing is as per ceiling notes |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
166 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 52 |  |  |  |  | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor |  |  | 1 | [7 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | More information required for a decision
167 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 53 |  |  |  |  | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor |  |  | 1 | [7 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | More information required for a decision
168 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 54 |  |  |  |  | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
169 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 54 |  |  |  |  | Third row à Maybe |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
170 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 54 |  |  |  |  | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. |  |  | Vol 1 |  |  |  | Noted | The breakdown is provided to be clear and specific about the requirements. 20/03/2017 | Noted: no action required | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
171 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 55 |  |  |  |  | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. |  |  | Vol 1 |  |  |  | Noted | The breakdown is provided to be clear and specific about the requirements. 20/03/2017 | Noted: no action required | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
172 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 56 |  |  |  |  | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
173 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 57 |  |  |  |  | Multi storey application only. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
174 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 58 |  |  |  |  | - Multi storey application only. Too much detail required. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
175 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 59 |  |  |  |  | Last 5 yellow rows à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
176 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 60 |  |  |  |  | - 2nd row à ? Building Code complaint for new works. Unknown for much existing |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
177 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 60 |  |  |  |  | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
178 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 62 |  |  |  |  | Thermal barrier à ? Floor insulation is all that is relevant in residential. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
179 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 63 - 65 |  |  |  |  | All pages à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
180 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 66 |  |  |  |  | Whole page à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
181 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 67 |  |  |  |  | Acoustic row, content  maybe Cost  X Rest of page  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
182 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 68 |  |  |  |  | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
183 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 70 |  |  |  |  | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) |  |  | Vol 1 |  |  |  | Noted | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. 20/03/2017 | Noted: no action required | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
184 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 71 |  |  |  |  | Whole page  undefinable in existing housing. |  |  | Vol 1 |  |  |  | Noted | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. 20/03/2017 | Noted: no action required | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
185 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 72 |  |  |  |  | Vents  ✓ Membrane rows  Define what membrane? |  |  | Vol 1 |  |  |  | Noted | The membrane refers to the membrane between the foundation and the floor. 20/03/2017 | Noted: no action required | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
186 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 72 |  |  |  |  | Foundation area, content à ? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
187 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 73 |  |  |  |  | à See previous foundation notes |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | As the page numbers do not correspond with the document please provide additional comments for context. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
188 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 74-77 |  |  |  |  | All pages à ✕ |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | As the page numbers do not correspond with the document please provide additional comments for context. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
189 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? |  |  | Vol 1 |  |  |  | Noted | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
190 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Load wind/fix  Not known in existing stock |  |  | Vol 1 |  |  |  | Noted | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. 20/03/2017 | Noted: no action required | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
191 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Frame_Tr  not always identifiable Frame_ Sp  why? |  |  | Vol 1 |  |  |  | Noted | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
192 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Cost row à ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
193 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 80 |  |  |  |  | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
194 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 80 |  |  |  |  | Last 3 rows  Is this needed and how is it defined? |  |  | Vol 1 |  |  |  | Sector Discussion | Please specify the rows. 20/03/2017 | Sector Discussion | Sector Discussion | Please specify the rows. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
195 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 81 |  |  |  |  | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. |  |  | Vol 1 |  |  |  | Noted | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
196 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 81 |  |  |  |  | First row, QA Validation  N/A needs to be applied here |  |  | Vol 1 |  |  |  | Noted | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. 20/03/2017 | Noted: no action required | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
197 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 82 |  |  |  |  | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
198 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 82 |  |  |  |  | Last 5 rows  as per previous notes |  |  | Vol 1 |  |  |  | Sector Discussion | Please specify the rows. 20/03/2017 | Sector Discussion | Sector Discussion | Please specify the rows. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
199 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 83 |  |  |  |  | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ |  |  | Vol 1 |  |  |  | Noted | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
200 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 84 |  |  |  |  | Whole page  ✓ apart from: Cost row  ? |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
201 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 85 |  |  |  |  | First 3 rows  ? |  |  | Vol 1 |  |  |  | Sector Discussion | Please specify the rows. 20/03/2017 | Sector Discussion | Sector Discussion | Please specify the rows. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
202 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 85 |  |  |  |  | Last row, QA validation à Critical |  |  | Vol 1 |  |  |  | Sector Discussion | Please provide more information on the requirement. 20/03/2017 | Sector Discussion | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
203 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 86 |  |  |  |  | Risk  ✓ Resil, Des_Perf  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
204 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 87 |  |  |  |  | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
205 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 88 |  |  |  |  | Whole page à ✓ Apart from Cost row à ? |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
206 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 89 |  |  |  |  | First 3 rows à? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
207 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 89 |  |  |  |  | critically, QA Validation à Critical |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
208 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 90 |  |  |  |  | All 3 rows  ? Row 3  Too much detail |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
209 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 91 |  |  |  |  | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
210 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 92 |  |  |  |  | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
211 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 93 |  |  |  |  | All 4 rows  ✕, ?, ?, ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
212 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 94 |  |  |  |  | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
213 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 94 |  |  |  |  | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Not certain how to answer this one. 20/03/2017 | Included | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | No action
214 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 95 |  |  |  |  | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
215 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 96 |  |  |  |  | Whole page à✕. Risk – could relate to a water risks |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
216 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 97 |  |  |  |  | Whole page à ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
217 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 98-101 |  |  |  |  | Classifications, Masterpec, Enclosure à not sure what this is representing? |  |  | Vol 1 |  |  |  | Noted | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz 20/03/2017 | Noted: no action required | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | COMMUNICATION | [5 empty] | No action
218 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 101 |  |  |  |  | Ins-Type, R_Value à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
219 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 102 |  |  |  |  | Whole page  ✓ Insulation installer and warranty  maybe |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
220 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 103 |  |  |  |  | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
221 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 104-106 |  |  |  |  | Whole pink pages/part  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
222 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 109 |  |  |  |  | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable |  |  | Vol 1 |  |  |  | Noted | Not required for residential housing at Housing NZ | Noted: no action required | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
223 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 109 |  |  |  |  | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
224 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 110 |  |  |  |  | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
225 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 110 |  |  |  |  | Grout and Wall Structure Joint  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
226 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 111 |  |  |  |  | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
227 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 112 |  |  |  |  | Condition  ✓ Repairs  ? |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
228 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 113 - 115 |  |  |  |  | Structure, Bracing à As per floor and roof bracing |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
229 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 116 |  |  |  |  | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
230 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 118 |  |  |  |  | Wall, Design Life à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
231 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 119 |  |  |  |  | Condition  ✓ Cost row  ✕ Repairs  ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
232 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 121 |  |  |  |  | Fire barrier à Multiunit. May not be known on existing stock |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
233 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 124-125 |  |  |  |  | Orange à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
234 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 126 |  |  |  |  | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
235 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 132 |  |  |  |  |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
236 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 133 |  |  |  |  | Whole page à why would we use this information? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
237 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 134 |  |  |  |  | Acoustic and Thermal rating à Not used. Where applicable? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | 2017-03-20 | Noted: no action required | Reviewed and Noted only | Reviewed and Noted only | 2.5 Structure - Minor | 1 | [8 empty] | 1 |  |  |  | what is to be included? These fields already exist. | updated comment | [5 empty] | NOTED | [5 empty] | No action
238 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 137-138 |  |  |  |  | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
239 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 141 |  |  |  |  | à Why / how would we use this? Too much information required. |  |  | Vol 1 |  |  |  | Noted | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. 20/03/2017 | Noted: no action required | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
240 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 142 |  |  |  |  | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
241 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 143 |  |  |  |  | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
242 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 144 - 146 |  |  |  |  | Pages  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
243 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 151 |  |  |  |  | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | not certain what is being suggested. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
244 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 151 |  |  |  |  | Framed and Frame material à not defined in window anatomy page 149 |  |  | Vol 1 |  |  |  | Sector Discussion | Update diagram on p149 | Sector Discussion | Sector Discussion | Update diagram on p149 | 2.5.3 Windows |  |  | 1 | [5 empty] | 1 | [6 empty] | change needed | update diagrams for buildings GISSA TO FIND DIAGRAMS | n/a | n/a | n/a | REVIEW DIAGRAM | [5 empty] | Modify Diagram
245 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 151 |  |  |  |  | Height of windows in mm à what value? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | am open to suggestions. 20/03/2017 | Noted: no action required | Reviewed and Noted only | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | NOTED | [5 empty] | No action
246 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Condition  ✓ Width  why needed? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | am open to suggestions. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
247 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Manufacturer, warranty, installation date, installer àUnknown on existing |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
248 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Design life à How to define? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
249 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Repairs à ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
250 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 153 |  |  |  |  | Page à✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
251 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 154-156 |  |  |  |  | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
252 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 156 |  |  |  |  | Hardware à Locks, Yes. Lever/knobs maybe. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
253 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 157 |  |  |  |  | Whole Column Name – Full is circled à Not always known on existing. Why needed? |  |  | Vol 1 |  |  |  | Noted | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. 20/03/2017 | Noted: no action required | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action
254 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 157-159 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
255 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6 Utilities | 163 |  |  |  |  | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | 2017-03-20 | Included | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | 1 | [8 empty] | 1 |  |  |  | your suggested response does not answer the question of why was it included. | updated comment | [5 empty] | NOTED | [5 empty] | No action
256 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6 Utilities | 164 |  |  |  |  | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6 Utilities |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
257 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6 Utilities | 164 |  |  |  |  | Services, pink section àmore commercial application. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6 Utilities |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
258 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.2 Electrical Components (Polyline) | 168-170 |  |  |  |  | à No! How is this captured realistically and why? |  |  | Vol 1 |  |  |  | Haydn | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
259 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.3 HVAC-General (Point) | 172-175 |  |  |  |  | Not applicable to Residential |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
260 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.4 | [5 empty] | Not applicable to Residential |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
261 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.5 | [5 empty] | Not applicable to Residential |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
262 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Plumbing – Fittings (point) | 187 |  |  |  |  | à Would we use this at a per item attribute? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
263 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Plumbing – Fittings (point) | 188 |  |  |  |  | Type à ✓ Last row, content à NA |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
264 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.7 Plumbing – Pipework (Polyline) | 192 |  |  |  |  | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
265 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.7 Plumbing – Pipework (Polyline) | 194 |  |  |  |  | àToo difficult and unnecessary info |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
266 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7 Services | 197 |  |  |  |  | à Stove have heater fans |  |  | Vol 1 |  |  |  | Noted | Included as part of the product fact sheet provided with the appliance. 20/03/2017 | Noted: no action required | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action
267 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7 Services | 198 |  |  |  |  | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
268 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7 Services | 199 |  |  |  |  | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
269 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.72 Data & Communication (Point) | 202 |  |  |  |  | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
270 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.72 Data & Communication (Point) | 203 |  |  |  |  | Pink section  Not sure how much of this is required/useful |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
271 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 211 |  |  |  |  | Blue section - ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
272 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 211 |  |  |  |  | Asset type à ✓ Kitchen Vanities in contents |  |  | Vol 1 |  |  |  | Included | Add to codelist | Included | Included | Add to codelist | 2.7.4 Fixtures & Fittings | 1 | [8 empty] | 1 | [10 empty] | DONE NEW CODE LIST ENTRY | [5 empty] | New Code List entry for Fittings Type proposed | Kitchen Vanities
273 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 211 |  |  |  |  | Length, Height, Width à Why? |  |  | Vol 1 |  |  |  | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. 20/03/2017 | Sector Discussion | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings |  |  | 1 | [6 empty] | 1 | [5 empty] | make mention of change request |  | n/a | n/a | n/a | NOTED | n/a | n/a | n/a | n/a | request documented | More information required for a decision
274 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 212 |  |  |  |  | Whole page à Doubt this would be known |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
275 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.5 Fire Protection Components (Point) | 217 |  |  |  |  | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
276 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.6 Fire Protection Components | 221 |  |  |  |  | à Covered in Building WOF. *Specialist area = consultant needed = $$ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
277 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.7 Lifts (Polygon) | 226 |  |  |  |  | àSpecialists information and only applicable to multi-unit/storey complexes. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
278 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.9 Security (Point) | 237 |  |  |  |  | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.9 Security |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
279 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.10 Signage | 242 |  |  |  |  | à Not so useful in residential and difficult to maintain/update. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
280 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.8.1 Space (Polygon) | 248 |  |  |  |  | à Not really applicable to existing housing. Maybe some use in multi-unit development. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.8.1 Space |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
281 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 252 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
282 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 254 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Will have a particular application for connection to civil works. | Included | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | NOTED | [5 empty] | No action
283 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 255 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
284 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 256 |  |  |  |  | Material à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
285 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 257 |  |  |  |  | Pipe type à ✕ |  |  | Vol 1 |  |  |  | Noted | Required for assets recorded in a building 20/03/2017 | Noted: no action required | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
286 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 257 |  |  |  |  | Water type à ? |  |  | Vol 1 |  |  |  | Noted | To address if this is potable, recycled, raw etc. 20/03/2017 | Noted: no action required | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
287 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | General | [5 empty] | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | General | Statement noted. To be considered in business case. No changes required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
288 | Andy Walmsley | Housing NZ | Buildings | Vol 2 |  | iv |  |  |  |  | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Front End | Rewrite "In Summary", to reflect public asset ownership. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Edited to make clearer | No Specific Reference | 1 | [8 empty] | 1 | [10 empty] | CHGNAGE DONE COMMUNICATION | [5 empty] | No action |  | Modified text |  |  | 2 | 2
289 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.1 Purpose of this Document | 8 |  |  |  |  | This document excludes industrial buildings and Ancillary building’s  provide examples | Front End | Remove Table 1. Table 1 and reference are no longer needed, as two standards are combined, refers to the building act. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 2 | 2
290 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.1 Purpose of this Document | 9 |  |  |  |  | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Front End | Remove Table 1. Table 1 and reference are no longer needed, as two standards are combined, refers to the building act. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 2 | 2
291 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.1 Purpose of this Document | 10 |  |  |  |  | Added Laundry to Outbuildings, included in the Residential standard | Front End | Remove Table 1. Table 1 and reference are no longer needed, as two standards are combined, refers to the building act. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 2 | 2
292 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.2 Structure of Standard | 10 |  |  |  |  | The bullet points à are they attributes or measures? | Front End | Changed this to schema's and align with cohorts. | Vol 2 |  |  | Included in draft |  |  | Included | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  |  | y | completed | 2 | 2
293 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.2 Structure of Standard | 12 |  |  |  |  | What is Boolean data type? | Front End | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Vol 2 |  |  | noted |  |  | Excluded | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type |  | 1 | [7 empty] | 1 | [7 empty] | no action | no action | no action | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
294 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.4 Context of Asset Data and Analytics | 16-17 |  |  |  |  | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Vulnerability | Vulnerability Schema has now been added -was missing from draft. No change required. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | already done | y | no change | 2 | 2
295 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.4 Context of Asset Data and Analytics | 17 |  |  |  |  | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Criticality | Agreed. Action: Wording will be changed to clarify: e.g. removal/failure | Vol 2 |  |  | Yes it is also failure, in a broad sense. More reflects removal of service of asset (for example, the asset could be turned off), as opposed to failure per se |  |  | Included | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | no action |  | ? | y | Updated comment | 2 | 2
296 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.4 Context of Asset Data and Analytics | 18 |  |  |  |  | The third and fourth suite of analytics à seems very granular? | Front End | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2 | 2
297 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | Asset Management Frameworks (volume 5) | 19 |  |  |  |  | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Front End | No change required. Only intended as examples. A full list applicable to everyone HNZ through Corrections, MoE etc. would be enormous. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | References are being considerd | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
298 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.8 Theory and practice | 29 |  |  |  |  | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Front End | Updated | Vol 2 |  |  | Included in draft |  |  | Included | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  |  | y | no change | 2 | 2
299 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2 Condition Schema | 30 |  |  |  |  | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Condition | No change required. This is a metadata standard., not a condition manual. Each organisation needs to decide their own frequency. Condition is a snapshot at any given time which, together with age and working life can be used to assess when an asset may need attention ($). | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action |  |  |  |  | 2 | 2
300 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2.3 Interfaces with Other Schema | 31 |  |  |  |  | Table 4. à unclear what this actually shows? | Condition | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Vol 2 |  |  | Noted |  |  | Noted: no action required | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action |  |  |  |  | 2 | 2
301 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2.4 Assessing Asset Condition | 32 |  |  |  |  | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Condition | 2.06 & 2.07Atributes optional. 2.11 Attribute optional. 2.12 Attribute optional. 2.14 & 2.15 They are calculated but are estimates yes. No changes required. | Vol 2 |  |  | Adjusted in draft |  |  | Included | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | modified mandatory fields | y | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | 2 | 2
302 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2.5.1 Description of Condition Rating | 36 |  |  |  |  | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Condition | Agreed. Action: to add. | Vol 2 |  |  | George | For action | Is this addressed in the work you did? 26/3/2017 | Included | Included | Updated in draft Standards | Code List 16: Condition Rating | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed in docs | check if done | n/a | n/a | n/a | [6 empty] | No action |  |  | y | completed | 2 | 2
303 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 3.4 Components | 42 |  |  |  |  | Operations definition à What does this mean? Is this routine/preventative maintenance? | Repairs, Maintenance & Operations | Maintenance attributes defined in Volume 2 | Vol 2 |  |  | George |  |  | Noted: no action required | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [6 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
304 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 3.4 Components | 43-45 |  |  |  |  | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Repairs, Maintenance & Operations | 3.02 is Planned, Reactive or operational. no action required. 3.03-3.05 Agreed. Action: Other then start date, all optional. 3.08 Agreed, action: should be optional. 3.14-3.15 Agreed. Action: should be optional as answer may be "zero" 3.16 Agreed, action: change to optional. 3.19 No action needed. Example "it broke because we didn't maintain it -e.g. didn't lubricate bearings". 3.20 No action needed. Attempts to capture future maintenance obligations. 3.22 & 3.23 No action needed. Not mandatory as it may be a reactive repair 3.24 No action needed. Not much point in recording any of this info if we don't capture cost 3.26 & 3.27 Agreed. Action: take out information. Not vital in this context. | Vol 2 |  |  | Adjusted in draft |  |  | Included | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  | modified mandatory fields | y | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | 2 | 2
305 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 3.4 Components | 43-45 |  |  |  |  | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Repairs, Maintenance & Operations | 3.04 -3.06 Agreed, it's optional. No action needed. 3.08 Action: needs to be an optional field. Your comment seems to refer to multiple items that might be done on one "Job" for an individual asset (Say a house). 3.09 Agreed. Action: change to optional field. 3.19 & 3.20 Agreed, Action: change to optional field. Capex is not covered by this schema. That's defined as replacing the asset at end of life. This is about repairing it during its life. No action required. | Vol 2 |  |  | George and Adjusted in draft |  |  | Included | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  | modified mandatory fields | y | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | 2 | 2
306 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 4.4 Calculating Utilisation | 50-51 |  |  |  |  | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Utilisation | If you decide to fill it in, some attributes are required and other aren't. 4.06 & 4.07 No action needed. They may be contracted out not all orgs will do in-house 4.06 - 4.09 Optional. | Vol 2 |  |  | Included in draft |  |  | Sector Discussion | Included | Mandatory / Optimal and Optional will be discussed | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | modified mandatory fields | y | Updated comment | 2 | 2
307 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 4.5 Utilisation Code Lists | 52 |  |  |  |  | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Utilisation | Will vary for different building types | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
308 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 5.4 Calculating Demand | 55 |  |  |  |  | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Demand | No action required. HNZ has X houses with Y beds, the demand for this housing is presumably different to X and Y we should be able to put one figure over the other to produce a percentage. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2 | 2
309 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 6.2 Purpose of Schema | 59 |  |  |  |  | 1st bullet point à E.g. roof? Fire alarms? | Criticality | Can be as granular as needed. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Can be as granular as needed. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
310 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 6.6 Calculating Critically | 61 |  |  |  |  | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Criticality | Change reference. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Updated in Draft Standards | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  | ? | y | Updated comment | 2 | 2
311 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.1 Definition of risk | 67 |  |  |  |  | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Risk | Definition is based on the guidelines, not an exact copy. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
312 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.4 Components of Risk | 68 |  |  |  |  | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Risk | No change required. This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2 | 2
313 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.4 Components of Risk | 69 |  |  |  |  | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Risk | Phrases deleted in newer version. A new schema covering vulnerability has now been created and separated from Risk or Criticality. No action required. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | N/A | y | completed | 2 | 2
314 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.4 Components of Risk | 69 |  |  |  |  | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Risk | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
315 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.5 Calculating Risk | 69 |  |  |  |  |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Risk | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
316 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.5 Calculating Risk | 70 |  |  |  |  | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Risk | It's optional depending on the granularity of asset data collection. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
317 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 Risk Code lists | 72 |  |  |  |  | Code G, Malicious damage à Does this include tenant damage? | Risk | Yes | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
318 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 Risk Code lists | 73 (code List 22) |  |  |  |  | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Risk | Tables are based on the guidelines, not an exact copy. No action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
319 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 Risk Code lists | [5 empty] |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Risk | The purpose of the table is to provide the needed information without having to consult another document. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
320 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.7 Consequence Table | 73, 74-79 (code list 22 & 23) |  |  |  |  |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Risk | We require one standard for all organisation or we can't compare them. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
321 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.7 Consequence Table | 73, 74-79 (code list 22 & 23) |  |  |  |  |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Risk | Noted. Action: need rewrite, two paragraphs are too similar to reflect difference. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 | [5 empty] | 1 | [6 empty] | check if done CHANGE STATUS TO INCLUDED | [9 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  | y | Updated comment | 2
322 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.7 Consequence Table | 73, 74-79 (code list 22 & 23) |  |  |  |  |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Risk | Each organisation needs to determine at what level risk will be determined. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
323 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 & 7.7 | [5 empty] | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Risk | No action required. That is what this review is hoping to achieve. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
324 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 8 Resilience Schema | 82 |  |  |  |  | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Resilience | No action required. Understood. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. Understood. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
325 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.3 Interface with Other Schema | 95 (table 13) |  |  |  |  | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Financial Performance | Noted and Updated | Vol 2 |  |  | Included in draft |  |  | Included | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  | N/A | y | Updated comment | 2
326 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 97 (table 10) |  |  |  |  | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Financial Performance | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | To discuss with technical Working Groups |  |  |  |  | 2
327 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 99 (table 10a) |  |  |  |  | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Financial Performance | The attribute is optional. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | The attribute is optional. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
328 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 104 (table 10d) |  |  |  |  | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Financial Performance | If you can't identify what it is replacing, it is default a new asset. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
329 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 103 (table 10c) |  |  |  |  | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Financial Performance | Each organisation needs to determine at what levelof granularity will suffice. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
330 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 11.6 Service Performance Attributes | 109-112 |  |  |  |  | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Service Performance | These items are scored in Table 11a & code lists following. They are very subjective assessments and most are optional. Some items should be easily scorable like accessibility. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | These ar at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
331 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 1.5 | 2 | 1 |  |  |  | Add USB memory sticks/hard drives to this list. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | changed 28/2/2017, also for all other specs | Included | Included | changed 28/2/2017, also for all other specs | 1.5 Deliverables | 1 | [8 empty] | 1 | [5 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
332 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 1.5 | 3 | Construction Company |  |  |  | Question: Are there requirements for developers to retain information after transmission? |  |  | Vol 1 |  |  |  | Noted | relevance? We see this as something for the developer to make the call if they retain a copy or not. 28/2/2017 | Noted: no action required | Noted: no action required | relevance? We see this as something for the developer to make the call if they retain a copy or not. 28/2/2017 | 1.5 Deliverables |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
333 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.1.3 | 8 | Dates |  |  |  | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. |  |  | Vol 1 |  |  |  | Noted | keep current practice. 28/2/2017 | Excluded | Excluded | keep current practice. 28/2/2017 | 2.1.5 Attribute Data Fields |  | 1 | [7 empty] | 1 | [7 empty] | no action | no action | no action | n/a | [5 empty] | No action
334 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.1.8 | 14 | Unique_ID |  |  |  | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? |  |  | Vol 1 |  |  |  | Noted | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. 28/2/2017 | Noted: no action required | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. 28/2/2017 | 2.1.10 Common Attributes |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
335 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.2.1 | 18 | Permit_No |  |  |  | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? |  |  | Vol 1 |  |  |  | Under Review | need to determine impact of including 'extended' alpha-numeric characters 28/2/2017 | Sector Discussion | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters 28/2/2017 | 2.2.1 Area of Work Extent |  |  | 1 | [6 empty] | 1 | [16 empty] | More information required for a decision
336 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.1 | 25 | Length_m |  |  |  | For circular assets, should length and width both be populated and be the same (diameter)? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | For circular assets, length is not required and will be made conditional 28/2/2017 | Included | Included | For circular assets, length is not required and will be made conditional 28/2/2017 | 2.3.1 Containment Structure | 1 | [8 empty] | 1 | [5 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
337 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.1 | 25 | Length_m |  |  |  | Rename to Length Metres for consistency |  |  | Vol 1 |  |  |  | INCLUDED - DOC | change all instances to length metres and length millimetres as appropriate 28/2/2017 | Included | Included | change all instances to length metres and length millimetres as appropriate 28/2/2017 | 2.3.1 Containment Structure | 1 | [8 empty] | 1 | [5 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
338 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.1 | 27 | OS_RL |  |  |  | Overflow = OS? What does OS stand for? Should this be OF? |  |  | Vol 1 |  |  |  | Noted | this term was agreed to by the TWG, retain 28/2/2017 | Noted: no action required | Noted: no action required | this term was agreed to by the TWG, retain 28/2/2017 | 2.3.1 Containment Structure |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
339 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.4 | 41 | 1 |  |  |  | Earlier wells were requested to be polygon type. Is the point supplementary? |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | typo corrected, should be polygon 28/2/2017 | Included | Included | typo corrected, should be polygon 28/2/2017 | 2.3.4 Well | 1 | [8 empty] | 1 | [5 empty] | done | change needed | done | come back to this as not included at moment | done | n/a |  |  |  |  | come back to this as not included at moment | Change made document updated
340 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.4.6 | 69 | Note |  |  |  | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? |  |  | Vol 1 |  |  |  | George/Haydn | need more information, 2.4.6 refers to a pumping station? 28/2/2016 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station |  |  | 1 | [6 empty] | 1 |  |  |  | ok |  |  | It is upto each asset owner to determine the most appropriate way to manage non authority data | no action | no action | no action | n/a | [5 empty] | More information required for a decision
341 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.5.1 | 92 | Manu |  |  |  | I believe this table and its attribute names have become mis-aligned. |  |  | Vol 1 |  |  |  | Under Review | Looks OK, need more information 28/2/2017 | Sector Discussion | Sector Discussion | Looks OK, need more information 28/2/2017 | 2.5.1 Equipment |  |  | 1 | [6 empty] | 1 | [16 empty] | More information required for a decision
342 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 1.6 | 3 | R&M/O |  |  |  | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? |  |  | Vol 1 | Not the intention, all replacements are 'new assets' when replaced |  |  | Haydn | cant see that myself 10/03/2017 | Noted: no action required | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | n/a | [5 empty] | No action
343 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 1.8 | 3 | Pumping Station |  |  |  | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. |  |  | Vol 1 | The standrds are recording as-constructed |  |  | Haydn | This is indicative and expect to be advised by Council 10/03/2017 | Noted: no action required | Noted: no action required | The standrds are recording as-constructed | 1.8 Theme Structure |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
344 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 1.8 | 3 | Valve |  |  |  | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? |  |  | Vol 1 | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID |  |  | Haydn | Is this a question of how each organisation will record and manage? 14/3/2017 | Noted: no action required | Noted: no action required | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
345 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.1.1 | 6 | 2 |  |  |  | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. |  |  | Vol 1 |  |  |  | Noted | 2017-03-10 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
346 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.1.1 | 6 | 6 |  |  |  | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. |  |  | Vol 1 | That is a special case, the spatial component is a standard requirement for all infrastructure |  |  | Haydn | would be happy to discuss with him 10/03/2017 | Noted: no action required | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
347 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.2.1 | 17 | 1 |  |  |  | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. |  |  | Vol 1 |  |  |  | George/Haydn | Can this be added into the comments field where from a different project? 14/03/2017 | Sector Discussion | Included | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent |  |  | 1 | [6 empty] | 1 |  |  |  | change to sector discussion for consideration for inclusion |  | make mention of change request | [9 empty] | request documented | More information required for a decision
348 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.2.1 | 17 | 1 |  |  |  | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? |  |  | Vol 1 |  |  |  | Noted | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed 14/03/2017 | Noted: no action required | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
349 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | 3 |  |  |  | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. 14/3/2017 | Included | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | 1 | [7 empty] | 1 | [6 empty] | make mention of change request clarify comment |  | done | done | done | n/a |  |  |  |  | request documented | Change made document updated
350 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | Figure 4 |  |  |  | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. |  |  | Vol 1 |  |  |  | Noted | see comment 349 14/03/2017 | Noted: no action required | Noted: no action required | see ID 349 | 2.3.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
351 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | Figure 4 |  |  |  | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? |  |  | Vol 1 |  |  |  | Noted | see comment 349 14/03/2017 | Noted: no action required | Noted: no action required | see ID 349 | 2.3.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
352 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 21 | 2 |  |  |  | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. |  |  | Vol 1 |  |  |  | Noted | The polygon refers to the interior of the structure 14/03/2017 | Noted: no action required | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
353 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.3 | 34 | 4 |  |  |  | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. |  |  | Vol 1 |  |  |  | Noted | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. 14/03/2017 | Noted: no action required | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. | 2.3.3 Fitting |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
354 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.3 | 34 | Figure 8 |  |  |  | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? |  |  | Vol 1 |  |  |  | Noted | Whatever is stated in the attributes 14/03/2017 | Noted: no action required | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
355 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.3 | 34 | Figure 8 |  |  |  | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. |  |  | Vol 1 |  |  |  | George/Haydn | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | Sector Discussion | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
356 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 3 |  |  |  | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. |  |  | Vol 1 |  |  |  | George/Haydn | It has been identified through the workshops that this level of detail is required to efefctively manage the asset. 14/03/2017 | Sector Discussion | Included | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe |  |  | 1 | [6 empty] | 1 |  |  |  | suggest that direction is provided otherwise it will be a smorgasbord or requirements suggested by each organisation creating uncertainty for the data providers | Will do that but how is a discussion with the sector | [11 empty] | More information required for a decision
357 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 6 |  |  |  | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. |  |  | Vol 1 |  |  |  | Under Review | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. 14/03/2017 | Sector Discussion | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
358 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 8 |  |  |  | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-14 | Included | Included | Precision is defined in the standards | 2.3.4 Pipe | 1 | [8 empty] | 1 |  |  |  | what is to be included? | updated comment |  |  | done | done | done | n/a | [5 empty] | No action
359 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 10 |  |  |  | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. |  |  | Vol 1 |  |  |  | Under Review | Please be specific about which statements 14/03/2017 | Sector Discussion | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
360 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 11 |  |  |  | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. |  |  | Vol 1 |  |  |  | Noted | Please refer to the example for the irregular shaped structures 14/03/2017 | Noted: no action required | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
361 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 12 |  |  |  | These changes should be coded into the pipe geometry, not as separate notes about the pipe. |  |  | Vol 1 |  |  |  | Under Review | Please be specific about which statements 14/03/2017 | Sector Discussion | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
362 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 12 |  |  |  | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Noted adjustments will be made for consistency. 14/3/2017 | Included | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Changes made documents updated
363 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 12 |  |  |  | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. |  |  | Vol 1 |  |  |  | Under Review | Please provide examples of specific instances so they can be considered for inclusion 14/03/2017 | Sector Discussion | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [11 empty] | n/a | [5 empty] | More information required for a decision
364 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 43 | Unique_ID |  |  |  | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. |  |  | Vol 1 |  |  |  | Noted | There will be two assets provided therefore there will be two contractor ID's 14/03/2017 | Noted: no action required | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
365 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 43 | Owner |  |  |  | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
366 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 44 | Cost |  |  |  | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. |  |  | Vol 1 | ODRC / ORC / RC are included |  |  | Haydn | 2017-03-14 | Included | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
367 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 51 | Grnd_Water |  |  |  | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. |  |  | Vol 1 |  |  |  | George/Haydn | Have no view on this 14/03/2017 | Sector Discussion | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe |  |  | 1 | [6 empty] | 1 |  |  |  | this discussion is not aboput the actual pipe but about the attribute fields of soil etc in the pipe table. Please review and re draft response | updated comment not answered | [11 empty] | More information required for a decision
368 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 52 | RI_Rn_Mtd |  |  |  | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? |  |  | Vol 1 |  |  |  | George/Haydn | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | Included | Included | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | 1 | [8 empty] | 1 |  |  |  | ok | [12 empty] | No action
369 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 53 | RI_RN_Mat |  |  |  | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes |  |  | Vol 1 |  |  |  | George/Haydn | The date of construction is to be used. Was the thickness recorded to address heat transfer? What is the impact of it not being recorded? 14/03/2017 | Sector Discussion | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
370 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.7.2 | 106 | 3 |  |  |  | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. |  |  | Vol 1 |  |  |  | George/Haydn | There is no obligation for the consultant to match their data to the existing infrastructure. The obligation is to show where existing infrastructurwe does not align with the new infrastruture from a mapping perspective. That is from mapping data they have been proviided with and are expected to align to. There are two aspects to this requirement. Firstly that the consultant identifies the anomaly and secondly that the Local Governmnet addresses the adjustment in their information systems. 14/03/2017 | Sector Discussion | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
371 | Gerri Waterkamp | Auckland Transport | Stormwater | Vol 1 & Vol 2 | General | [5 empty] | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Comments noted. Workshops will be held in May for further contribution | Sector Discussion | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
372 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | What are the timeframes for this being adopted as mandatory? | Implementation | Business Case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case. | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | NO ACTION | NO ACTION | NO ACTION | NO ACTION | [5 empty] | No action
373 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Will there be a further round of submissions / comments? | Implementation | Yes. Seminars in November. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Yes. Seminars in November. | N/A |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | NO ACTION | NO ACTION | NO ACTION | NO ACTION | [5 empty] | No action
374 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Mandatory Fields | Mandatory - industry best practice - optional to be included. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Mandatory, Optimal, Optional will be discussed with the sectors | General | 1 | [7 empty] | 1 |  |  |  |  | review with haydn when will optional be included and how selected | Mandatory vs Optimum vs Optional Data sets |  | action needed once agreed with haydn | action needed once agreed with haydn | action needed once agreed with haydn | action needed once agreed with haydn | action needed once agreed with haydn | [5 empty] | More information required for a decision |  | ? | y | Updated comment
375 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Implementation | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
376 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Volume Interaction | Statement noted. HR to confirm. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | Sector discussion |  |  |  |  | 2
377 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Coverage | Action - to be looked at by Opus. | Vol 1 - Vol 2 |  | Treatment is not included |  |  |  | Noted: no action required | Noted: no action required | Treatment is not included | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
378 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | 1 | [8 empty] | 1 |  |  |  | ok |  | review against standard |  | done | done | done | n/a | [5 empty] | Changes made documents updated |  | N/A
379 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Treatment is not included |  |  |  | Noted: no action required | Noted: no action required | Included in Instruments | Instruments |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
380 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Endeavouring to differentiate information 26/3/2017 | Noted: no action required | Noted: no action required | Separate sections of data cohorts | General |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | No action
381 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | noted | Comments noted. Workshops will be held in May for further contribution. | Sector Discussion | Noted: no action required | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
382 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | QA | Statement noted. To be actioned. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Statement noted. To be actioned. | General | 1 | [8 empty] | 1 |  |  |  | previously missed still some xx placegolders for haydn to address at start of document | Publishers edit completed | change needed in docs |  | done | done | done | done | [5 empty] | Changes made documents updated |  | ?
383 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | Sector Discussion | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well |  |  | 1 | [6 empty] | 1 |  |  |  | ok |  |  |  | no action | no action | no action | no action | [5 empty] | No action |  | N/A
384 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Modify section 1.5 to remove CD label representation and include with section 1.5.1 table. 26/3/2017 | Included | Included | Standards will be updated | 1.5 Deliverables | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed in docs |  | done | done | done | done | [5 empty] | Changes made documents updated |  | N/A
385 | Jennifer Carew | Waipa Distric Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Mandatory Fields | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | Vol 1 - Vol 2 |  | noted |  |  |  | Sector Discussion | Included | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | 1 | [8 empty] | 1 | [6 empty] | action needed once agreed with haydn | [9 empty] | More information required for a decision |  | ? | y | Updated comment
386 | Graham Clark | Christchurch City Council | Wastewater | Vol 1 | General | [5 empty] | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | no action | [5 empty] | No action
387 | Graham Clark | Christchurch City Council | Wastewater | Vol 1 | Abstract | i | 1 |  |  |  | a standardised approach to the collation of data relating to As Built (As Constructed) asset information |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | Abstract |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | no action | [5 empty] | No action
388 | Graham Clark | Christchurch City Council | Wastewater | Vol 1 | Executive Summary | iv | 4 |  |  |  | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. |  |  | Vol 1 | Could do yes - I can add in |  |  | Haydn | Do you want to include? 14/03/2017 | Included | Included | Will consdider for final edit - happy to add in. | Executive Summary | 1 | [8 empty] | 1 | [6 empty] | check with haydn | [9 empty] | Haydn |  |  | y | Updated comment
389 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 1.5 | 2 | 1 |  |  |  | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. |  |  | Vol 1 |  |  |  | Under Review | Need recommended maximum attachment size 28/2/2017 | Sector Discussion | Sector Discussion | Need recommended maximum attachment size 28/2/2017 | 1.5 Deliverables |  |  | 1 | [6 empty] | 1 | [6 empty] | each organisation to determine practical limits | done | done | done | done | [5 empty] | More information required for a decision
390 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.1.1 | 7 | 1 |  |  |  | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. |  |  | Vol 1 |  |  |  | Noted | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. 28/2/2017 | Noted: no action required | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. 28/2/2017 | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | no action | [5 empty] | No action
391 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. |  |  | Vol 1 |  |  |  | Noted | picked up previously 28/2/2017 | Included | Included | picked up previously 28/2/2017 | 2.1.2 Projections and Datums | 1 | [16 empty] | done | done | done | done | [5 empty] | Change made document updated
392 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.4 | 65 | 7 |  |  |  | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. |  |  | Vol 1 |  |  |  | Noted | agreed, but per pipe section, there is a from-node and a to-node, one of each. 28/2/2017 | Noted: no action required | Noted: no action required | agreed, but per pipe section, there is a from-node and a to-node, one of each. 28/2/2017 | 2.4.4 Node |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
393 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.5 | 67 | 5 |  |  |  | We split pipes when there is a valve or hydrant on them. While other councils may not |  |  | Vol 1 |  |  |  | Noted | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. 28/2/2017 | Noted: no action required | Noted: no action required | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. 28/2/2017 | 2.4.5 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
394 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.5 | 67 | 6 |  |  |  | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. |  |  | Vol 1 |  |  |  | Under Review | need examples 28/2/2017 | Sector Discussion | Sector Discussion | need examples 28/2/2017 | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
395 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.6 | 74 | Pipe Attribute & Validation File Format Instructions Diameter |  |  |  | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. |  |  | Vol 1 |  |  |  | George/Haydn | this was agreed to by the TWG, what is your suggestion? 28/2/2017 | Included | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | 1 | [8 empty] | 1 |  |  |  | ok | [12 empty] | No action
396 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.5.2 | 95 | Pump Attribute & Validation File Format Instructions |  |  |  | A lot of the attributes seem to be duplicated |  |  | Vol 1 |  |  |  | Noted | attributes are all different 28/2/2017 | Noted: no action required | Noted: no action required | attributes are all different 28/2/2017 | 2.5.2 Pump |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
397 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.7.1 | 132 | Figure 44 |  |  |  | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | agreed, diagram will be corrected 28/2/2017 | Included | Included | agreed, diagram will be corrected 28/2/2017 | 2.7.1 Instruments | 1 | [7 empty] | 1 | [7 empty] | change needed DOC need to find or create new diagrams | [9 empty] | No action
398 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | QA | Noted | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Updated | General | 1 | [7 empty] | 1 | [17 empty] | Changes made documents updated |  | ?
399 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | QA | Updated | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Updated | General | 1 | [7 empty] | 1 | [17 empty] | Changes made documents updated |  | ?
400 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Implementation | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
401 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Metadata terminology | This is a metadata standard not asset management standards. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | This is a metadata standard not asset management standards. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
402 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Implementation | Updated | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Updated | General | 1 | [7 empty] | 1 | [6 empty] | Use of Spec… change needed in docs |  | done | done | done | done | [5 empty] | Changes made documents updated |  | ?
403 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | QA | These are differentr in some cases / in others they are not, not the same definitions across sectors | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | These are differentr in some cases / in others they are not, not the same definitions across sectors | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
404 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | NA | This is a volume 3 exercise | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | This is a volume 3 exercise | 1.5 Deliverables |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
405 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | No action |  |  |  |  | 1 | 1
406 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | NA | References to be removed. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | References to be removed. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
407 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Coverage | No action required. These standards do not cover treatment plants. Requirements for covering treatments plants will be developed later. Reference can be made to buildings, do not see if this will add value though | Vol 1 - Vol 2 |  | Treatment is not included |  |  |  | Noted: no action required | Noted: no action required | Treatment is not included | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
408 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Service Performance | Out of scope. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Out of scope. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
409 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Land – no parameters are set for the recoding of land information. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Not part of this scope. 26/3/2017 | Excluded | Excluded | Out of scope. | No Specific Reference |  | 1 | [7 empty] | 1 |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
410 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Vulnerability | Action required. Vulnerability is developed as a separate schema. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | Vulnerability, Criticality, Risk and Resilience | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | No action |  | ? | y | Updated comment | 1 | 1
411 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Criticality | Other critical infrastructure is already being considered in a later edition. No action required. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
412 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Implementation | Covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Detailed in business case only | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
413 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Mandatory Fields | Standards covers mandatory and optional field. The benefits to costs covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Standards covers mandatory and optional field. The benefits to costs covered in business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
414 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Mandatory Fields | Covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Covered in business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
415 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Implementation | Covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Covered in business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
416 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Implementation | Covered in business case. Pilot testing currently being undertaken. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
417 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | Noted | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
418 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
419 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
420 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | George |  | Noted | Accuracies Incorporated in updated version. | Included | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed - add precision tables | do we add for buildings? Speak with haydn | done | done | done | do we add for buildings? Speak with haydn | [5 empty] | No action |  | N/A | y | I have not updated in Vol 2, it should be the same 'paragraph' content as Vol 1, ead your comment as though you had
421 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | George |  | Under Review | Clarify description of requirement. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
422 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Spatial | Action on volume 1. In Volume 2, the use can select coordinate system. Specifying a singular system is not required | Vol 1 - Vol 2 |  | George |  | Noted | Please refer to updated documents sections 2.1.3 & 2.1.4. 26/3/2017 | Noted: no action required | Noted: no action required | Included in the draft Standards | General |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | No action
424 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Spatial | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | Noted: no action required | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | No action
425 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Spatial | Action on volume 1. In Volume 2, the use can select coordinate system. Specifying a singular system is not required | Vol 1 - Vol 2 |  | George |  | Noted | Included in updated documents. 26/3/2017 | Included | Included | Included in the draft Standards | 2.1.2 Projections and Datums | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed |  | done | done | done | done | [5 empty] | Changes made documents updated |  | N/A
426 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Coverage | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. Action: make clear in the standard. | Vol 1 - Vol 2 |  | George |  | Noted | 26/3/2017 | Included | Noted: no action required | Included in the draft Standards Asset categories included as guidance for each organisation | General | 1 | [7 empty] | 1 |  |  |  |  | change your comment to "Asset categories included as guidance for each organisation" | Added | [11 empty] | No action |  | N/A
427 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Coverage | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. Action: make clear in the standard. | Vol 1 - Vol 2 |  | To discuss - AMIS constraints are not within the considerations of these standards |  |  |  | Noted: no action required | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
428 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
429 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Maintenance, Repairs and Maintenance | Action: Include attribute for "Maintenance Responsibility" | Vol 1 - Vol 2 |  | Included in the draft standards |  |  |  | Included | Included | Included in the draft standards | General | 1 | [7 empty] | 1 | [6 empty] | late pickup can be dealt by the asset owner after asset data is provided | [10 empty] | No action |  | ?
430 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Implementation | Agreed. Action on volume 1. | Vol 1 - Vol 2 |  | To discuss - optioneering system structure is not within the structure of these standards |  |  |  | Noted: no action required | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
431 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | NA | Action ono volume 1 and data scientist. In the case of establishing condition of pipe, it would matter how big an asset is etc. So you know what length of pipe the condition relates to . | Vol 1 - Vol 2 |  | To discuss - optioneering system structure is not within the structure of these standards |  |  |  | Noted: no action required | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
432 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Maintenance, Repairs and Maintenance | Action: Include attribute in maintenance | Vol 1 - Vol 2 |  | George |  | Noted | The ownership is at Council level. 26/3/2017 | Included | Noted: no action required | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | your suggested response does not answer the question is it to define council departments or that its council's vs someone elses. Please use the response in column T |  | late pickup can be dealt by the asset owner after asset data is provided | [10 empty] | No action |  | ?
433 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | NA | Organisations will record the level of granularity as required | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
434 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Sector Discussion | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
435 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | NA | Organisations will record the level of granularity as required | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
436 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | NA | Organisations will record the level of granularity as required | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
437 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | NA | Nodes are required for analytical differentiation purposes | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
438 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Clarify description of requirement. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Nodes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
439 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Implementation | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
440 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | George |  | Noted | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | Noted: no action required | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
441 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Financial Performance | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
442 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Mandatory Fields | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
443 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | Noted: no action required | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
444 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
445 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Data collection is out of scope from these standards |  |  |  | Noted: no action required | Noted: no action required | Data collection is out of scope from these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
446 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | General | Included in standard. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference | 1 | [7 empty] | 1 | [19 empty] | ? |  |  | 1 | 1
447 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | This requirement will generally only apply to Potable Water. | Noted: no action required | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
448 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Financial Performance | Action: Granularity to be decided by organisation. To be clarified further in Volume 1 or Volume 2. | Vol 1 - Vol 2 |  | Junctions / end points are not assets. |  |  |  | Excluded | Excluded | Junctions / end points are not assets. | General |  | 1 | [6 empty] | 1 | [8 empty] | no action | no action | no action | n/a | [5 empty] | No action
449 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Financial Performance | Action: Granularity to be decided by organisation. To be clarified further in Volume 1 or Volume 2. | Vol 1 - Vol 2 |  | Junctions / end points are not assets. |  |  |  |  | Excluded | Junctions / end points are not assets. | No Specific Reference |  | 1 | [6 empty] | 1 | [8 empty] | no action | no action | no action | n/a | [5 empty] | No action |  |  |  |  | 1 | 1
450 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Please provide details of which value is preferred. To be reviewed by the TWG for consideration. 26/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
451 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | The lowest granularity for a pipe asset is piece of asset pipe and recorded as such with a specific pipe asset AssetID. Canenated pipe pieces make up a Mains Pipe. And, allow for 'pieces of pipe to be replaced, again at an AssetID. |  |  |  | Noted: no action required | Noted: no action required | The Idv proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
452 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft standards Cod lists have been supplied | General | 1 | [7 empty] | 1 | [6 empty] | add codelsits |  | done | done | done | done | [5 empty] | Change made document updated |  | N/A
453 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Implementation | Action on volume 1 and business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action on volume 1 and business case. | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | Nodes do not indicate meters |  |  |  | n/a | [5 empty] | No action
454 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Implementation | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
455 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Implementation | Statement noted. Action on volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Data transfer is not in scope. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
456 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Granularity | No action required. Metadata standard is more than meeting minimum national reporting purposes. Granularity question. | Vol 1 - Vol 2 |  | The reporting granularity so for an asset manager managing any single or number of assets |  |  |  | Noted: no action required | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
457 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | General | 1. Completed 2. Further information required from respondent. 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | 1. Completed 2. Further information required from respondent. 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
458 | Kerry Thompson | KTA | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | General | Statement noted. Consideration for Volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Consideration for Volume 1. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
459 | Kerry Thompson | KTA | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | NA | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. No action required. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
460 | Kerry Thompson | KTA | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | NA | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. No action required. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
461 | Myles Lind | Queenstown Lakes District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | NA | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. No action required. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
462 | Myles Lind | Queenstown Lakes District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | NA | Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
463 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | NA | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
464 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Volume Interaction | Statement noted. To be considered. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. |  |  |  | Noted: no action required | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
465 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Volume Interaction | The introduction of cohorts and schemas should help clarify this situation. Action Required for volume 1 to identify the three schema's. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. Action to look at this. | Vol 1 - Vol 2 |  | These inconsistencies have been actioned in the draft standards |  |  |  | Included | Included | These inconsistencies have been actioned in the draft standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | ?
466 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Normalisation | Data tables being looked at by data scientist. | Vol 1 - Vol 2 |  | These inconsistencies have been actioned in the draft standards |  |  |  | Included | Included | These inconsistencies have been actioned in the draft standards | General | 1 | [7 empty] | 1 | [6 empty] | Note: while the structure is normalised in the standard it is opfetn de-normalised to accommodate organisations needs. |  | no action required | no action required | no action required | no action required | work required | work required | work required | work required |  | No action |  | N/A
467 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | NA | Not in scope | Vol 1 - Vol 2 |  | To discuss |  |  |  | Sector Discussion | Sector Discussion | To discuss | No Specific Reference |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision |  | N/A |  |  | 1 | 1
468 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action for volume 1. | 1.7 Heirarchy |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
469 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Coverage | Out of scope. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Sector Discussion | Included | Tables to be discussed in Final Version Vol 1 | No Specific Reference | 1 | [7 empty] | 1 | [6 empty] | change needed | change category and response to sector discussion | n/a | further information required from workshops not to include treatment plants tunnels added | n/a | n/a |  |  |  |  | document request | More information required for a decision Tunnels have been included |  | N/A | y | no change
470 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | Noted: no action required | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
471 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | NA | Data hierarchy to be look at by data scientists. Think this comment applies mostly to Volume 1, but data hierarchy needs to be considered for Vol 2 also | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards |  |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | 1 | [7 empty] | 1 | [6 empty] | review against notes | haydn please note these has been no work to harmonise Vol 2's with Vol 1's | no action required | no action required | no action required | no action required |  |  |  |  | follow up with Nick Walmsley for further information To note that organisations may have different hierarchies - the purpose of this document is to standardise the requirements for the data service providers and provide consistency in data delivery to the asset owners | No action |  | ? | y | Yes there has….. They are harmonised by the primary key fields of each of the decision elements and the tables 'nested' within them No need to standardise across Vol 1 & 2
472 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Terminology | Action: check definitions are consistent across both volumes 1 and 2. | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards |  |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action | [7 empty] | 1 | [7 empty] | haydn please note these has been no work to harmonise Vol 2's with Vol 1's | no action required | no action required | no action required | no action required | [5 empty] | No action |  | ? | y | Yes there has….. They are harmonised by the primary key fields of each of the decision elements and the tables 'nested' within them No need to standardise across Vol 1 & 2
473 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Data | Action required: data scientists to review Volume 1. Heierarchy question | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Tables will be referenced in Final Versions | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action |  | N/A
474 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Spatial | Action on volume 1 | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action |  | N/A
475 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Implementation | Statement Noted. Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement Noted. Business case. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
476 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Implementation | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
477 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Implementation | Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business case. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
478 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Implementation | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
479 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Mandatory Fields | Action required: Give further thought to what fields are mandatory with consideration to data maturity and sophistication. Implementation issues are covered under the Business Case | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Implenmentation is not within scope | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
480 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Implementation | Business Case | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
481 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Implementation | Business Case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
482 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Implementation | These comments are identical to Oliver Mander See comments Haydn | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
483 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Implementation | These comments are identical to Oliver Mander See comments Haydn | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
484 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [7 empty] | add codelists need specific instances where this has occurred to check against master | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action |  | N/A
485 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards |  |  |  | Included | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | 1 | [7 empty] | 1 | [17 empty] | No action
486 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The current drafts need additional work at the hierarchy level and better definition / guidance. | NA | Hierarchy is Volume 1. Definition may apply to Volume 2. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Sector Discussion | Included | Asset Classifications have been defined in the Standards | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest change status to Sector discussion and change response to More information is required to inform a way forward | Changed | [11 empty] | More information required for a decision
487 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Implementation | Action: to be clarified in "In Summary" chapter. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | This is about conext for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | 1 | [7 empty] | 1 |  |  |  |  | ok |  |  | general roles and responsibilities are part of creating a standardised way of developing best practice | [9 empty] | Further discussion with Sector |  | N/A |  |  | 1 | 1
488 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | NA | Volume 1 only. | Vol 1 - Vol 2 |  | George |  | Noted | 26/3/2017 | Noted: no action required | Noted: no action required | Included in the draft Standards | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
489 | Nick Walmsley | Water NZ | Potable water | Vol 1 | Executive Summary | iv | 3 |  |  |  | savvy - edit out slang words like this |  |  | Vol 1 |  |  |  | Noted | removed in current version 28/2/2017 | Included | Included | removed in current version 28/2/2017 | Executive Summary | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | n/a | n/a | n/a | [5 empty] | Change made document updated
490 | Nick Walmsley | Water NZ | Potable water | Vol 1 | Executive Summary | v | In Summary - 2 |  |  |  | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. 28/2/2017 | Included | Included | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. 28/2/2017 | In Summary | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
491 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.1 | 1 | 2 |  |  |  | Consultants - Replace by organisations? |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | Term consultants now included in glossary. 28/2/2017 | Included | Included | Term consultants now included in glossary. 28/2/2017 | 1.1 Register | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
492 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.4 | 1 | 1 |  |  |  | Again, misuse of term 'consultants. edit through the document to correct this. |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | Term consultants now included in glossary. 28/2/2017 | Included | Included | Term consultants now included in glossary. 28/2/2017 | 1.4 Disclaimer | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
493 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.5 | 3 | Facsimile |  |  |  | Is this still used? |  |  | Vol 1 |  |  |  | Noted | optional supply 28/2/2017 | Noted: no action required | Noted: no action required | optional supply 28/2/2017 | 1.5 Deliverables |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
494 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 1 | 1 |  |  |  | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? |  |  | Vol 1 |  |  |  | Noted | both schemata and schemas are both acceptible words for the plural of schema. 28/2/2017 | Noted: no action required | Noted: no action required | both schemata and schemas are both acceptible words for the plural of schema. 28/2/2017 | 1.6 Global Schemas |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
495 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 4 | Volume 3 - 1 |  |  |  | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? |  |  | Vol 1 | This is not within the remit of the standards |  |  | Haydn | need a direct response 28/2/2017 | Noted: no action required | Noted: no action required | This is not within the remit of the standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
496 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 4 | Volume 4 - 1 |  |  |  | how can the analytics standardise the data that has already been standardised? |  |  | Vol 1 | The data definitions have been standardised, the actual data can be standardised against that. |  |  | Haydn | need a direct response 28/2/2017 | Included | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | 1 | [7 empty] | 1 | [17 empty] | No action
497 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 5 | Volume 5 - 1 |  |  |  | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? |  |  | Vol 1 | No, this is not an asset Management Standard - it is an asset data standard |  |  | Haydn | need a direct response 28/2/2017 | Noted: no action required | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
498 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.8 | 1 | 1 |  |  |  | i.e. not fixed and topics can be added? |  |  | Vol 1 |  |  |  | Noted | Agree, asset classes can be added as agreed to 28/2/2017 | Included | Included | Agree, asset classes can be added as agreed to 28/2/2017 | 1.8 Theme Structure | 1 | [7 empty] | 1 | [17 empty] | No action
499 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.9 | 4 | Potable water Asset class Table |  |  |  | what does this mean? No? but no Y for yes? |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | N changed to N/A 28/2/2017 | Included | Included | N changed to N/A 28/2/2017 | 1.9 Data Principles | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
500 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.1 | 6 | 2 |  |  |  | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? |  |  | Vol 1 |  |  |  | Noted | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time 28/2/2017 | Noted: no action required | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time 28/2/2017 | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
501 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.1 | 6 | 2 |  |  |  | precisely? 'well' is a subjective term |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed 7/3/2017 | Included | Included | changed | 2.1.1 Accuracy Requirements for Locating Assets | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
502 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.1 | 6 | 5 |  |  |  | no 's' |  |  | Vol 1 |  |  |  | Under Review | cannot identify 7/3/2017 | Sector Discussion | Sector Discussion | cannot identify | 2.1.1 Accuracy Requirements for Locating Assets |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
503 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Format Instructions Hlth_Sfty |  |  |  | change 'issues' to 'risks' throughout document |  |  | Vol 1 |  |  |  | Noted | not a risk but an issue 7/3/2017 | Noted: no action required | Noted: no action required | not a risk but an issue | 2.1.10 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
504 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.3.4 | 40 | 1 |  |  |  | Well - change to 'bore' |  |  | Vol 1 |  |  |  | Noted | term agreed to by TWG 7/3/2017 | Noted: no action required | Noted: no action required | term agreed to by TWG | 2.3.4 Well |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
505 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.4.3 | 60 | 4 |  |  |  | does this create a 'node'/ if not then it is a problem for modelling. |  |  | Vol 1 |  |  |  | George/Haydn | Can be post processed to be a node by the agency 7/3/2017 | Included | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
506 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.4.5 | 67 | 13 |  |  |  | how is a locator or IP cable taped to the pipe represented? |  |  | Vol 1 |  |  |  | Under Review | Need more information and example 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and example | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
507 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.4.6 | 74 | Pipe Attribute & Validation File Format Instructions Diameter |  |  |  | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? |  |  | Vol 1 |  |  |  | George/Haydn | this was agreed to by the TWG, what is your suggestion? Needs to be appropriate to pipe type and ability of person capturing the detail to supply the data 7/3/2017 | Included | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
508 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.5.1 | 93 | Mechanical Equipment Attribute & Validation File Format Instructions |  |  |  | Is a backflow preventer a mechanical equipment asset or a valve/ |  |  | Vol 1 |  |  |  | Under Review | Need more information and recommendation 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
509 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.8.2 | 140 | 1 |  |  |  | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. |  |  | Vol 1 |  |  |  | Noted | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time 7/3/2017 | Noted: no action required | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
510 | Nick Walmsley | Water NZ | Potable water | Vol 1 | Glossary | 145 | 1 |  |  |  | this could be much larger with additional definitions e.g.. 'trunk main' |  |  | Vol 1 |  |  |  | Noted | wil expand over time 7/3/2017 | Noted: no action required | Noted: no action required | wil expand over time | Glossary |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
511 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Volume Interaction | Statement noted. To be considered. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | Yes. Key objective to make them as useable as possible by all stakeholders: what is the solution then? |  |  | Included | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
512 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Normalisation | This will be looked at by the Data scientists? | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards | Common data: The antithesis applies where designers are designing a 'stormwater' solution. Risk advocated with a 'de-normalised' structure: Agreed: note work being completed by Metaconnect. |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
513 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Implementation | See comments Haydn | Vol 1 - Vol 2 |  | This is not within the scope of these standards | Specific roles: not specified. Different places: agreed, more about how… not so much if. "specific" regulatory implementation: noted, probably need to think about what if scenarios, i.e.. What if not adopt? Application by all users: noted and agreed. Flexibility within the standard: agreed with all this. |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
514 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | General | Further discussion with Wellington Water. Business Case. Details discussed in further feedback from Wellington Water. | Vol 1 - Vol 2 |  | Volume 2 is complete in these draft standards | Good for discussions - guideline first, but also need 'analytical consistency'… |  |  | Noted: no action required | Noted: no action required | Volume 2 is now complete | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
515 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | Data specifications in volume 1: it does - as co-ordinates in x-y & height (z). Not the role of the document to determine how spatial data is represented: agree (but should point to international standard OGC) |  |  | Noted: no action required | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
516 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | NA | a. Action on volume 1. Possible flow on to volume 2. b. These structures are outside of scope of the structure as agreed in technical workgroup. C. action on volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards | a. noted. B. noted will include. C. same hierarchy: note, there are some ISO (IFC - Industry Federation Class) developments in the UK which deal with this too. C. preamble at odds with structure into 3 volumes - can we understand where/how - this is not the intent. |  |  | Sector Discussion | Included | Included in the draft Standards | 1.7 Heirarchy | 1 | [7 empty] | 1 | [16 empty] | MAY NEED FURTEHR DISCUSSION WITH Oliver Same hierarchy has been ap[plied and only assets that are in the network are included are these additional assets in tretament plants ? | More information required for a decision |  | n/A
517 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Other standards | Statement noted. The standards as they are reflect the feedback from the technical working groups (industry feedback and experts advisors) | Vol 1 - Vol 2 |  | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | Yes, building code, ISO Metadata, OGG (spatial). |  |  | Included | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
518 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Data | Action required: data scientists to review Volume 1. Heierarchy question | Vol 1 - Vol 2 |  | Haydn & George | Haydn & George |  |  | Included | Included | Tables will be referenced in Final Versions | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action |  | N/A
519 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Implementation | Raises some important points. Implementation question to be considered. Outside the scope of this current standard. | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | Asset Management decisions and practices limitations: it is to a point - but in an analytical sense - this is a data standard for algorithms and evidence for evidence base decision-making. If there are more analytical outputs which require more attribute/data the lets discuss. a. yes - analytics in many divers instances (evidence) b. not so - for discussion - this is about analytical engines - then decisions. c. few options - but less discuss (e.g.. data completeness, or stochasticity values etc...) Outcome based standard: all outcomes are underpinned by measureable outputs first... at least complimenting for evidence. |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
520 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Implementation | See comments Haydn | Vol 1 - Vol 2 |  | This is not within the scope of these standards | Only to set appropriate expectations: not so sure - but certainly an implementation questions - to discuss. Data loss and integrity issues: not necessarily - FME tools etc. |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
521 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. |  |  | Vol 1 |  |  |  | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | Noted: no action required | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
522 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. |  |  | Vol 1 | [5 empty] | Noted: no action required | Noted: no action required | Service level performance is included in Volume 2 | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
523 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. |  |  | Vol 1 |  |  |  | Under Review | Have the code lists been distributed? Can be assigned as sector discussion This detail was identified at the previous workshops and determined to be appropriate . 26/3/2017 | Sector Discussion | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | codelists added | codelists added | codelists added | n/a | [5 empty] | More information required for a decision
524 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. |  |  | Vol 1 |  |  |  | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | Noted: no action required | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
525 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. |  |  | Vol 1 |  |  |  | Noted | Please refer to Project and common data | Noted: no action required | Noted: no action required | Please refer to Project and common data | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
526 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. |  |  | Vol 1 |  |  |  | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | Noted: no action required | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
527 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. |  |  | Vol 1 |  |  |  | Noted | Please refer to Project and common data | Noted: no action required | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
528 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). |  |  | Vol 1 |  |  |  | Under Review | Please provide details for the specific tables and the relevant attributes to be considered Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
529 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. |  |  | Vol 1 |  |  |  | Under Review | Please provide details for the specific tables and the relevant attributes to be considered Workshops will be held in May for further contribution | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pump Station |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
530 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. |  |  | Vol 1 |  |  |  | Noted | This will be catered for through recording the "Source" 14/03/2017 | Noted: no action required | Noted: no action required | This will be catered for through recording the "Source" | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
531 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. |  |  | Vol 1 |  |  |  | George/Haydn | Say more about this. Which aspect of data accuracy the completeness of the data or the spatial accuracy of the data? 14/03/2017 | Included | Included | This is a derivation for Volume 3, including precision of survey data | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
532 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. |  |  | Vol 1 | Now normalised and standardsed with Metaconnect |  |  | Haydn | which document is this referring to? 14/03/2017 | Included | Included | Now normalised and standardsed with Metaconnect | General | No action | [7 empty] | 1 | [17 empty] | No action
533 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. |  |  | Vol 1 |  |  |  | George/Haydn | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | Excluded | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General |  | 1 | [6 empty] | 1 |  |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
534 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks |  |  | Vol 1 |  |  |  | George/Haydn | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | Sector Discussion | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
535 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
536 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). |  |  | Vol 1 |  |  |  | Noted | Already incorproated into the table 16/03/2017 | Included | Included | Already incorproated into the table | 2.3.1 Containment Structure | 1 | [7 empty] | 1 | [17 empty] | No action
537 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. |  |  | Vol 1 |  |  |  | Noted | To be read in conjunction with the codelist specified Retaining Structure Type 16/03/2017 | Noted: no action required | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
538 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
539 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. |  |  | Vol 1 |  |  |  | Noted | Please refer to the field "Purpose" and the code list Retaining Structure Purpose 16/03/2017 | Noted: no action required | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
540 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type |  |  | Vol 1 |  |  |  | under review | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
541 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! |  |  | Vol 1 |  |  |  | George/Haydn | The attributes in this asset class were reviewed and agreed to at the previous workshops. Please identify what allowance is required - as in what additional data and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall |  |  | 1 | [5 empty] | 1 |  |  |  |  | change response to More information is required to inform a way forward | Changed | [11 empty] | More information required for a decision
542 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? |  |  | Vol 1 |  |  |  | George/Haydn | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | Included | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
543 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. |  |  | Vol 1 |  |  |  | George/Haydn | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | Sector Discussion | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
544 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
545 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard 16/03/2017 | Included | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | 1 | [7 empty] | 1 | [6 empty] | change needed doc | example provided for review | done | done | done | n/a | n/a | n/a | n/a |  |  | Change made document updated
546 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. |  |  | Vol 1 |  |  |  | under review | Please provide your definition for "observation and/or survey data" 16/03/2017 | Sector Discussion | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
547 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. |  |  | Vol 1 | Vol 1 & 2 are inherantly linked by asset ID and location |  |  | Haydn | 2017-03-16 | Included | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | 1 | [7 empty] | 1 | [17 empty] | No action
548 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? |  |  | Vol 1 |  |  |  | under review | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
549 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. |  |  | Vol 1 |  |  |  | George/Haydn | Don’t have an issue one way or another - this is the only mention of it so far as I can recall. | Sector Discussion | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 |  |  |  |  | change response to To be reviewed by the TWG for consideration of inclusion | Added | make mention of change request | [9 empty] | request documented | More information required for a decision
550 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. |  |  | Vol 1 |  |  |  | under review | Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
551 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | More information is needed to inform a way forward. Also refer to code lists | Sector Discussion | Included | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | 1 | [7 empty] | 1 | [6 empty] | change response and status | refer to code list | refer to code list | refer to code list | refer to codelist | [5 empty] | DOCUMENT AS A REQUEST request data prior to next workshops | More information required for a decision
552 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). |  |  | Vol 1 |  |  |  | Noted | Please refer to comment above 16/03/2017 | Noted: no action required | Noted: no action required | Please refer to comment above | 2.4.2 Channels |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
553 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. |  |  | Vol 1 | Put hydraulic profiles as code list |  |  | Haydn | Not sure what is being requested here. If they are talking about the detail that is in the cross swections then this can be accessed from the design plans once verified that what has been designed has been built 16/03/2017 | Sector Discussion | Included | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | 1 | [7 empty] | 1 | [7 empty] | Haydn pleaseexplain how this will be included | [9 empty] | More information required for a decision |  |  | y | create code list of profile shape
554 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. |  |  | Vol 1 | Vol 1 & 2 are inherantly linked by asset ID and location |  |  | Haydn | 2017-03-16 | Included | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | 1 | [7 empty] | 1 | [17 empty] | No action
555 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
556 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. |  |  | Vol 1 | Either - the analytic will define that based on analytic computatoinal assumption |  |  | Haydn | 2017-03-16 | Included | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | Haydn
557 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard 16/03/2017 | Included | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | change needed doc | changed to Date the asset was constructed/built/installed/relined/renewed | done | done | done | done | [5 empty] | Change made document updated
558 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. |  |  | Vol 1 |  |  |  | under review | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. 16/03/2017 | Sector Discussion | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
559 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. |  |  | Vol 1 |  |  |  | Noted | The invert level is to be recorded against a pipe 16/03/2017 | Included | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | No action
560 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? |  |  | Vol 1 |  |  |  | Noted | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | Included | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | No action
561 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? |  |  | Vol 1 | yes in Volume 2 |  |  | Haydn | 2017-03-16 | Included | Included | yes in Volume 2 | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | No action
562 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard. | Included | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | changed mind review wording to reflect that there is always something at the end of a pipe, maybe an end point, a blank end an access point | h. IL's are always placed on the pipe irrespective of its end point. Regards Pipe End - Noted. It is proposed that there will always be some kind of feature depicting where the pipe ends to assist with creation of a topological structure once the data is provided each asset owner will then be able to address it as needed. e.g. Maybe a fitting (blank end), maybe a structure, maybe a non physical feature (pipe end) | done | done | done | n/a | [5 empty] | Change made document updated
563 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. |  |  | Vol 1 |  |  |  | under review | Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
564 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). |  |  | Vol 1 | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's |  |  | Haydn | 2017-03-16 | Noted: no action required | Noted: no action required | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
565 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
566 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. |  |  | Vol 1 |  |  |  | Noted | Attribute fields are included in the Pupm asset class for motors. Please review and provide details of additional | Included | Included | Attribute fields are included in the Pupm asset class for motors. Please review and provide details of additional | 2.5.2 Pump | 1 | [7 empty] | 1 | [17 empty] | No action
567 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. |  |  | Vol 1 |  |  |  | Noted | An attribute field currently exists for this "Pump Usage" 16/03/2017 | Included | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | 1 | [7 empty] | 1 | [17 empty] | No action
568 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Will include for ratification by the reviewers. 16/03/2017 | Sector Discussion | Included | Will include for ratification by the reviewers. | 2.5.2 Pump | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | [9 empty] | request documented | New attribute proposed | Trigger level
569 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. |  |  | Vol 1 |  |  |  | under review | Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
570 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. |  |  | Vol 1 |  |  |  | Noted | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG 16/03/2017 | Included | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | 1 | [7 empty] | 1 | [17 empty] | No action
571 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). |  |  | Vol 1 |  |  |  | Noted | Please review the Project and Common attributes 16/03/2017 | Noted: no action required | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
572 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
573 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard 16/03/2017 | Included | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
574 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date |  |  | Vol 1 |  |  |  | Noted | 2017-03-07 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [13 empty] | No action
575 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. |  |  | Vol 1 |  |  |  | George/Haydn | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities 7/3/2017 | Sector Discussion | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you review your response as it onlyt partly answers the question | updated comment not certain how this would be done as it is specific to each asset | [11 empty] | New Code List proposed | Health & Safety Type
576 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? |  |  | Vol 1 |  |  |  | George/Haydn | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | Sector Discussion | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
577 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) |  |  | Vol 1 |  |  |  | Noted | 10 character fields have been adopted to allow for expansion 7/3/2017 | Noted: no action required | Noted: no action required | 10 character fields have been adopted to allow for expansion | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
578 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. |  |  | Vol 1 |  |  |  | Under Review | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate. 7/3/2017 | Sector Discussion | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
579 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. |  |  | Vol 1 |  |  |  | Under Review | Need more information and example 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and example | General |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
580 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). |  |  | Vol 1 |  |  |  | Under Review | Need more information and example 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and example | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
581 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | can be included through health and safety column and codelist | [7 empty] | request documented | More information required for a decision
582 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. |  |  | Vol 1 |  |  |  | Noted | Already defined as a polygon feature 7/3/2017 | Included | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | 1 | [9 empty] | 1 | [15 empty] | No action
583 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | new ATTRIBUTE FIELD AND ASSOCITED code list created | [7 empty] | request documented | New Code List proposed | Burial Status Above ground Below ground Partially buried
584 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. |  |  | Vol 1 |  |  |  | Noted | Terms agreed to by TWG. WWL can map from this to their own terminology. 7/3/2017 | Noted: no action required | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
585 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. |  |  | Vol 1 |  |  |  | Noted | Length, height and width are fields and are conditional on asset shape 7/3/2017 | Noted: no action required | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
586 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
587 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
588 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
589 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
590 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
591 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. |  |  | Vol 1 |  |  |  | Noted | Chamber Type is already included. Additional Types can be included. 7/3/2017 | Included | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | 1 | [9 empty] | 1 | [15 empty] | No action
592 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. |  |  | Vol 1 |  |  |  | George/Haydn | Not an 'As Constructed' attribute | Excluded | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment |  | 1 | [6 empty] | 1 |  |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
593 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure - WELL a. Include Ground Water Level |  |  | Vol 1 |  |  |  | Noted | Ground Water Level varies and may misrepresent the situation if recorded 7/3/2017 | Noted: no action required | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
594 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure - WELL b. Resource Consent number |  |  | Vol 1 |  |  |  | Noted | Included in Project Attributes 7/3/2017 | Included | Included | Included in Project Attributes | 2.3.4 Well | 1 | [9 empty] | 1 | [15 empty] | No action
595 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading |  |  | Vol 1 |  |  |  | George/Haydn | Will this be known at time of construction? 7/3/2017 | Sector Discussion | Included | Code lists for NZDWS could be included - for discussion | 2.3.4 Well |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you review your response as it onlyt partly answers the question | [12 empty] | More information required for a decision
596 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
597 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New attribute proposed | Manufacturer
598 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. |  |  | Vol 1 |  |  |  | Noted | Tee is inlcuded in the codelist for fitting type 7/3/2017 | Included | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | 1 | [9 empty] | 1 | [15 empty] | No action
599 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. |  |  | Vol 1 |  |  |  | Noted | Agreed | Included | Included | Agreed | 2.4.3 Fitting | 1 | [9 empty] | 1 | [15 empty] | Change made document updated
600 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. Is this common across the industry? | Sector Discussion | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | suggest no - only have the attributes against the fitting create a lsiting of node numberrs and the type of asset it is associated with | [9 empty] | More information required for a decision |  |  | y | A node is not an asset updated comment
601 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. What needs to be known about them? | Sector Discussion | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New Asset Class proposed Detail of data requirements needed | Support Structures
602 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material |  |  | Vol 1 |  |  |  | George/Haydn | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. Attribute will be added to accommodate the 'sub-components' | Included | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. Attribute will be added to accommodate the 'sub-components' | 2.4.5 Pipe | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | Pipe Coating Material Pipe Lining Material
603 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type |  |  | Vol 1 |  |  |  | Noted | Joint Method already included. Joint Type not required as per TWG. 7/3/2017 | Included | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
604 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. |  |  | Vol 1 |  |  |  | Noted | Already catered for. 7/3/2017 | Included | Included | Already catered for | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
605 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. |  |  | Vol 1 |  |  |  | George/Haydn | Pressure pipe typically does not include IL but may be handy. 7/3/2017 | Included | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you review your response as it onlyt partly answers the question as IILalready included. I also misread the comment - this is about where the IL is measured on the pipe. | [12 empty] | No action
606 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level |  |  | Vol 1 |  |  |  | Noted | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted. 7/3/2017 | Noted: no action required | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
607 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation |  |  | Vol 1 |  |  |  | Noted | From and To node used to determine flow directions.7/3/2017 | Included | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
608 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | change in all documents 7/3/2017 | Included | Included | change in all documents | 2.4.5 Pipe | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | n/a | [5 empty] | Changes made documents updated
609 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | removed nom_Bore 7/3/2017 | Included | Included | removed nom_Bore | 2.4.5 Pipe | 1 | [9 empty] | 1 |  |  |  |  | check done | make mention of change request | done | done | done | done |  |  |  |  | make mention of change request | Removal of attribute proposed Have marked for removal in documents
610 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
611 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. What kind of descriptors are applicable? | Sector Discussion | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
612 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? |  |  | Vol 1 |  |  |  | Under Review | Need examples and diagrams. 7/3/2017 | Sector Discussion | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
613 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
614 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). |  |  | Vol 1 |  |  |  | Under Review | Need examples and diagrams. 7/3/2017 | Sector Discussion | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
615 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? |  |  | Vol 1 |  |  |  | Under Review | Are vents used with potable water network? 7/3/2017 | Sector Discussion | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
616 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
617 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New attribute proposed | Portable generator (Y/N)
618 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” |  |  | Vol 1 | Propose to add another attribute for the calculation |  |  | Haydn | parts of this are already included, note that the standard may vary over time. Pump Station refererence not include in the version GISSA is using, what version was sent out for review? 7/3/2017 | Included | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | 1 | [9 empty] | 1 |  |  |  | New attribute to be included in standard | suggest add another field and keep original field clean | make mention of change request | review | [7 empty] | document request | New attribute proposed | Calculation
619 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. Is WWL requesting the inclusion? | Sector Discussion | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
620 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. |  |  | Vol 1 |  |  |  | Under Review | Consider making Op_Mode a Codelist | Sector Discussion | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New Code List proposed | Valve Control & Automatic Control
621 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. |  |  | Vol 1 |  |  |  | Under Review | see 00620 7/3/2017 | Sector Discussion | Sector Discussion | see 00620 | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New Code List proposed | Valve Power
622 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. |  |  | Vol 1 |  |  |  | Noted | Can be provided as part of the operational instructions at hand over 3/7/2017 | Noted: no action required | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
623 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. |  |  | Vol 1 |  |  |  | Under Review | Refer to Valve Type codelist to see if this can be covered here. | Sector Discussion | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
624 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. |  |  | Vol 1 |  |  |  | George/Haydn | Covered 2.1.7 and 2.1.8. 7/3/2017 | Included | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
625 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-07 | Included | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok |  | make mention of change request | [9 empty] | request documented | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection
626 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. |  |  | Vol 1 |  |  |  | Noted | Can be provided as part of the operational instructions at hand over 3/7/2017 | Noted: no action required | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
627 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE i. Add an attribute to record the incoming pressure of the valve (incoming_pressure, integer, kPa) during normal operation. |  |  | Vol 1 |  |  |  | George/Haydn | Will be determined at commissioning and can be provided at hand over Proposed Attribute | Included | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | Incoming Pressure
628 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE j. Add an attribute value to record the outgoing pressure of the valve (outgoing_pressure, integer, kPa) during normal operation. |  |  | Vol 1 |  |  |  | George/Haydn | Will be determined at commissioning and can be provided at hand over Proposed Attribute | Included | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | Outgoing Pressure
629 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE k. Add attribute for the maximum headloss through the valve (headloss, integer, kPa) at peak flow (ie, not when valve is shut). |  |  | Vol 1 |  |  |  | George/Haydn | Will be determined at commissioning and can be provided at hand over Proposed Attribute | Included | Included | Will be determined at commissioning and can be provided at hand over Proposed Attribute | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | Headloss
630 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE l. Valve mechanism code list should be similar to: BFL Butterfly DIA Diaphragm SLC Sluice GAT Gate BAL Ball KNF Knifegate DAV Double air FLP Flap gate NED Needle SAV Single air SND Solenoid WSC Check PRV Pressure reducing RLV Pressure relief |  |  | Vol 1 |  |  |  | George/Haydn | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | Sector Discussion | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson | 2.5.3 Valve |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  | change needed in docs | make mention of change request | [8 empty] | document the split | New Code List proposed to split existing Valve Type | Valve Mechanism Butterfly Diaphragm Sluice Gate Ball Knifegate Double air Flap gate Needle Single air Solenoid Check Pressure reducing Pressure relief
631 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE Pressure relief m. Valve operational role code list should be similar to: AIRIN Air In AIROUT Air Out AIRINOUT Air In & Out PRES BDY Boundary Press. Zone CTRLFLOW Control - Flow CTRLPRESS Control - Pressure CTRLFLPR Control Flow & Press SERV Customer Service FIREFIGHT Fire fighting FIRE Fire Service Connection PRESREDU Pressure Reducing PRESRG Pressure Regulating PRESRELF Pressure Relief SAMPLE Sampling Point SCOUR Scour BYPASS Facilate main valve operation DMA BDY DMA boundary isolation NRV Non- return/backflow |  |  | Vol 1 |  |  |  | George/Haydn | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | Sector Discussion | Sector Discussion | Do we split the current field to accommodate 0630 and 0631 GH speak with Martyn Simpson 7/3/2017 | 2.5.3 Valve |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  | change needed in docs | make mention of change request | [8 empty] | document the split request | New Code List proposed to split existing Valve Type | Valve Purpose Air In Air Out Air In & Out Boundary Press. Zone Control - Flow Control - Pressure Control Flow & Press Customer Service Fire fighting Fire Service Connection Pressure Reducing Pressure Regulating Pressure Relief Sampling Point Scour Bypass DMA boundary isolation Non- return/backflow
632 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP a. Include attribute fields describing how the pump is powered - electrical, diesel, petrol. |  |  | Vol 1 |  |  |  | Under Review | Does this relate to the motor or the pump? To be compared to the attributes of the motor. 7/3/2017 | Sector Discussion | Sector Discussion | Does this relate to the motor or the pump? To be compared to the attributes of the motor | 2.5.2 Pump |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
633 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP b. Include attribute fields describing pump orientation (vertical or horizontal). |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.5.2 Pump |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New attribute proposed | Pump oreintation
634 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP c. “Actual pump rate” will at times be meaningless because of Variable Speed Drive (VSD) pumps, that can run at different speeds. This field is therefore either irrelevant for VSD, although it may be an eventual ‘input’ of actual data from control systems. |  |  | Vol 1 |  |  |  | Noted | 2017-03-07 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.2 Pump |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
635 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT a. Include Purchase Date, Install Date, and Warranty Date |  |  | Vol 1 |  |  |  | under Review | Install date - construction date in common attributes, warranty date - warranty start date, Purchase date to be reviewed. 7/3/2017 | Sector Discussion | Sector Discussion | Install date - construction date in common attributes, warranty date - warranty start date, Purchase date to be reviewed. | 2.5.1 Equipment |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
636 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT b. Include Capitalized cost as well as purchase cost |  |  | Vol 1 | ODRC / ORC / RC are included |  |  | Haydn | 2017-03-07 | Included | Included | ODRC / ORC / RC are included | 2.5.1 Equipment | 1 | [9 empty] | 1 | [15 empty] | No action
637 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT c. The abbreviated and full attribute names contained in this table are not related to each other (this is possible a typographical error). |  |  | Vol 1 |  |  |  | Noted | 2017-03-07 | Noted: no action required | Noted: no action required | Resolved in updated version | 2.5.1 Equipment |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
638 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Electrical asset - EQUIPMENT a. An attribute field with an ability to include a SCADA reference should be included. |  |  | Vol 1 |  |  |  | Noted | Refer to Telemetry 7/3/2017 | Noted: no action required | Noted: no action required | Refer to Telemetry | 2.5.1 Equipment |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
639 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Electrical Asset - CABLING a. Ductwork poses a tricky question because it is separate from cabling. Ductwork can be a part of the structure, and can carry many cables. If it is going to be recorded, Ductwork needs to be an asset class in its own right. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
640 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Instrumentation - INSTRUMENTS a. SCADA and RTU (controllers) are not instruments, because they do not measure variables. Include them under electrical equipment. |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | 2017-03-07 | Included | Included | Reviewed and Noted for Inclusion | 2.7.1 Instruments | 1 | [9 empty] | 1 |  |  |  |  | check done |  | done | done | done | n/a | [5 empty] | Change made document updated
641 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | All Asset Classes a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Will ensure that they are applied. 14/3/2017 | Included | Included | Will ensure that they are applied. | General | 1 | [9 empty] | 1 |  |  |  |  | NOTED | [10 empty] | Changes made documents updated
642 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | All Asset Classes b. Missing asset classes: There are a number of missing asset classes in the Wastewater Standard – including “Containment Structures” and “Tunnels”. Wellington Water has 23 containment structures for Wastewater, which is material in terms of asset renewal. |  |  | Vol 1 |  |  |  | George/Haydn | Are these assets part of a treatment plant? If so treatment plants are not included at this point. However both asset classes will be included Not necessarily | Sector Discussion | Included | Additional Assets and attributes will be added to final version | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change response and status to sector discussion also additional work to be further cosnisderation | are these part of treament plants? | n/a |  | n/a | n/a | n/a | n/a | n/a | n/a | request further information from WWL | More information required for a decision |  |  | y | No these are not part of treatments plants, they are assets to include
643 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | All Asset Classes c. It was uncertain how the ‘crossover’ between the Wastewater and Stormwater network is managed within the Standard (including weirs). |  |  | Vol 1 |  |  |  | Noted | Otherwise please be specific about the uncertainty. 14/03/2017 | Noted: no action required | Noted: no action required | Otherwise please be specific about the uncertainty. | General |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
644 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER a. A definition may be required in relation to “relative level”. Relationship of ladders to access chamber; H&S attributes may be required, as ladders need to be certified. Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. This should be considered for inclusion in Volume 2. |  |  | Vol 1 | Include H&S Attributes |  |  | Haydn | 2017-03-14 | Included | Included | Include H&S Attributes | 2.3.1 Access Chamber | 1 | [9 empty] | 1 | [15 empty] | Haydn
645 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS a. Vegetation should not form part of this asset class data attribute for the Wastewater network! |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.2 Channel |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request its part of the asset and important to know it can be split off to other classes after digestion by asset owner | [9 empty] | request documented | More information required for a decision
646 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS b. Is this really an ‘asset class’ for Wastewater (open sewers?) |  |  | Vol 1 |  |  |  | Noted | If they do not exist then this asset class will not be used 14/03/2017 | Noted: no action required | Noted: no action required | If they do not exist then this asset class will not be used | 2.3.2 Channel |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
647 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES a. Generally felt to be a ‘solid’ set of data attributes related to pipes. |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.3.4 Pipe |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
648 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES b. Is there scope for a new field called “expected remaining life” based on observations? |  |  | Vol 1 | Remaining life is 'expected', observed or otherwise (e.g. calculated) - reltaed to intervention type |  |  | Haydn | This is an asset management aspect that will be determined by the asset owner after all data is provided 14/03/2017 | Included | Included | Remaining life is 'expected', observed or otherwise (e.g. calculated) - reltaed to intervention type | 2.3.4 Pipe | 1 | [9 empty] | 1 | [15 empty] | Haydn
649 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES c. How are ‘pipe supports’ treated within the Standard? |  |  | Vol 1 |  |  |  | Under Review | Please provide examples of the types of supports that are used 14/03/2017 | Sector Discussion | Sector Discussion | Please provide examples of the types of supports that are used | 2.3.4 Pipe |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
650 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES d. The “Material Description “ field contents need to be set at the correct level – a significant impact on design life results between different materials such as uPVC, mPVC and oPVC, MDPE, HDPE and HPPE |  |  | Vol 1 |  |  |  | George/Haydn | Don’t know what is being suggested. 14/03/2017 | Included | Included | Material is a mandatory attribute | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 | ok | [12 empty] | No action
651 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES e. Soil Type should also be captured as part of this Standard (impacts design life) and used to inform a wider geospatial dataset. We need to remember that a pipe may cross several soil types. |  |  | Vol 1 |  |  |  | under Review | Was previously discussed and rejected by the TWG 14/03/2017 | Sector Discussion | Sector Discussion | Was previously discussed and rejected by the TWG | 2.3.4 Pipe |  |  | 1 | [7 empty] | 1 | [15 empty] | Change made document updated
652 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES f. Surface Material should be recorded as part of this Standard – impacts structural composition. We need to remember that this field must be an updatable attribute based on non-3W observations. Pipes will also cross several different surface material |  |  | Vol 1 | Add Surface Material |  |  | Haydn | 2017-03-14 | Included | Included | Add Surface Material | 2.3.4 Pipe | 1 | [9 empty] | 1 | [15 empty] | New attribute & associated Code List proposed | Surface Material Surface Material Type
653 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. |  |  | Vol 1 | This is a geospatial layer and can attribute accordingly |  |  | Haydn | I expect that this is captured as part of the Volume 2 14/03/2017 | Included | Included | This is a geospatial layer and can attribute accordingly | 2.3.4 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
654 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION a. In general, the focus group thought this was a well thought out set of attributes associated with Pump Stations. |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.3.5 Pump Station |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
655 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION b. Attributes related to power supply are important; elements of the “electrical” asset class are related to the pump station (see comments in section 2.9 related to the parent-child relationship inherent in pump stations). Attributes include (at least) an ICP number. |  |  | Vol 1 |  |  |  | Noted | Already included. 14/03/2017 | Included | Included | Already included. | 2.3.5 Pump Station | 1 | [9 empty] | 1 | [15 empty] | No action
656 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION c. The Standard is silent on elements related to “Access” and/or “Easements” for this asset class. |  |  | Vol 1 |  |  |  | Noted | Correct. Volume 1 focusses on recording asset data at practical completion 14/03/2017 | Noted: no action required | Noted: no action required | Correct. Volume 1 focusses on recording asset data at practical completion | 2.3.5 Pump Station |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
657 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION d. “Overflow” is a required data element – not included in the Standard. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.5 Pump Station |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request what is required? | [9 empty] | request documented | More information required for a decision
658 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION e. The cost attribute is associated with a particular construction date – ie, the pump station is assumed to be ‘static’. This is not likely. (again – may relate to parent-child relationship of pump station to assets it contains). |  |  | Vol 1 | ODRC / ORC / RC are included |  |  | Haydn | 2017-03-14 | Included | Included | ODRC / ORC / RC are included | 2.3.5 Pump Station | 1 | [9 empty] | 1 | [15 empty] | No action
659 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION f. Safe working limits are a legal requirement  does this form part of the building standard? |  |  | Vol 1 | Depth is recorded |  |  | Haydn | 2017-03-14 | Included | Included | Depth is recorded | 2.3.5 Pump Station | 1 | [9 empty] | 1 | [15 empty] | No action
660 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION g. “Building Owner” could be split between multiple owners |  |  | Vol 1 |  |  |  | George/Haydn | Please provide an example where this has occurred and the benefit of knowing the information. 14/03/2017 | Included | Included | Owner vs manager fields available in the draft standard Catenate multiple owners in field Buildings are separate assets, see buildings | 2.3.5 Pump Station | 1 | [7 empty] | 1 |  |  |  | 1 | suggest you review your response as I don’t think it answers the question about multiple owners of a building. | updated comment not answered |  | change needed to field so as to add comma delimited field only issue cant QA on multiple entries ?? | [9 empty] | More information required for a decision
661 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP a. Elements of a pump may be regarded as a distinct asset – such as motors, impellors, control system, cabling. The attributes of a pump relate to the pump type – this field may need further expansion and/or definition. |  |  | Vol 1 |  |  |  | George/Haydn | Currently information is to be provided about the pump and motors, this does not 14/03/2017 | Excluded | Excluded | Detailed drawing and component information is provided in manuals on handover - a reference attribute is included | 2.4.2 Pump |  | 1 | [6 empty] | 1 |  |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
662 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP b. The line between a pump asset and maintenance is not discussed within the Standard – even though this could change the asset function. |  |  | Vol 1 | Per GISSA |  |  | Haydn | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | Sector Discussion | Sector Discussion | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How its treated after the data is provided is upto each asset owner. | 2.4.2 Pump |  |  | 1 | [7 empty] | 1 | [15 empty] | Change made document updated
663 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT a. The data attributes within this section seem to relate entirely to Electrical Equipment; this does not make sense for this asset class. For example, the “Serial #” field has a description related to “protective material”. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | To be resolved in all 3W tables. 14/3/2017 | Included | Included | To be resolved in all 3W tables. | 2.4.1 Equipment | 1 | [9 empty] | 1 |  |  |  |  | change needed doc | done | done | done | done | n/a |  |  |  |  | possible review check original notes request review from next workshop | More information required for a decision
664 | Oliver Mander | Wellington Water | Wastewater | Vol 1 | [6 empty] | Asset Class: Electrical asset - EQUIPMENT a. “Risk” should be a key field – with a strong relationship to a relevant Volume 2 table. Safety in Design elements (and residual risk) should form part of this also. |  |  | Vol 1 | Links are not within the remit of these standards - this is an analytical element |  |  | Haydn |  | Noted: no action required | Noted: no action required | Links are not within the remit of these standards - this is an analytical element | 2.4.1 Equipment |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
665 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | Data Relationships: Linkages shown in charts between Schema are inconsistent. For example, the “Repairs & Maintenance” schema is shown as interfacing to “As-constructed” and “Condition” schemas. But other Schemas have “Repairs & Maintenance” as an interface. For example, “Financial Performance” and “Demand” both have “Repairs & Maintenance” as an interface. If interlinkages are not shown to be consistent then the validity of the Standard can be questioned. This aligns with the overall statement made in section 1.9 of this document. | Data | Action: The interface tables could possibly be limited to the cohort description, rahter then in the individual schema's. | Vol 2 |  |  | Mapping is not necessarily two way….. Mapping is reflective of reliance of data from elements for interoperaility analytics to determine outputs from those analytics. |  |  | Sector Discussion | Sector Discussion | Relationships are explained in depth in Vol 2 | No Specific Reference |  |  | 1 | [7 empty] | 1 | [15 empty] | No action |  | ? |  |  | 1 | 1
666 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 2. Project Area: The project area artefact could apply to any business project over the 3 waters and not simply a new subdivision reticulation e.g. new facility or augmentation of WW or WS plant, refurbishment of upgrading of network etc. Understanding how projects/investments are delivered and perform is an important AM capability. The metadata schema should not constrain how assets are managed to meet desired outcomes. | Spatial | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Statement noted. This standard is not a tool to manage the asset but a reporting tool. | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
667 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 3. Delivery Risk: In order to generate valid information and outcomes the recording of data in a schema for national reporting will require consistency both within an organisation and between organisations over time. This should be recognised as a risk to the successful delivery of benefits by the Data Standard. | Implementation | Action: to be captured in preamble of the standard. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Delivery risk is a risk for Volume 3 - Methodology | 1.4.2 Intervention Methodologies (Volume 3) |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
668 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 4. Units of measure in asset management would include flow, pressure, time - these are not in the Code list 1, but these and other units are referenced throughout the schemas. Note that different flow and pressure measurement units will apply to different assets or uses. | Code List | Amended Code list | Vol 2 |  |  | Included in draft |  |  | Included | Included | Amended Code list | Table 2: Water Supply Service Attributes | 1 | [9 empty] | 1 | [5 empty] | check if done | n/a | n/a | n/a | n/a | [5 empty] | No action |  | done | y | completed | 1 | 1
669 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 5. Date Range & Traceability: Similar to the comments made in section 2.1 related to Volume 1, key fields in Volume 2 should be auditable, giving the ability to track when changes are made, why and by whom. While a function of an information system, the requirement for such should be included in a metadata standard. | Data | Action required: data scientists to review | Vol 2 |  |  | George | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required tofully iundertstand this feedback, but systems business rules (e.g. date ranges) are the place for defining extents, not these standards Assessors are included Data Table 1: Condition Attributes Assessor_N Assessor Name text | No Specific Reference |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | ? |  |  | 1 | 1
670 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 6. Code lists provided for Volume 2 generally require more work to develop consistent, full and meaningful references for use. We note that code lists have not been provided for Volume 1. | Code List | Code lists are examples, but not exhaustive. Intended to be developed through the life of the standard. A method of expanding the code lists needs to be developed. Action: Codelist of volume 2 to be reviewed. Codelist of volume 1 are provided to some organisations. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Code lists have been updated for comment. | List of Code Lists | 1 | [9 empty] | 1 | [15 empty] | No action |  | N/A |  |  | 1 | 1
671 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 7. Depreciation Data: Depreciation is an indicator of loss of service potential. Replacement value must reflect the true value of replacement in the current environment – which may be different to the environment at original installation. Changes to value and the rate of deterioration may be due to specific changes to asset attributes and environment over time. There must be fields to link changes to time and place. | Financial Performance | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Code List 47: Financial Performance Metrics |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
672 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 8. Lack of observation schema: As noted in section 4.4(a), the lack of an “Observations” schema hampers the ability for observation to inform multiple data schemas – such as condition or updates of asset attributes in the as-built schema. | General | Statement noted. Observations will feed into the attributes. | Vol 2 |  |  | There is a terminology issue here only observation = intervention. Intervention is defined by methodology, one such intervention methodology is a visual assessment (for example) or an observation. |  |  | Noted: no action required | Noted: no action required | Statement noted. Observations will feed into the attributes. | Data Table 1: Condition Attributes |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
673 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | General | [5 empty] | 9. H&S Data: Changes in the way that H&S features are recorded within asset data (“Safety in Design”) may create additional data attributes for assets classes. | General | To be considered. This can be added in, in subsequent revisions. Action: to be discussed with HR. | Vol 2 |  |  | Well made point - let's discuss with you. |  |  | Included | Sector Discussion | Now included in Risk attributes Con_Rat_HS Consequence Rating Health and Safety | Table 7: Risk Attributes | Consequence Rating Health and Safety |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision |  | ? |  |  | 1 | 1
674 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition a. Condition data is relevant for a range of decisions and processes in the asset lifecycle, most particularly around renewals, risk and valuations. The following comments consider these aspects but also apply to many of the other processes in some degree. | Condition | Statement noted. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Statement noted. | 2.2 Condition Schema | Condition Schema | [9 empty] | 1 | [17 empty] | N/A |  |  | 1 | 1
675 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition b. The inclusion of a calculated remaining useful life within the condition schema is fundamentally flawed because it does not account for other relevant asset life determining factors. Examples of such include criticality, demand, performance, optimisation and the asset’s operating environment. By linking condition grade directly to remaining useful life, the schema pre-supposes an end of life or replacement date decision. These conclusions should only be made while considering the wider factors as above. Noting this, Code List 6 linking condition grade to remaining useful life should be removed. | Condition | This is the remaining life based on condition only. Other measures can be considered. Action: Confirm that normal working life is captured in volume 1, to be able to calculate RUL in volume 2. | Vol 2 |  |  | Let's discuss - it's replacement on condition alone. We are not suggesting you should make a decision on condition alone. But oif you want to this is how you would. But if your note is about definition of remaining useful life then let’s chat. |  |  | Sector Discussion | Sector Discussion | Let's discuss - these standards are not about decision-making - they are elements for decisionmaking - these standards define each of these elements. We are not suggesting you should make a decision on condition alone. But if your note is about definition of remaining useful life then let’s chat. | 2.2 Condition Schema |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision |  | ? |  |  | 1 | 1
676 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition c. It is recommended that the schema be modified to take into account the level of confidence in condition grades. There is little or no recognition of the probabilistic nature of condition assessments and hence the confidence limits which apply to the grades. Any condition grade is made within a band of confidence at a point in time. The confidence level is relative to whether it is being applied to a subject asset or extrapolated to an asset group, and whether it is applied at the time of assessment or projected forward. | Confidence | Action: Insertion of confidence grade to be discussed with HR. | Vol 2 |  |  | This is a calculable field, for example, stochasticity |  |  | Noted: no action required | Noted: no action required | This is a calculable field, for example, stochasticity | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
677 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition d. The basis of the interfaces with other schema (Table 5) is unclear and the linkages shown do not acknowledge the relationships between condition data and all other schema. Eg: i. Criticality determines priorities for condition data collection ii. Repairs and maintenance activities are a key potential source of condition data iii. Condition is indicative of likelihood of failure and hence helps determine risk iv. Service and financial performance are impacted by condition v. Demand and utilisation inform the criticality of an asset and hence priority for condition data collection. | Condition | Statement noted. No action required. | Vol 2 |  |  | These are analytical outputs of specific problems being solved. We can discuss |  |  | Noted: no action required | Noted: no action required | These are analytical outputs of specific problems being solved. We can discuss | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
678 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition e. Items included in the condition data attributes (Table 2) appear to be a mix of data at different levels of detail; some being at the assessment level and others at the observation level. Any hierarchy or relationship between these is not implied or explained however. The potential one-to-many linkages from asset to assessments and further to observations are not apparent. Any data required must be clarified in terms of how it relates to other data to enable practical processes for capture and storage. | Condition | Action: To be discussed with Wellington Water. | Vol 2 |  |  | A methodological analytical question. This is a question for the NZ Pipe Replacement Guidelines |  |  | Sector Discussion | Sector Discussion | Action: To be discussed with Wellington Water. | Data Table 1: Condition Attributes |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision |  | ? |  |  | 1 | 1
679 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition f. The description of condition grades against physical deterioration (Code List 2) is a good approach however the terminology is inconsistent. Most descriptors but not all relate to asset failure. All should be described on the same basis to allow for consistent interpretation. “Asset failure” in this sense also requires definition and is unclear in the schema. | Condition | Action: comments for condition 1 and 4 to be changed. | Vol 2 |  |  | Failure of an asset ultimately is when it is unable to provide the service at the level of service as intended upon design - as opposed to 'broken'… e.g.. cracked pipe. This does need more work by the sector. |  |  | Included | Included | Uniform terminology now applies | Code List 16: Condition Rating | 1 | [9 empty] | 1 | [5 empty] | check if done | n/a | n/a | n/a | n/a | [5 empty] | No action |  | ? | y | Updated comment | 1 | 1
680 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition g. The condition grade types (Code List 3) are unclear and do not give any sense of the distinctions or relationships between structural, service, mean, peak and overall grades. | Condition | Action: add structural and overall + add definitions. | Vol 2 |  |  | To discuss |  |  | Included | Included | Condition code lists (e.g. structural, exterior, interior) are now included in Vol 2 | Code List 16: Condition Rating | 1 | [9 empty] | 1 | [5 empty] | check if done | n/a | n/a | n/a | n/a | [5 empty] | No action |  |  | y | Updated comment | 1 | 1
681 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Condition | [5 empty] | Condition h. The condition grade assessment methodologies (Code List 4) and assessment types (Code List 5) are extremely limited and do not capture many methodologies that are currently available and in use. Terminology is not consistent with the purpose of the list, ie; “Cut out” is a sampling methodology rather than an assessment type as listed. A cut out may be assessed visually, by destructive and/or non-destructive testing, or other means. Code lists 7 – 10 are similarly limited and the purpose and usage of which are unclear. | Code List | Action: To be considered to change code list into examples. | Vol 2 |  |  | There was not any intention in std's to define intervention types - should we? Code list 7 - 10 - good point to discuss. |  |  | Sector Discussion | Sector Discussion | See code list | Code List 17: Condition Rating – Methodology |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision |  | ? |  |  | 1 | 1
682 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance a. The Proactive and Reactive Activity Type descriptions need additional clarification to minimise ambiguity. How should “impairment” be interpreted - breakdown, significant performance issue or just incipient failure only detectible with monitoring equipment (e.g. bearing vibration, thermographic image, etc)? Also “Scheduled” needs to exclude non-routine or one-off activities that are set to occur in the future. | Maintenance, Repairs and Maintenance | Action: definition for impairment to be provided: affecting level of service. Change definition of scheduled. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | See code list | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
683 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance b. The schema does not support optimisation of maintenance tasks through RCM analyses or other FMECA based approaches. An example would be the need for a clear and unambiguous definition of asset function. This is not well covered in Part 1 attributes. Comment should be requested from an RCM practitioner. | Maintenance, Repairs and Maintenance | Statement noted. This is not a maintenance management system. | Vol 2 | [5 empty] | Noted: no action required | Noted: no action required | Statement noted. This is not a maintenance management system. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
684 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance c. Recording the “Image_ID” against activities does not cater for referencing other types of digital files. Suggest this optional attribute is made generic and capable of accepting hyperlinks to reference files in other systems. | Maintenance, Repairs and Maintenance | This is an analytical requirement | Vol 2 | [5 empty] | Noted: no action required | Noted: no action required | This is an analytical requirement | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
685 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance d. Fail_Mode and Cause_Iss is important but must be specific to each asset type rather than generic across all assets. It’s not clear if this is the intention. | Maintenance, Repairs and Maintenance | Statement noted. No action required, it is the case. | Vol 2 |  |  | Yes it is. |  |  | Noted: no action required | Noted: no action required | This is an analytical requirement and is matched to other elements (e.g. AssetID) to determine response | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
686 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance e. A key decision for every asset is to either run to failure or apply a scheduled maintenance/inspection plan. | Maintenance, Repairs and Maintenance | Statement noted. No action required. | Vol 2 |  |  | This is an analytical requirement (i.e. both) |  |  | Noted: no action required | Noted: no action required | This is an analytical requirement (i.e. both) | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
687 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance f. In Part 1 Condition Assessment Type is an asset attribute, but Condition is part of a different schema. Shouldn’t these go together to reflect the fact that the condition assessment approach may change over time? | Maintenance, Repairs and Maintenance | See comment HR. | Vol 2 |  |  | Yes, but in the analytical phase. |  |  | Included | Included | Yes, but in the analytical phase. | No Specific Reference | 1 | [7 empty] | 1 |  |  |  |  | add HR comment Yes, but in the analytical phase. | Yes but in the analytical phase see code lists | [11 empty] | No action |  |  |  |  | 1 | 1
688 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance g. It isn’t clear how maintenance strategies are to be handled (i.e. managing maintenance work that has weekly/monthly/annual/ etc activities). AMIS functional requirements should be considered before fields like Recur and Recur_Cyc are established. | Maintenance, Repairs and Maintenance | Statement noted. Standard is not intended to populate a maintenance plan. | Vol 2 |  |  | Yes, but this informes the decision. Not a schema document? A policy decision. |  |  | Noted: no action required | Noted: no action required | Standard is not intended to populate a maintenance plan. Code Lists are included to handle this requirement e.g. Recurrence Cycle | Code List 5: Recurrence Cycle Unit |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
689 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance h. Need quantity as well as cost information to be able to analyse trends and predict future costs. Need to record all resources – not restricted. | Maintenance, Repairs and Maintenance | Statement noted. Code lists for quanitifying repairs requested from Working Group but have not yet receieved. Can populate further depending on if code lists are meant to be examples or exhaustive. | Vol 2 |  |  | It does. |  |  | Noted: no action required | Noted: no action required | Code lists for quanitifying repairs included | Code List 6: Bases of Cost |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | New Code List from Working Group |  |  |  |  | 1 | 1
690 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance i. The combination of Activity Type, start date/time, end date/time does not appear to meet the requirements for DIA non-financial reporting for urgent/non-urgent callouts (i.e. need to separately record time to reach site and time to resolve issue). | Maintenance, Repairs and Maintenance | Action: Align standard with with DIA requirements | Vol 2 |  |  | This is a Volume 3 Item - or a management system item |  |  | Noted: no action required | Noted: no action required | Type of maintenance activity is included | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
691 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance j. There needs to be a new Event Type similar to “Upgrade/Improvement”. Irrespective of the funding source (capital vs operational) assets need to have a full history of events recorded against them. If we exclude upgrades and rely solely on project registers to capture this information we make lifecycle management significantly more difficult. | Maintenance, Repairs and Maintenance | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Vol 2 |  |  | Upgrade is a new asset and would be recorded as such. |  |  | Noted: no action required | Noted: no action required | Statement noted. Capital improvements are covered under the financial performance schema. Operational improvements are covered under R&M schema. Upgrades may flow through as new As-constructed data. | Code List 49: Description of Financial Performance Element |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
692 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance k. Why record overflows etc. in repairs and maintenance schema and not in the level of service? Overflows are recorded per financial year, different organisations have different financial years, is history recorded i.e. over time. Should other compliance activities i.e. RON and CDEM should also be coded. | Maintenance, Repairs and Maintenance | Action: overflows goes into level of service. | Vol 2 | [5 empty] | Included | Included | One is a record of the type event One is a record a service level e.g. overflows per year and an analytic | Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
693 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance l. Asset versus component issue can give rise to different design criteria and system performance i.e. a pump has a l/s design while a filer has (say) minimum pressure drop, but it is performing of the pumping station that is the issue. | Granularity | Statement noted. Granularity question to be answered by organisation. | Vol 2 |  |  | but granularity question to measure all you require. |  |  | Noted: no action required | Noted: no action required | Statement noted | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
694 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance m. Does not appear to allow for other investigation methods e.g. vibration analysis, DCVG results, thermal imaging, usage data analytics for identifying if an intervention is required. | Code List | Code lists to be developed in the future. | Vol 2 |  |  | , but a code list… |  |  | Included | Included | Code lists to be discussed against current code lists e.g. Condition (This is really a Volume 3 question) | Code List 17: Condition Rating – Methodology | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
695 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance n. As found and as left condition or status is useful for items like valves, could also apply to depth of cover, locks etc. | Maintenance, Repairs and Maintenance | Statement Noted: No action required. | Vol 2 | [5 empty] | Included | Included | Statement Noted: No action required. | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
696 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance o. Asset performance does not clearly link to key result areas or key performance indications set by organisations in the management of assets or demanded by consumers. | Maintenance, Repairs and Maintenance | Action: To be discussed with Wellington Water. Further clarification required. | Vol 2 |  |  | Let's discuss this is important. |  |  | Sector Discussion | Sector Discussion | This is an anlytical question - discuss with sector | No Specific Reference |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision |  | ? |  |  | 1 | 1
697 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance p. Asset or service performance - it is not clear what is referred to or if this is consistent. | Maintenance, Repairs and Maintenance | Action: To be discussed with Wellington Water. Further clarification/examples required. | Vol 2 | [5 empty] | Sector Discussion | Sector Discussion | Section updated in Volume 2 | 5.4 Service Performance Schema |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision |  | ? |  |  | 1 | 1
698 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance q. How are components and soft parts etc linked to assets, is the lifecycle of O&M supported by this? | Granularity | Statement noted. Component type is an attribute in the repair schema and captured under each asset. Granularity Issue. | Vol 2 |  |  | To discuss - but an analytical question. |  |  | Noted: no action required | Noted: no action required | Component type is an attribute in the repair schema and captured under each asset. | 2.3.4 Components of Repairs, Maintenance and Operations |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
699 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance r. Benchmarking - same as identified in service levels schema, consistency is required for valid and useful outputs to be obtained. | Maintenance, Repairs and Maintenance | Statement noted and agreed. | Vol 2 |  |  | Agreed. |  |  | Noted: no action required | Noted: no action required | Statement noted and agreed. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
700 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance s. Outage duration - mandatory for all actions but what if no outage? Also what if the customers are reinstated over time ie 95% connected in 1 hour while the rest are out for days? Outage is linked to ' number of people' - this can be impossible to measure depending on each connection (as in an apartment block), would customer or property be a better measure. | Maintenance, Repairs and Maintenance | Agreed. Then outage duration = 0. | Vol 2 |  |  | Or both? Mesh blocks - population specifically (dept stats) - how we calculted 'density'. |  |  | Noted: no action required | Noted: no action required | Agreed. Then outage duration = 0. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
701 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance t. Third party damage excluded from outage definition but included in repair schema as cause. | Maintenance, Repairs and Maintenance | Action: 3rd party damage to be included. | Vol 2 | [5 empty] | Included | Included | Third Party attribute included | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause | 1 | [7 empty] | 1 | [7 empty] | check with haydn if done | n/a | n/a | n/a | n/a | [5 empty] | No action |  |  | y | Updated comment | 1 | 1
702 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance u. Maintenance planning - focused on time based maintenance (elapsed), but could encompass operating hours or CBRM. A MMS would do a better job, would it be better not to specify these matters in the schema and just have an objective for an outcome based system in place. This could be applied throughout the data standard noting the issues with consistently in benchmarking. | Maintenance, Repairs and Maintenance | Action: clarify with Oliver Mander | Vol 2 |  |  | To discuss |  |  | Sector Discussion | Sector Discussion | Analytical elements included in standards to schieve this analytic | No Specific Reference |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision |  | ? |  |  | 1 | 1
703 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance v. It would be desirable to have costs for maintenance collected on an area/project basis for performance analysis. | Granularity | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | Vol 2 |  |  | Costs are collected at an assetID first, but analytically examined per note. |  |  | Included | Included | Statement noted. Granularity Issue. Cost are related to asset. Project cost are not required as they can be calculated as a number of assets together. (project or area cost) | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
704 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Repairs and Maintenance | [5 empty] | Repairs and Maintenance w. Should complaints be linked to an issue or root cause rather than an address or asset - this would enable better linking and development of appropriate solutions and priority setting than a collection of disparate reports. Also need to know the outcome of the assessment of a compliant ie internal plumbing, no issue found etc before an organisation make decisions on number of complaints. Option of an outcome based CRM system rather than data standard? | Maintenance, Repairs and Maintenance | Action: Add in "root cause" Consider putting complaints in Service Performance. | Vol 2 |  |  | Asset first, root cause second… You always know asset, cause can be problematic. CRM system: this is the derivative LOS. |  |  | Included | Included | Linking CRM information to asset information is not in scope These root cause examples in the code list are asset related interrogations for asset management purposes. | No Specific Reference | 1 | [7 empty] | 1 | [7 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
705 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Utilisation | [5 empty] | Utilisation a. Asset utilisation needs to consider the level of redundancy in the network or asset system required to achieve the desired overall level of risk. The proposed calculation of utilisation could work for an individual pump, but would be of little/no value for a trunk main network. It could easily be misinterpreted. | Utilisation | Action: Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | Vol 2 |  |  | Yes it does - level of redundancy Agree - Utilisation is optional |  |  | Included | Included | Redundancy is include in the codelists in Vol 2 as an analytical attribute (see vulnerability). | Code List 43: Global Resilience Rating Elements | 1 | [7 empty] | 1 | [7 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
706 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Utilisation | [5 empty] | Utilisation b. Until the intervention methodologies are proposed for each of the 3 waters we find it difficult to understand what fields may or may not be wanted for this schema. | Utilisation | Statement noted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Statement noted. | 3.2.5 Code Lists |  |  |  | 1 |  |  |  |  | 1 | [22 empty] | 1 | 1
707 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Demand | [5 empty] | Demand a. Demand applies to collections of assets. Why would you want to record demand against an individual asset such as a pipe or valve? | Demand | Statement noted. You would require information at both asset at network level. Granularity question. | Vol 2 |  |  | Time value of utilisation |  |  | Included | Included | This is an analytics requirement, but may no be required agaist all asset components. | No Specific Reference | 1 | [7 empty] | 1 | [22 empty] | 1 | 1
708 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Demand | [5 empty] | Demand b. The fields offered are very limiting in this schema and the use of demand needs to be thought through in more depth. | Demand | Statement noted. Typically only interested in the flow. Some confusion may be caused by the coverage at the front end which covers non-pipe and pump assets such as retaining wall which do not really have a demand. | Vol 2 |  |  | Algorithms for current, potential and future demand are available |  |  | Noted: no action required | Noted: no action required | Demand Section has been updated in Volume 2 | 3.3 Demand Schema |  |  |  | 1 |  |  |  |  | 1 | [22 empty] | 1 | 1
709 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Demand | [5 empty] | Demand c. Peak demand at a system level is not the sum of zone demands due to the diversity/averaging effect as the study area increases in size. Average demand at a system level is the sum of the zone demands. The schema does not seem to recognise this. | Demand | Action: clarify with Oliver Mander. Granularity question to be determined by the organisation. | Vol 2 |  |  | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler |  |  | Noted: no action required | Noted: no action required | The standard is not saying this, its describing the attributes to determine peak demand at any point on the network at any time It's an analytical enabler | Data Table 4: Demand Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
710 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Demand | [5 empty] | Demand d. What analytics would this schema (as is) be used to support? | Demand | Statement noted: Used to support justification for asset enhancement. | Vol 2 |  |  | population growth (future demand) against current demand using flow readings at poin ton network where growth is expected (for example, a pipe connection point where a new subdivision is expected to connected to) |  |  | Noted: no action required | Noted: no action required | Future connections on flow (population demand) | Code List 33: Demand – Measure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
711 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Demand | [5 empty] | Demand e. Should this schema exist in an AMIS? | Demand | Statement noted. Yes. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Yes | 3.3 Demand Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
712 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Criticality | [5 empty] | Criticality a. Criticality is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Criticality | No change | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No change | 4.3 Criticality Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
713 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Criticality | [5 empty] | Criticality b. The current approach to criticality from Wellington Water uses criticality as an equivalent to consequence in the evaluation of risk. To this effect the criteria for criticality that we have developed uses cumulative weighted impacts in combination with importance (exposure) factors to derive risk. My view is that the criticality descriptors offered in the standards are only one component of the consequence variable in the risk equation ie the exposure factor. To this extent it is puzzling to identify how criticality as described could be used in the evaluation of risk – given the subsequent content of the risk schema. | Criticality | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | Vol 2 |  |  | This standard is about defining the analytical attributes which calculate, in a quantitative way the decision elements wwhich infulence investment in public assets. When and how asset manager chose to do this is at their discretion. Some have interoperability algorithms which analyse these elements, this is the intent of these metadata standards. There is more detailed explanation in the Section 4. |  |  | Noted: no action required | Noted: no action required | Criticality and Risk are treated as two separate schemas in line with project requirements. The philosophy of the project is to "silo" the schemas. Criticality only considers the amount of people and type of facility left without services. | 4.3 Criticality Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
714 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Criticality | [5 empty] | Criticality c. For example if the renewal of a pipe was being considered wrt risk of failure – condition is an indicator of probability, the potential impacts could be social, environmental or financial loss and the exposure is measured by the number of people or the importance of the facility affected by the loss of service. | Criticality | Statement noted. | Vol 2 |  |  | These are analytic outputs using the schemas, with other data sets (for example, economic data) to determine a specific output. |  |  | Noted: no action required | Noted: no action required | These are analytical inferences which are attributed in code in algorithms by attributes these standards define | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
715 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Criticality | [5 empty] | Criticality d. Until worked examples are provided as to how the consultants perceive criticality being used for different decisions we struggle to see how the schema as offered would be useful or at best would have limited value. | Criticality | Statement noted. Will become apparent when resilience and vulnerability schema's are added. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Explanation found in criticality schema | 4.3 Criticality Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
716 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Criticality | [5 empty] | Criticality e. The code list 27,28,29 tables have some potential flaws in our view. i. Special facilities is too vague as a term for Code 5. Few utilities would have munition storage or critical data centres and in most cases data centres would have back up. How is this derived for example if it was potential damage from blowing up a munitions store, how would compare to an LPG centre or holding tanks containing solvents ii. For a water utility is a hospital really less critical than a data centre? iii. What happens when an asset services 3 or 4 hospitals iv. Where is economic loss factored into these tables – they seem to be very “government” centric v. We struggle to think that decision making using criticality for small towns of less than 5000 people would only ever have code 3 assets as their most important asset. Risk is about context and the context must consider the community and the economic scale of their investment. We do not believe one size fits all. | Criticality | I. Incorrect table shown in standard is. To be actioned. II. To be actioned. III. Picked up by higher residential rating. Statement noted. IV. Criticality is about the network and not about economics. V. Statement noted. | Vol 2 |  |  | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. |  |  | Noted: no action required | Noted: no action required | i. noted ii. Per the NZ Building Code iii. Criticality increases iv. Economic loss like economic yield is a calculable field… other data sets are required e.g. property, GDP (or the economic rent). v. neither do we. Let's chat. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
717 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk a. Risk is used in some way as an important component to the following decisions i. Maintenance Planning ii. Understanding Operational Risk iii. Operational Performance iv. Understanding Customer service v. Understanding the impacts of obsolescence and new technologies vi. Planning asset disposal vii. Planning for growth or decline viii. Understanding and planning network capacity ix. Levels of service improvements including environmental outcomes and consents x. Hazard Resilience planning xi. Renewals planning | Risk | Statement noted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Statement noted. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
718 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk b. We assume that the risk schema is intended to facilitate risk management within water utilities. | Risk | Statement noted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Yes, and for buildings per the Biulding Standard | 4.4 Risk Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
719 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk c. We have reviewed this schema with respect to the principles of risk management as outlined in Section 3 of the guideline document for AS/NZS 31000:2009 | Risk | Statement noted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Noted | 4.4 Risk Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
720 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk d. In particular the schema as drafted inhibits the following principles: | Risk | Statement noted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Noted | 4.4 Risk Schema |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
721 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk e. 3(g) Risk management is aligned with the organisations external and internal context and risk profile | Risk | Further discussion with Wellington Water. Discussed at workshop in depth. | Vol 2 |  |  | This is about the risk of an asset |  |  | Sector Discussion | Sector Discussion | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema |  |  | 1 | [7 empty] | 1 | [15 empty] | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  | ? |  |  | 1 | 1
722 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk f. 3(h) Risk management recognises the capabilities, perceptions, and intentions of external and internal people that can facilitate or hinder the achievement of the organisations objectives | Risk | Statement noted. | Vol 2 |  |  | These standards are about the risk of assets |  |  | Noted: no action required | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema |  |  |  | 1 | [6 empty] | 1 | [15 empty] | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  |  |  |  | 1 | 1
723 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk g. 3(j) Risk management continually senses and responds to change. As external and internal events occur, context and knowledge change, monitoring and review of risks takes place, new risks emerge, some change, others disappear | Risk | Statement noted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct | 4.4 Risk Schema |  |  |  | 1 | [6 empty] | 1 | [15 empty] | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  |  |  |  | 1 | 1
724 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk h. To propose a specific risk matrix into a national standard seems to conflict with these basic principles | Risk | Statement noted. There is a tradeoff between being organisation specific and national application. The schema presented is intended to be adopted to by all organisation hence it may not align with the organisations risk profile | Vol 2 |  |  | There is an analytical answer to this question, related to scale and audience |  |  | Noted: no action required | Noted: no action required | This is a risk schema for assets to inform organisationsal risk assessments, within an analytical construct And any organisation can taylor the analysis to the local context | 4.4 Risk Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  |  |  |  | 1 | 1
725 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk i. Although interdependencies between other schemas are stated it is difficult to extract how they would be used together. Risk, criticality and condition must be interconnected but there is no indication as to how the application of these schemas would allow this | Risk | Resolved with cohorts. | Vol 2 |  |  | This is the role of data and interoperability analytics. |  |  | Noted: no action required | Noted: no action required | This would depend on the problem being solved and the analytical approach in doing so | 4.4 Risk Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  |  |  |  | 1 | 1
726 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk j. The suggestion that probability scales for different events and water types are the same is unhelpful in the absence of worked examples. Are there examples to demonstrate a sensible cross relationship for the use of probability scales in water supply and stormwater? | Risk | Statement noted. Likelihood scales are intended to cover the majority of events that may occur to any of the 3 waters. Furthermore, probability scales based on indicative tables in ISO 31000. | Vol 2 |  |  | Yes, but this is contextual and the sensitivity and scenario's analysis will show this in time. |  |  | Noted: no action required | Noted: no action required | Unclear of what this means, but the scales are adaptive to event type, but specifiuc to asset type | 4.4 Risk Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | To discuss analytical elements and algorithmas that analyse risk with regards to 'assests' |  |  |  |  | 1 | 1
727 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk k. Other than flood risk, how do you assess time based probabilities? The use of the word “time to time” or “in your career” will lead to subjective assessments that will simply promote inconsistent investment decisions rather than secure them. | Risk | Statement noted. Yes there is a part subjectivity to this. | Vol 2 |  |  | Time base probabilities are statistically calculable (actuarial analysts) output |  |  | Noted: no action required | Noted: no action required | Code list updated | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  |  |  | 1 | 1
728 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Risk | [5 empty] | Risk l. We believe the contents of the fields that describe 1- 5 consequences should be omitted. A decision to occupy these fields for a national risk schema to derive nationally consistent approaches to risk will do exactly the opposite – it promotes subjective assessment and also directly contravenes the principles of risk management as described in AS/NZS 31000. | Risk | Statement noted. This approach was agreed at Technical Working Groups. Consequences established at Technical Water Group to cover full range of consequences regardless or organisation size Action: to be discussed with Wellington Water. | Vol 2 |  |  | To discuss |  |  | Noted: no action required | Noted: no action required | To discuss, see code lists | Code List 41: Consequence Rating |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | More information required for a decision |  |  |  |  | 1 | 1
729 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Resilience | [5 empty] | Resilience NO schema offered However, we urge you to consider a fundamental question when addressing resilience for water utilities. Is the assessment of an assets’ resilience important or is it more important to assess the resilience of the service provided to customers on a national scale? We would suggest the latter, and therefore question the merits of offering a schema for asset resilience. If it is the latter, we also suggest that resilience is better attributed to customers rather than assets. | Resilience | Updated | Vol 2 |  |  | Included in draft |  |  | Included | Included | Schema updated | 4.5 Resilience Schema | 1 | [7 empty] | 1 | [17 empty] | No action |  | Done |  |  | 1 | 1
730 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Design Performance | [5 empty] | Design Performance This schema is not required. We don’t need evaluative criteria here. Attributes should be in the as built schema and actual performance should be in service performance. Table 12 in all volume 2 documents (sections 9.3) refer to the linkages with the resilience schema not the design performance | Design Performance | Statement noted - keep schema. No action required. | Vol 2 |  |  | Let's discuss this is important. |  |  | Noted: no action required | Noted: no action required | Let's discuss this is important. Design performance is different than Service Performance | 5.2 Design Performance Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | More information required for a decision |  |  |  |  | 1 | 1
731 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Financial Performance | [5 empty] | Financial Performance a. General comment – It would be interesting to know what is determined to be core data requirements with regards to the attributes. There is a large set of attributes to collect a large number would only be relevant to a small number of organisations. | Financial Performance | Action: Mandatory fields to be reviewed. Granularity question - Organisation to determine what level of granularity to collect data at. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | 5.3 Financial Performance Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
732 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Financial Performance | [5 empty] | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Financial Performance | No Change - this was agreed with ML | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
733 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Financial Performance | [5 empty] | Financial Performance b. Costs of maintenance activities is not obvious – is contained in the Repairs, Maintenance and Operations Attributes table. | Financial Performance | No Change - this was agreed with ML | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Cost of asset activities are not financial performance of assets | 5.3 Financial Performance Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
734 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Financial Performance | [5 empty] | Financial Performance c. Valuation date doesn’t seem to appear anywhere. | Financial Performance | No change - it is present. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Included in standards | Data Table 10c: Valuation Attributes Details (Collected Level Indicated) |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
735 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Financial Performance | [5 empty] | Financial Performance d. Linking the financial information e.g. revised asset lives with condition data. | Financial Performance | Statement noted - that is the intend. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Attributes included in standards, this is an analytical exercise | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
736 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Financial Performance | [5 empty] | Financial Performance e. Terminology is not consistent with the Repairs and Maintenance schema e.g. reactive/planned/etc. | Financial Performance | Action: Clarify comment with Oliver. The financial performance scheme generally does not make reference to the Repairs, Maintenance and Operation schema other than to say that expenses are recorded there. There does not appear to be any inconsistency | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Now consistently applied | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
737 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance Level of service is recorded against individual assets, this may cause issues where service level is required from a network, facility, project, contract or organisational levels. These levels of service may not directly relate to asset parameters or the level of service at an asset may relate to another asset upstream (e.g. minimum pressure at a downstream point relates to the upstream network and pumps/regulators etc). Also levels of service are not static and these may change (this change may be the result of internal or external drivers). | Granularity | Statement noted. No action required. Table 15 indicates that some elements can be measured at different levels, as necessary. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | These are analytical constructs from an individual assetID dataset. How consolidated into geographic units os for the specific analysis, e.g. network, zone, catchement etc. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
738 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance a. Benchmarking relies on the consistency of inputs. In order to generate valid information and outcomes the recording of data in a scheme for national reporting will require consistency in an organisation, between organisations and over time. Other national standards have shown there are issues with this approach, will the benefits of a metadata standard be realised (what are the risks and assumptions to the achievement of this benefit)? | Service Performance | Statement noted. No action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | This is a reference to standardised analytical approaches | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
739 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance b. Residential demand figure, valid for industrial or commercial areas, how updated and how is history against assets recorded? | Service Performance | Statement noted. It's only applicable for residential areas. History: Implementation question. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | This is a reference to an analytical approach. E.g. ParcelID District Plan Zone type and connection demand (or Level of Service). | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
740 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance c. Is it feasible that the same assessor (individual) is used for all items in each asset i.e. cultural significance and technical design and financial measures? | Service Performance | Statement noted. Multiple assessors can be used. Organisation can decide. No action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | The same or multiple | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
741 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance d. Consents compliance is linked to an asset when consents are typically given on an activity/facility - correct linkages and business processes will need to be established and implemented to ensure that compliance is achieved in light of asset changes. | Service Performance | Action: Consent attributes generally captured at property level which is inconsistent with reporting at network/zone level as specified in the stands. An allowance is made for capturing at asset level if the capability is available - make this clearer | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Consent attributes ar captured at property level which is not inconsistent with reporting at network/zone level - i.e. it is a spatial query between the two data sets. The attributes are specified for capturing asset detail in the standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
742 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance e. Third party damage is excluded from service measures (interruptions) for water supply. This is a valid facet of AM, and the scheme has this included in repair and maintenance for WW assets. | Service Performance | This is to be consistent with Water NZ’s National Performance Review. This measure is aligned to their NPR WSS1 measure and excludes third party. We agreed to just have one measure and not three for simplicity. There is a separate measure NPR WSS4 for third party interruptions: The number of unplanned interruptions to service caused by third parties Note that NPR WSS3 is for maintenance and repair interruptions: Total number of planned interruptions to water service for maintenance or renewal works | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Included in the Standards | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
743 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance f. MoH grading should be linked to a time the grade was awarded, and possibly should be greater than just a single field i.e. who assessed etc. We question the merit of this as a valid asset performance measure as it is always system based. | Service Performance | This MoH grading measure was put forward for inclusion by workshop participants. WSL includes this measure but only for treatment. We noted it as optional so OK for it to be deleted. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Included in the Standards | Data Table 11: Service Performance Attributes – Functional |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
744 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Service Performance | [5 empty] | Service Performance g. The fact a health and safety assessment has been carried out is interesting, but it is the results that are important (have the risks been addressed or are there outstanding issues etc) and there is no mention of this. | Service Performance | Statement noted. Outside of scope. See Haydn's comments | Vol 2 |  |  | Noted - but not for the standard, this is a process question. And, a question for any OH&S Manager of an HRIS for an organisation |  |  | Noted: no action required | Noted: no action required | Included in the Standards | Table 2: Water Supply Service Attributes & Code List 41: Consequence Rating |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | whats your comment? | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
745 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Maintenance Planning | [5 empty] | Maintenance Planning i. Will the scheme provide an effective (and efficient) link to maintenance management systems that are in use currently? | Implementation | Statement noted. Yes that is the intention for the future. | Vol 2 |  |  | noted |  |  | Included | Included | Yes that is the intention for the future. | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
746 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Maintenance Planning | [5 empty] | Maintenance Planning ii. Are all costs collected at an asset level, won't different treatments give rise to different outcomes, ie, where are staff or contractor costs added to a facility, item or asset. Is maintenance carried out on assets as they exist or on notional assets? | Maintenance, Repairs and Maintenance | Statement noted. Cost of any Repairs, Maintenance and operations captured at asset level. Granularity issue to be decided by organisation. | Vol 2 |  |  | Analytical question - but likely maintenance applied to cohorts. |  |  | Included | Included | Application of costs will be at the discretion of the rganisation, but likely to be applied to a cohort of assets when being maintained | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
747 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Operational Performance | [5 empty] | Operational Performance i. Actual performance should also be recorded as well as consent compliance - is water quality improving over time or always just inside the limit? | Service Performance | Action: add in to schema (design performance? Service performance) | Vol 2 |  |  | To discuss, include 'result of analysis attribute' |  |  | Included | Included | Action: add in to schema (design performance? Service performance) | Data Table 9: Design Performance Attributes | 1 | [7 empty] | 1 | [17 empty] | No action |  | already done |  |  | 1 | 1
748 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Operational Performance | [5 empty] | Operational Performance ii. There is reference to LAWA framework – is this commonly used throughout the country? Would it be better to refer to the National Policy Statement or specific Regional rules as applicable for the authority? | Service Performance | Action: LAWA was discussed at the working group | Vol 2 |  |  | All regional councils use LAWA |  |  | Noted: no action required | Noted: no action required | All regional councils use LAWA | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
749 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Valuation and Depreciation | [5 empty] | Valuation and depreciation Asset life versus economic/accounting life, does asset structure match the chart of accounts used by all organisations and applied in all business models i.e. contracted services? | Financial Performance | See Haydn comment | Vol 2 |  |  | IFRS standards apply here. |  |  | Noted: no action required | Noted: no action required | Yes - there are appropriate fields for ODRC, ORC, RC and Forecast, Actual and Budget financial information in Finance Performance sections | Code List 47: Financial Performance Metrics |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | whats your comment? | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
750 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Planning for growth or decline | [5 empty] | Planning for growth or decline i. Assets will need lifecycle stages not just in service ie proposed (linked to project), out of service, in store, abandoned, leased for F/O etc (assets can provide other services, not just those implicit in the standard) | Maintenance, Repairs and Maintenance | Action: to be incorporated by 3 waters and buildings. Code list. Discuss which schema to include under | Vol 2 |  |  | Codelists exist which include this |  |  | Included | Included | Discuss with Sector - to consider schema | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | Create a code list of service types as suggested here? |  |  |  |  | 1 | 1
751 | Oliver Mander | Wellington Water | 3-Waters | Vol 2 | Planning for growth or decline | [5 empty] | Planning for growth or decline ii. Levels of service can change over time on different assets, this will need to be understood/recorded | Service Performance | Statement noted. No action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Atributes to do this are included in the standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
752 | Todd Davis | SCIRT | Wastewater | Vol 1 | 1 | 1 | 1 |  |  |  | In talking about As Managed, I assume this is for how the councils handle data rather than how the data supplied by survey from the field, as these are two different worlds? |  |  | Vol 1 |  |  |  | George/Haydn | Cannot find in document to determine context 14/03/2017 | Sector Discussion | Sector Discussion | This is a discussion in the development of Volume 3 | No Specific Reference |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | ok | [12 empty] | No action |  |  |  |  | 1 | 1
753 | Todd Davis | SCIRT | Wastewater | Vol 1 | 1.5 | 3 | Table 1 Date submitted |  |  |  | While there is a date submitted and date constructed, there isn't an associated surveyed date. This is important, as this is when the assets were actually captured and events (e.g. earthquakes) could alter survey data and data owners should be aware of this |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion Surveys are discrete interventions and recorded as such (i.e. before an event and after an event) | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  |  | is this to cover existing infrastructure that has been surveyed? | yes, i.e. when it was last surveyed Don’t agree that it’s an extra field | Not necessarily part of the As Cons. It’s a separarte event and can be done when required and recorded in the asset owners system | [10 empty] | More information required for a decision
754 | Todd Davis | SCIRT | Wastewater | Vol 1 | 1.5 | 3 | Table 1 Transformation |  |  |  | There is increased risk to data accuracy in companies that are not working all the time with software projection transformations. As the client, I would always want to receive the data in it original projection and transfer it myself |  |  | Vol 1 |  |  |  | George/Haydn | The requirement is for each company to deliver the data in the final projection and datum | Included | Included | The requirement is for each company to deliver the data in the final projection and datum | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
755 | Todd Davis | SCIRT | Wastewater | Vol 1 | 1.9 | 4 | Table |  |  |  | Why is this BIM Enabled? Should this not be BIM Enabled/Geospatial Representation as these still hold and display 3d information. |  |  | Vol 1 | Update, asset management and facility management systems do…. |  |  | Haydn | Geospatial systems do display 3D data other than the ability to store the information as attributes 14/03/2017 | Noted: no action required | Noted: no action required | Update, asset management and facility management systems do…. | 1.9 Data Principles |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
756 | Todd Davis | SCIRT | Wastewater | Vol 1 | 1.1 | 5 | 1 |  |  |  | This surely should be "current parcel" boundaries. Not sure as to what a title/property boundary is, as what is the definition of property (residence, address, rating unit, parcel(s))? Also, is this relevant?You want the assets to be shown in true survey location even if this shows them being constructed illegally through private property. |  |  | Vol 1 |  |  |  | George/Haydn | Is this meant to be 2.1? Duncan can you answer 14/03/2017 | Sector Discussion | Sector Discussion | For analytical purposes Have added 'geographical units' code list | 2.1 Technical Reference Information |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | suggest you review your response as it doesn’t answer the question about the accuracy of captuirng and showing them in their systems. This was agreed to by the TWG | For analytical purposes Have added 'geographical units' code list updated comment | [11 empty] | More information required for a decision
757 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.1.2 | 8 | 4 |  |  |  | I believe this is how data should be stored, but supply of data should be as captured. By forcing this to the supplier you are increasing the risk of error, with groups that will only project data occasionally more likely to make mistakes |  |  | Vol 1 |  |  |  | George/Haydn | The intent of this is to educate the indutsry in what capability it will need | Noted: no action required | Noted: no action required | The intent of this is to educate the indutsry in what capability it will need | 2.1.2 Projections and Datums |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
758 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.1.5 | 10 | Attribute Name |  |  |  | Why would you develop a new specification and then allow for it to be supplied in a historic format such as shapefile. This also means that the defined "text" geometry type cannot be supplied and instead would need to be changed to a point |  |  | Vol 1 |  |  |  | Noted | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF has. 14/03/2017 | Noted: no action required | Noted: no action required | Currently this is still a preferred format for many organisations as they have the capability to author and edit. In time this will become redundant in much the same way that DXF | 2.1.7 Metadata Definitions |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
759 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Format Instructions Cost |  |  |  | Is this cost of the asset or cost of the asset plus installation? Is this standard cost of the recommended price of the asset, rather than any discounts were achieved? |  |  | Vol 1 | All replacement costs include installation |  |  | Haydn | 2017-03-14 | Noted: no action required | Noted: no action required | All replacement costs include installation | 2.1.10 Common Attributes |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
760 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | 3 |  |  |  | Is the central location the centre of access (i.e. manhole lid)or the centre of the structure? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. 14/3/2017 | Included | Included | Centre of the structure. However the description and diagrams need to be modified to reflect that the requirement for the placement of the point is at the intersection of the pipe assets. | 2.3.1 Access Chamber | 1 | [9 empty] | 1 | [6 empty] | done | done | done | n/a | [5 empty] | Change made document updated
761 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.3.1 | 21 | Figure 5 |  |  |  | Pipe length shown here is neither the length of the digital pipe feature or the length of the real world feature, as you are not taking into account the "faux" pipe connectors angle. The middle pipe length here is very confusing! |  |  | Vol 1 | Agreed |  |  | Haydn | Noted - clarification required in the description of what is being depicted in the diagram 14/03/2017 | Sector Discussion | Noted: no action required | Need more information for a way forward | 2.3.1 Access Chamber |  |  |  | 1 | [6 empty] | 1 | [15 empty] | More information required for a decision
762 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.3.3 | 38 | Fittings Attribute & Validation File Format Instructions Bel_Gmd |  |  |  | Does this mean covered by dirt and not readily accessible or below ground level? |  |  | Vol 1 |  |  |  | Noted | Below ground level 14/03/2017 | Noted: no action required | Noted: no action required | Below ground level | 2.3.3 Fitting |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
763 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 6 |  |  |  | What happens when two separate pipes are installed between access points (e.g. different material etc). Also there are examples were pipes may not have access chambers (as defined by this document). While that may be not best practice, it does occur. |  |  | Vol 1 |  |  |  | Noted | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists 14/03/2017 | Noted: no action required | Noted: no action required | In the first point two separarte pipe segments are provided and recorded. Understood that there are other access point types or structure types eg head walls and blank end. Thes are taken into account. The diagram is a general description and needs to be read in conjunction with the relevant code lists | 2.3.4 Pipe |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
764 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.3.4 | 49 | Pipe Attribute & Validation File Format Instructions Length_m |  |  |  | Is this the digital length or the real world length? |  |  | Vol 1 |  |  |  | Noted | This is the real world length as described in the QA validation field. 14/03/2017 | Included | Included | This is the real world length as described in the QA validation field. | 2.3.4 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
765 | Todd Davis | SCIRT | Wastewater | Vol 1 | 2.7.2 | 106 | 4 |  |  |  | What does this mean? What level of accuracy is defined as a discrepancy? |  |  | Vol 1 |  |  |  | George/Haydn | Clarify the wording 14/03/2017 | Included | Included | Changes made to wording to reflect tolerances used in practice ('field') | 2.7.2 Matching to Existing Infrastructure | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs | wording to reflect a sensible tolerance to discuss with Haydn | wording to reflect a sensible tolerance to discuss with Haydn | [8 empty] | Change made document updated |  |  | y | Updated comment
766 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.7 | 1 | Diagram |  |  |  | Asset Group: To be consistent with Section 1.8 Should this heading be changed to "Asset Category" ? (Or in section 1.8 change "Asset Category" to "Asset Group" |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Change to Asset Group for consistency. 7/3/2017 | Included | Included | Change to Asset Group for consistency. | 1.7 Heirarchy | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
767 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.7 | 1 | Diagram |  |  |  | Asset Type: To be consistent with Section 1.8, should this be changed to "Asset Class" |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Changed to Asset Class. 7/3/2017 | Included | Included | Changed to Asset Class. | 1.7 Heirarchy | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
768 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.8 | 1 | 1 |  |  |  | The paragraph refers to "Asset Types", yet table 1.8 does not reference "Asset Types", only "Asset Class". If these are not interchange in relation to meaning, then I suggest a explanation of "Asset Type" and "Asset Class" be documented within the document somewhere. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Changed to Asset Class. 7/3/2017 | Included | Included | Changed to Asset Class. | 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
769 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.8 | 1 | Table |  |  |  | My personal preference is to utilize "Asset Class" as standard terminology, and replace any instances of "Asset Type" within the document if they are inferring the same meaning. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Changed to Asset Class. 7/3/2017 | Included | Included | Changed to Asset Class. | 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  |  |  | change needed doc | changed where relevant | done | done | done | done | [5 empty] | Change made document updated
770 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.8 | 1 | Table |  |  |  | My personal preference is to utilize "Asset Category" as standard terminology, and replace any instances of "Asset Group" within document. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Changed to Asset Class. 7/3/2017 | Included | Included | Changed to Asset Class. | 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  |  |  | change needed doc | Asset Group retained for time being | no action | no action | no action | no action | [5 empty] | Change made document updated
771 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.8 | 2 | Table |  |  |  | Conflicts with section 2.3.4 states that a well is to be represented as a polygon |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | Changed to Polygon 7/3/2017 | Included | Included | Changed to Polygon | 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  |  |  | done |  | done | n/a | n/a | n/a | [5 empty] | Change made document updated
772 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 1.9 | 4 | Table |  |  |  | Listed here as a guide, but each definition of the asset class states the required spatial representation. ie 2.3.1 states polygon feature. Therefore for clarity, should this table also list the requirement of the standard for each asset class? |  |  | Vol 1 |  |  |  | George/Haydn | More information is needed for a way forward | Sector Discussion | Included | More information is needed for a way forward | 1.9 Data Principles | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs | change response to sector discussion | CHANGE RESPONSE TO MORE INFO NEEDED | [8 empty] | More information required for a decision
773 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Format Instructions Source |  |  |  | I am assuming this only for Geo-spatial attributes? (As there may be different sources utilized across multiple attributes.) If this is correct, can this be added for clarity in the contents column. |  |  | Vol 1 |  |  |  | George/Haydn | Source at asset component level or attribute level? 7/3/2017 | Included | Included | Defined by organisation | 2.1.10 Common Attributes | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
774 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Format Instructions H_Prec |  |  |  | If the data source changes, is there a need to keep a date history of the changes. |  |  | Vol 1 |  |  |  | Noted | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. 7/3/2017 | Noted: no action required | Noted: no action required | Data is captured as a snashot in time, if source changes over time up to agency to determine if history is recorded. | 2.1.10 Common Attributes |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
775 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Format Instructions |  |  |  | Common Attributes for your consideration: (We currently have the following 3 attributes fields across all our assets) - Manufacturer (of asset) - Supplier (of asset) - Installed By (Contractor who installed asset) Fields to be utilized to identify failing assets due to manufacturer/supplier and potential faulty installation by a contractor. |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
776 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Format Instructions Photo_Ref |  |  |  | This field should be allowed to be empty. What if there is no photographic references available. Flows through to Asset Class definitions |  |  | Vol 1 |  |  |  | Under review | consider N/A as an appropriate response. 7/3/2017 | Sector Discussion | Sector Discussion | consider N/A as an appropriate response. | 2.1.10 Common Attributes |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
777 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.2 | 17 | 1 |  |  |  | Define "Asset Classes" and "Asset Types" |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-07 | Included | Included | Asset Classifications have been defined in the Standards | 2.2 Asset Categories | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
778 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.3.2 | 32 | Embankments (Dam, Weir, Bund, Levee) Attribute & Validation File Format Instructions Crest_Lvl |  |  |  | RL: Add a definition of RL in the "Glossary of Terms and Definitions" in the document (Reduced Level) "RL" acronym used in multiple places in the document. |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | Included in Glossary 7/3/2017 | Included | Included | Included in Glossary | 2.3.2 Embankment, Glossary | 1 | [9 empty] | 1 |  |  |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
779 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.3.4 | 44 | Well Attribute & Validation File Format Instructions |  |  |  | No Type field for Wells. ie Type_Well Is this an oversight or genuinely not needed? |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.4 Well |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
780 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.3.4 | 45 | Well Attribute & Validation File Format Instructions |  |  |  | Potential Attribute: Construction method: Driven, Drilled, Dug (We do not have any Wells in our network) |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.4 Well |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
781 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.4.1 | 51 | Access Chamber Attribute & Validation File Format Instructions |  |  |  | Seem to be missing Chamber Diameter, for circular access chambers. (As it states that AC_Length and AC_width only to be used if chamber is non circular) |  |  | Vol 1 |  |  |  | Under review | Needs some rework and clarifiation. 7/3/2017 | Sector Discussion | Sector Discussion | Needs some rework and clarifiation. | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
782 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.4.3 | 64 | Fittings Attribute & Validation File Format Instructions |  |  |  | Potential Attribute: Manufacturer of Fitting |  |  | Vol 1 |  |  |  | Noted | Already identified and will be refered to TWG. 7/3/2017 | Included | Included | Already identified and will be refered to TWG. | 2.4.3 Fitting | 1 | [9 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New attribute proposed | Manufacturer
783 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.4.5 | 67 | 6 |  |  |  | Water flow direction is not absolute. I am assuming this is for a network operating under "normal" conditions. |  |  | Vol 1 |  |  |  | Noted | Correct. For a network operating under 'normal' conditions. 7/3/2017 | Included | Included | Correct. For a network operating under 'normal' conditions. | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
784 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.4.6 | 68 | 1 |  |  |  | For clarity, perhaps include a diagram showing an irregular access chamber. Refer to page 20 in Vol 1 of the waster water meta-data standard (V1.2 DRAFT A - 14 July 2016) |  |  | Vol 1 |  |  |  | Under review | Completed | Sector Discussion | Sector Discussion | Completed | 2.4.6 Pump Station |  |  | 1 | [7 empty] | 1 | [6 empty] | done | exists | exists | n/a | [5 empty] | Change made document updated
785 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.5.1 | 92 | Mechanical Equipment Attribute & Validation File Format Instructions |  |  |  | Abbreviated and Full descriptions are incorrectly matched. EG Serial_No => Protective Material This is carried through to the Waste Water and Storm Water manuals. |  |  | Vol 1 |  |  |  | Noted | Resolved in current version. 7/3/2017 | Included | Included | Resolved in current version. | 2.5.1 Equipment | 1 | [9 empty] | 1 |  |  |  |  | change needed |  | done | done | done | n/a | [5 empty] | Change made document updated
786 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.5.1 | 93 | Mechanical Equipment Attribute & Validation File Format Instructions |  |  |  | Abbreviated and Full descriptions are incorrect matched. |  |  | Vol 1 |  |  |  | Noted | Resolved in current version. 7/3/2017 | Included | Included | Resolved in current version | 2.5.1 Equipment | 1 | [9 empty] | 1 |  |  |  |  | repeat of 785 |  | repeat of 785 | repeat of 785 | repeat of 786 | n/a | [5 empty] | Change made document updated
787 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.5.3 | 109 | Valve Attribute & Validation File Format Instructions Typ_Valve |  |  |  | In our AMIS we are planning to utilize two fields to describe valves. Valve Type: Eg Isolation, Scour, Toby, Pressure Reducing, etc .. Valve Mechanism: Eg Gate, Knife, Ball, Air Release, etc.. Rather than combine function and mechanism into one attribute field. |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG refer to 630, 631 | Sector Discussion | Sector Discussion | to be discussed with the TWG refer to 630, 631 | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
788 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.7.1 | 137 | Instruments Attribute & Validation File Format Instructions |  |  |  | Where are readings recorded? Should there not be an attribute for the latest meter reading and date it was recorded. |  |  | Vol 1 |  |  |  | Noted | As Constructed' data not operational data. 7/3/2017 | Noted: no action required | Noted: no action required | As Constructed' data not operational data. | 2.7.1 Instruments |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
789 | Warren Millar | Invercargill City Council | Potable water | Vol 1 | 2.8.2 | 139 | 3 |  |  |  | Incorrect reference: Should be 1.8 |  |  | Vol 1 |  |  |  | Noted | Resolved in current version. 7/3/2017 | Included | Included | Resolved in current version. | 2.8.2 Matching to Existing Infrastructure | 1 | [9 empty] | 1 |  |  |  |  | change needed in docs |  | done | done | done | n/a | [5 empty] | Change made document updated
790 | Warren Millar | Invercargill City Council | Potable water | Vol 2 | 1.1 | 9 | Table 1 |  |  |  | Terminology Constancy: In Vol 1, Section 1.8, a lot of the elements below are referred to as "Asset Classes" They are also referred to "Asset Classes" in the attribute and validation file format. Suggest change "Categories" to "Classes" | NA | Action for volume 1. | Vol 2 |  |  | George | Noted | Changes made in updated documents. 26/3/2017 | Noted: no action required | Noted: no action required | Standards updated to a consistent approach | Table 3: Asset Hierarchy Framework |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok |  | change needed in docs |  | done | done | done | done | [5 empty] | No action |  |  |  |  | 1 | 1
791 | Warren Millar | Invercargill City Council | Potable water | Vol 2 | 3.4 | 44 | 3.2 |  |  |  | I am unsure what this means. Can there be more explanation of the content in the Rules column. | NA | No Action required. Rules explained in Section 1.3.1 | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
792 | Warren Millar | Invercargill City Council | Potable water | Vol 2 | 3.4 | 44 | 3.21 |  |  |  | What is Rule 2? Ensure on what this means. | NA | No Action required. Rules explained in Section 1.3.1 | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Rules are defined in the Metadata definition | Table 4: Metadata Definitions |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
793 | Warren Millar | Invercargill City Council | Potable water | Vol 2 | 7.2 | 65 | 7.2 |  |  |  | How are these levels recorded in the date table 7? (ie Network, facility) Table 7 only links back to an individual asset level (Unique_ID) There does seem to be merit to applying Risk to a network level, sub-network level or at a facility level? Could also apply this thinking to Criticality definition? | Granularity | Action required. Include text how to capture data at network, facility level | Vol 2 |  |  | Portfolio (Network) vs Asset (component) - an analyticasl comparator |  |  | Sector Discussion | Sector Discussion | Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance or criticality | No Specific Reference |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision |  | ? |  |  | 1 | 1
794 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | Executive Summary | v | 4 |  |  |  | All three standards use this sentence correct for all 3 waters |  |  | Vol 1 |  |  |  | Under review | Please provide further information. 7/3/2017 | Sector Discussion | Sector Discussion | Please provide further information. | Executive Summary |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
795 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.7 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | Noted | Resolved in current version. 7/3/2017 | Included | Included | Resolved in current version. | 1.7 Heirarchy | 1 | [9 empty] | 1 |  |  |  |  | change needed |  | done | done | done | n/a | [5 empty] | Change made document updated
796 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.7 | 1 | Diagram |  |  |  | Believe there should be a level between asset group and asset type (see my hierarchy tree). Also Asset Class & Asset Category is not specified in the hierarchy. |  |  | Vol 1 |  |  |  | Under review | Please provide further information relating to your hierachy. 7/3/2017 | Sector Discussion | Sector Discussion | Please provide further information relating to your hierachy. | 1.7 Heirarchy |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
797 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.8 | 1 | Table |  |  |  | Defined as Asset Type on previous page |  |  | Vol 1 |  |  |  | Noted | Resolved in current version. 7/3/2017 | Included | Included | Resolved in current version. | 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
798 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.8 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | Noted | Resolved in current version. 7/3/2017 | Included | Included | Resolved in current version. | 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  |  |  | change needed |  | done | done | done | n/a | [5 empty] | Change made document updated
799 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.8 | 2 | Table |  |  |  | What information is required to determine if a tank/reservoir is a civil structure or not. i.e. How to determine if a tank/reservoir is a containment structure or a retaining structure. |  |  | Vol 1 |  |  |  | Noted | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | Noted: no action required | Noted: no action required | based on the hierachy developed by the TWG, tank and reservoirs is a Containment Structures | 1.8 Theme Structure |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
800 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.8.1 | 3 | 1 |  |  |  | Will there be reference documents for treatment plant assets? |  |  | Vol 1 |  |  |  | George/Haydn | Not at this point in time | Noted: no action required | Noted: no action required | Not at this point in time | 1.8.1 Other Asset Classes in the precinct of a Water Network |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
801 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 1.9 | 4 | Table |  |  |  | How would an asset that could be represented as more than one of these be represented. e.g. would a scour be a single asset (pipe) or two (pipe and fitting) or would that be up to the Client to determine |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-07 | Sector Discussion | Included | More information is required to inform a way forward | 1.9 Data Principles |  |  | 1 | [5 empty] | 1 |  |  |  |  | what is to be included? | updated comment | further information needed | two assets 1=scour 2=pipe | [9 empty] | More information required for a decision
802 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.1 | 7 | 1 |  |  |  | water |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed to Water. 7/3/2017 | Included | Included | changed to Water. | 2.1.1 Accuracy Requirements for Locating Assets | 1 | [9 empty] | 1 |  |  |  |  | change needed |  | done | n/a | done | n/a | [5 empty] | Change made document updated
803 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.3 | 8 | 13 |  |  |  | water code lists |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Section under review. 7/3/2017 | Included | Included | Section under review. | 2.1.5 Attribute Data Fields | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | codelists added | codelists added | codelists added | n/a | [5 empty] | Change made document updated
804 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.4 | 9 | Table Boolean |  |  |  | Definition etc missing |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Section under review. 7/3/2017 | Included | Included | Section under review. | 2.1.6 Attribute Data Type Definitions | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
805 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.5 | 10 | Table Attribute Name |  |  |  | ESRI is a propitiatory product. Is the intention here to 'force' councils/contractors to use an ESRI based product, or something else? if not suggest removing ESRI from this sentence. |  |  | Vol 1 |  |  |  | Noted | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for. 7/3/2017 | Noted: no action required | Noted: no action required | Intention is not to force a move to ESRI but rather for the accommoation of a limitation in ESRI format requirements and to meet these as a minimum so all systems are catered for | 2.1.7 Metadata Definitions |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
806 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.5 | 10 | Table Data Type |  |  |  | Section 2.1.4 |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Section under review. 7/3/2017 | Included | Included | Section under review. | 2.1.7 Metadata Definitions | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
807 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Format Instructions Net_Type |  |  |  | Does this code list include options for multiple networks? or is each network to be recorded as an individual project? |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-07 | Included | Included | ProjectID already included Yes it does - added multiples in Project Table | 2.1.9 Project Attributes | 1 | [7 empty] | 1 |  |  |  | 1 | what is to be included? | Already have projectID update your comment | change needed | table modified to include multiple networks+AN900 | TABLE MODIFIED | TABLE MODIFIED | TABLE MODIFIED | n/a |  |  |  |  | discuss with haydn changed response | Changes made documents updated |  |  | y | Updated comment
808 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Format Instructions Design_Co |  |  |  | Some companies include a number in their name. Alpha/Numeric instead? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Should be A/N. 7/3/2017 | Included | Included | Should be A/N. | 2.1.9 Project Attributes | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Changes made documents updated
809 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Format Instructions Const_Co |  |  |  | See note regarding Design Company above. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Should be A/N. 7/3/2017 | Included | Included | Should be A/N. | 2.1.9 Project Attributes | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Changes made documents updated
810 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Formation Instructions Source |  |  |  | Should this not be a code list? |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | what specifically? |  |  | n/a |  |  |  |  | request documented | More information required for a decision
811 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Formation Instructions Cost |  |  |  | What is the definition of cost for contractors? What is the value of capturing this when there are no controls around application of defining cost? |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-07 | Included | Included | Reviewed and Noted for Inclusion Financial code lists for ODRC, ORC and OC are included | 2.1.10 Common Attributes | 1 | [7 empty] | 1 |  |  |  |  | what is to be included? | updated comment | [11 empty] | haydn
812 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Formation Instructions Photo_Ref |  |  |  | What exactly are the photographic references? This appears to be a 250 Char field so completely useless for using this data. Is this intended to be used in a similar way to 'Unique ID' as a reference number for the photo? |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | could be used a reference to another source for the photo? | [7 empty] | request documented | More information required for a decision
813 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Formation Instructions Hltn_Safety |  |  |  | Again using a 250 character field means the data could be all over the place. Example uses this field to record specific instructions to access the asset. To me that should be a separately labelled field. |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.1.10 Common Attributes |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | what specifically? | [7 empty] | request documented | More information required for a decision
814 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.2.1 | 19 | Area of Work Extent & Project Attribute & Validation File Formation Instructions Design_Co |  |  |  | See note regarding this field on page 13 |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Should be A/N. 7/3/2017 | Included | Included | Should be A/N. | 2.2.1 Area of Work Extent | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
815 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.2.1 | 19 | Area of Work Extent & Project Attribute & Validation File Formation Instructions Const_Co |  |  |  | See not for Design Company on page 13 |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Should be A/N. 7/3/2017 | Included | Included | Should be A/N. | 2.2.1 Area of Work Extent | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
816 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.4.4 | 65 | Figure 18 |  |  |  | Would a T not be a fitting instead of a node? |  |  | Vol 1 |  |  |  | Noted | T is a fitting but also an intersection so therefore a node. 7/3/2017 | Noted: no action required | Noted: no action required | T is a fitting but also an intersection so therefore a node. | 2.4.4 Node |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
817 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.4.5 | 67 | 5 |  |  |  | Is there a particular reason that Valves etc do not 'break' pipes? When works are undertaken (renewals in particular) actual physical assets provide useful 'real world' demarcation points. |  |  | Vol 1 |  |  |  | Noted | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | Noted: no action required | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | 2.4.5 Pipe |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
818 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.4.6 | 69 | Figure 21 |  |  |  | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets |  |  | Vol 1 |  |  |  | Under review | is that the property boundary? 9/3/2017 | Sector Discussion | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 | [15 empty] | Modify Diagram
819 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.4.6 | 69 | Figure 22 |  |  |  | These should be clearly labelled as examples only. Not all TLAs may use the boundary as the demarcation point between public and private assets |  |  | Vol 1 |  |  |  | Under review | is that the property boundary? 9/3/2017 | Sector Discussion | Sector Discussion | is that the property boundary? 9/3/2017 | 2.4.4 Node & 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 | [15 empty] | Modify Diagram
820 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.4.6 | 74 | Pipe Attribute & Validation File Format Instructions Nom_Bore |  |  |  | What are the reasons for Internal Diameter, Nominal Diameter and Nominal Bore all being required? Are these all not essentially the same thing? |  |  | Vol 1 |  |  |  | George/Haydn | Not the same, they depict measurements from different types of pipes. Should we determine the relevent measurements according to the type of pipe? Eg pressure pipe vs gravity pipe. 9/3/2017 | Sector Discussion | Sector Discussion | The range of diameter types are an analytical requirement for interogating assets through a range of lenses | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
821 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.4.8 | 82 | 1 |  |  |  | Would this class also cover assets that provide access but are not part of a dam or weir wall? Suggest that this be added to the wastewater specification as well. |  |  | Vol 1 |  |  |  | Noted | Agreed 9/3/2017 | Included | Included | Agreed 9/3/2017 | 2.3.6 Tunnel | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | n/a | n/a | [5 empty] | Comment clarifed in potable water document and tunnel asset class added to wastewater document
822 | Waste and Water Services | Dunedin City Council | Potable water | Vol 1 | 2.6.1 | 116 | Cabling Attribute & Validation File Format Instructions Vendor |  |  |  | Should purchase date be included? Do some warranties apply from date of purchase? |  |  | Vol 1 |  |  |  | Under review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.6.1 Cabling |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | more information needed about which assets | [8 empty] | request documented | More information required for a decision
823 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.1 | 9 | 1 |  |  |  | a' instead of 'the' | QA | Action required: editor. | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [9 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
824 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.1 | 9 | 3 |  |  |  | Why is infrastructure for collection and treatment not covered? These assets are integral to potable water supply and asset managers need quality information that they can use to make asset management decisions. Sentence also contradicts itself. "does not cover infrastructure...treatment of water, except in the case of..infrastructure to treat water". | Coverage | No action required. These assets to be covered in subsequent standards. Out of scope. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | There is a desire to create anoter standard which includes these assets, as there is in th ebuilding environment for Large Commercial Buildings and Industrial Buildings | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
825 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.2 | 10 | Table 2 Quantity |  |  |  | Pressure is more of a Quality provision. Suggest moving this into Quality. | Service Performance | No Action required. Pressure can be included at either location | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Pressure is a Design Attribute How it performs against that design is a Design Performance attribute | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
826 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.2 | 11 | Table 2 Financial |  |  |  | Delete extra "that" | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [9 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
827 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.3.1 | 12 | 1 |  |  |  | outlines' | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [9 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
828 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.5 | 23 | 5 |  |  |  | investment' | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [9 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
829 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.8 | 29 | 2 |  |  |  | replace' | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
830 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.8 | 29 | 3 |  |  |  | Influences | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
831 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.8 | 29 | 4 |  |  |  | Replication | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
832 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 1.8 | 30 | 1 |  |  |  | General comment - risk and criticality are closely linked. Are they really different things? Just use one term and get rid of the other. | Risk | No action required. Decision to separate two schemas taken at project management level | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. Decision to separate two schemas taken at project management level | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
833 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 2.4 | 33 | Data table 2 |  |  |  | Table is missing a 'comments' field | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
834 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 2.5 | 36 | Code list 2 |  |  |  | Inconsistent with the wastewater and stormwater measure headings (Rating). Suggest same terminology is used across all three waters. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
835 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 2.5 | 36 | Code list 2 2 |  |  |  | Switch could and would. "could" more appropriate for grade 2, "would more appropriate for grade 3. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
836 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 2.5 | 36 | Code list 2 3 |  |  |  | Switch could and would. "could" more appropriate for grade 2, "would" more appropriate for grade 3. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
837 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 2.5 | 36 | Code list 4 PIPMAN |  |  |  | Is this a different manual than the 3rd Edition New Zealand Pipe Inspection Manual? If not use full document name as used in the wastewater and stormwater documents. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
838 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 3.4 | 40 | 3 |  |  |  | Should this not be in line with the wastewater and stormwater measures? (IIMM 2015) | QA | No action required. This is the same document | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. This is the same document | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
839 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 3.4 | 44 | Data table 3 3.23 - 3.24 |  |  |  | If this information is to be completed by field (maintenance and operations) staff they are unlikely to know if works have been deferred or will be deferred. | Financial Performance | No action required. Will be captured by asset manager. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Not an attribute of these standards | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
840 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 3.4 | 46 | Data table 3 3.31 |  |  |  | Replace "data" with "cost" | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | Haydn | 1 | [9 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
841 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 3.5 | 48 | Code list 15 |  |  |  | Stormwater document includes complete code lists for these items. Water and wastewater do not. | QA | Statement noted. To discuss whether code lists required for stormwater and wastewater. Action on Opus. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Code lists updated | List of Code Lists |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
842 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 4 | 50 | 1 |  |  |  | Not convinced that this is a useful or practical schema, at least for potable water assets. Perhaps don't bother with this and just use demand schema instead? They are similar. | Utilisation | Statement noted. Utilisation refers to demand compared to capacity, and can refer to current, potential or forecast. Action: Note to be added in 3 water schema's. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Utilisation and Demand are different decision elements as explained in the standards. | 3.2 Utilisation Schema 3.3 Demand Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
843 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 4.1 | 50 | 2 |  |  |  | Missing sentence from WW and SW Volume two further explaining the utilisation schema. " Utilisation is measured using time or other base unit measured against a known availability." | QA | Action required. Make edits. | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
844 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 4.2 | 50 | 6 |  |  |  | "Current Utilisation" at an asset by asset level would require an impractical amount of monitoring. i.e. are we really going to know average and peak flows through each and every length of water pipe? | Utilisation | Action required. Include text to make clear that councils can capture data at level allowable by their capabilities. Council's can decide which assets to collect this information for. Change mandatory code | Vol 2 |  |  | noted |  |  | Included | Included | This is an analytical construct, and easily monitored in an analytical sense at whatever frequency required for intervention circumstances | 3.2 Utilisation Schema | 1 | [7 empty] | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
845 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 4.2 | 50 | 7 |  |  |  | Partly a function of the pressure in the pipe. Are we really going to know potential utilisation for each and every length of water pipe? | Utilisation | Action required. Include text to make clear that councils can capture data at level allowable by their capabilities. Council's can decide which assets to collect this information for. Change mandatory code | Vol 2 |  |  | noted |  |  | Included | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
846 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 4.4 | 52 | Data Table 4 4.04 - 4.05 - 4.06 - 4.07 |  |  |  | Don't think it's possible to determine this for each and every asset. At least for potable water assets. | Granularity | Action required. Include text to make clear that councils can capture data at level allowable by their capabilities. Council's can decide which assets to collect this information for. Change mandatory code | Vol 2 |  |  | noted |  |  | Included | Included | Yes, this is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
847 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 5.2 | 55 | 6 |  |  |  | Difficult to determine on an asset by asset basis for water assets without extensive modelling. Alternatively would require data from modelling software. | Granularity | Action: Make clear that Council can decide what level of granularity to collect at | Vol 2 |  |  | noted |  |  | Included | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
848 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 5.2 | 55 | 7 |  |  |  | Difficult to determine on an asset by asset basis for water assets | Granularity | Action: Make clear that Council can decide what level of granularity to collect at | Vol 2 |  |  | noted |  |  | Included | Included | This is an analytical construct, and easily determined in an analytical sense at any point on the pipe and the connections on that pipe | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
849 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 5.5 | 58 | Code list 25 |  |  |  | This does not seem to be an relevant measure for water demand in a metropolitan situation. | QA | Action required. Change - Opus to make edits. | Vol 2 |  |  | noted |  |  | Included | Included | Completed - see Demand section | 3.3 Demand Schema | 1 | [7 empty] | 1 | [7 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
850 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 6.5 | 63 | 1 |  |  |  | Criticality varies across all three waters. While a data centre may have a higher water criticality than a hospital, the opposite would be true of wastewater. | Criticality | Action required. Remove reference to data centre. | Vol 2 |  |  | noted |  |  | Included | Included | Correct, which is why each asst class is treated differently when an analysis of things like criticality are conducted across a network | No Specific Reference | 1 | [9 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
851 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 7 | 65 | 1 |  |  |  | Of risk & criticality, which are both similar schema, criticality is much quicker and easier to measure and much less subjective. I would be tempted to exclude risk or use it with caution in decision-making compared the use of other schema. | Risk | No action required. Management schemas to be treated as "silos". | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | It will be required n some circumstances, and here it is defined when you do | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
852 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 7.5 | 69 | Data Table 7 7.08 - 7.09 |  |  |  | Ln only needs to be 1 due to 1,5 rule | QA | Action required. Change - edits to be made. | Vol 2 |  |  | noted |  |  | Included | Included | Completed | No Specific Reference | 1 | [9 empty] | 1 | [5 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
853 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 7.7 | 74 | Code List 32 2 |  |  |  | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated? | Risk | No action required. Given the full range of consequences from negligible to catastrophic, the scales are appropriately graded. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 | [6 empty] | 1 | [15 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  |  |  | 1 | 1
854 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 7.7 | 75 | Code List 32 3 |  |  |  | Even at a score of 3 this is a pretty major event. Are the scales correctly graduated? | Risk | No action required. Given the full range of consequences from negligible to catastrophic, the scales are appropriately graded. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 | [6 empty] | 1 | [15 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  |  |  | 1 | 1
855 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 7.7 | 75 | Code List 32 3 |  |  |  | Even at a score of 3 is a pretty major event. Are the scales correctly graduated? | Risk | No action required. Given the full range of consequences from negligible to catastrophic, the scales are appropriately graded. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 | [5 empty] | 1 | [16 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  |  |  | 1 | 1
856 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 7.7 | 76 | Code List 32 4 |  |  |  | Even at a score of 4 this is a pretty major event. Are the scales correctly graduated? | Risk | No action required. . Given the full range of consequences from negligible to catastrophic, the scales are appropriately graded. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 | [5 empty] | 1 | [16 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  |  |  | 1 | 1
857 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 10.4 | 90 | Data Table 10 |  |  |  | Not convinced there is much use in this table, at least for water assets. Most revenue is derived from consumption so would be associated with a meter and the usage of water. | Financial Performance | No action required. Organisation can choose how revenue is recorded against an asset | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. Organisation can choose how revenue is recorded against an asset | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 1 | 1
858 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 10.4 | 90 | Data Table 10 10.2 |  |  |  | So this is theoretical revenue? Not actual revenue? | Financial Performance | Action required. Change wording to make clear attribute refers to actual revenue. | Vol 2 |  |  | noted |  |  | Included | Included | Actual, Forecast and Budget included in financial code lists | Code List 6: Bases of Cost | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
859 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 10.4 | 96 | Data Table 10 10.35 |  |  |  | Delete this text. Captured in the field below. | QA | Action required. Change - edits to be made. | Vol 2 |  |  | noted |  |  | Included | Included | Completd | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
860 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11 | 100 | 1 |  |  |  | This whole section is confusing. It's trying to do two things at once. Individual asset attributes and whole of network attributes should be separated out. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
861 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 100 | 2 |  |  |  | So its not intended to be used for decisions at an individual asset level? If not, strip out all the individual asset measures and move somewhere else. | Service Performance | Statement noted. Schema is for use by asset managers. | Vol 2 |  |  | noted |  |  | Included | Included | It is in some circumstances to be used on an individual assetID | No Specific Reference | 1 | [8 empty] | 1 | [16 empty] | No action |  |  |  |  | 1 | 1
862 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 101 | Data Table 11 |  |  |  | This table seems to be a jumble of attributes for individual assets and DIA measures which are taken for the network / organisation as a whole. I'm not really sure the whole of network / organisation attributes are metadata. Delete DIA whole of network / organisation attributes or move to a separate table. dlane: Some data items are network wide while others are asset specific. If data capture is required these should be split into separate network and asset tables. | Service Performance | Action required : Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Volume 2 is completed in these draft standards. Network analytical tools are available to consolidate asset data at a network level to define network circumstances e.g. performance | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | This is not a data question, it is a data collection question. We define the attributes for components and consolidate for an asset, we doint define general codes for | 1 | 1
863 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 101 | Data Table 11 11.03 |  |  |  | How does this field work? Is it the duration of the most recent unplanned interruption, the the total duration of all unplanned interruptions (from field below) or the average unplanned interruption duration? | Service Performance | Action required. The unplanned duration of each interruption should be recorded. Make this clearer | Vol 2 |  |  | noted |  |  | Included | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
864 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 101 | Data Table 11 11.05 |  |  |  | How does this field work? Is it the connections affected in the most recent unplanned interruption, the total connections affected in all unplanned interruptions (from field below) or the average number of connections affected in unplanned an unplanned interruption? | Service Performance | Action required. The unplanned duration of each interruption should be recorded. Make this clearer | Vol 2 |  |  | noted |  |  | Included | Included | Analytics are completed based on problem being solved. It is possible to answer both of these questions from the code lists in Vol 2 | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
865 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 102 | Data Table 11 11.06 |  |  |  | Delete this field. It makes no sense and is confusing. Field Ref 11.04 does the job. | Service Performance | Action required. Remove attribute | Vol 2 |  |  | noted |  |  | Included | Noted: no action required | Table updated | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
866 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 102 | Data Table 11 11.07 |  |  |  | Need to include the units of measure. kPa,psi etc | Service Performance | Action required. Appears to be repetition on data. Remove reference to Repairs and maintenance schema | Vol 2 |  |  | noted |  |  | Included | Included | Tables updated in code lists of Vol 2 | Code List 44: Description of Design Performance – Engineering Unit of Measure | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | psi to be added |  |  | y | Updated comment | 1 | 1
867 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 102 | Data Table 11 11.09 |  |  |  | Surely this field would only be used for a reservoir asset. Not, say, a pipe supplied from the reservoir. Please clarify the use of this field. | Service Performance | Action required. Make clear that for reservoirs only | Vol 2 |  |  | noted |  |  | Included | Included | It can be both | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 1 | 1
868 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 103 | Data Table 11 11.10 |  |  |  | Not sure it would come from Repairs and Maintenance Schema. | Service Performance | This MoH grading measure was put forward for inclusion by workshop participants. WSL includes this measure but only for treatment. We noted it as optional | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | This MoH included in the Service Performance Attributes | Data Table 11: Service Performance Attributes – Functional |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 1 | 1
869 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 103 | Data Table 11 11.11 |  |  |  | Confusing to have it on this table. So this field is used at a facility level not an individual asset level? | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
870 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 103 | Data Table 11 11.12 |  |  |  | Confusing to have it in this table. So this field is used at an organisation level? The question of whether there is an adequate backflow prevention programme doesn't relate to individual assets? | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
871 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 104 | Data Table 11 11.13 |  |  |  | Whole of network / organisation measure, not an individual asset measure | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
872 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 104 | Data Table 11 11.14 |  |  |  | Whole of network / organisation measure, not an individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
873 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 104 | Data Table 11 11.15 |  |  |  | Whole of network / organisation measure, not an individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
874 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 104 | Data Table 11 11.16 |  |  |  | Whole of network / organisation measure, not an individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
875 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 104 | Data Table 11 11.17 |  |  |  | Whole of network / organisation measure, not an individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
876 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 105 | Data Table 11 11.18 |  |  |  | This is not a demand attribute, its abstraction/take and is source based. as you've said that this is potable water assets only I don't think it's appropriate here. | Service Performance | Statement noted. No action. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | A source is an asset (e.g. a reservoir), abstraction is the process, demand is the level of abstratcion on the asset - each are different and can apply to a pipe connection no less (e.g. a school) | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 1 | 1
877 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 105 | Data Table 11 11.19 |  |  |  | Whole of network / organisation measure, not and individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
878 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 105 | Data Table 11 11.20 |  |  |  | Whole of network / organisation measure, not an individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1 | 1
879 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 105 | Data Table 11 11.21 |  |  |  | Even at a score of 2 this is a pretty major event. Are the scales correctly graduated?. | Service Performance | No action required. Given the full range of consequences from negligible to catastrophic, the scales are appropriately graded. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Two types of code lists now apply for analytical interrogation | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating | No action |  |  | 1 | [5 empty] | 1 | [16 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  |  |  | 1
880 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 106 | Data Table 11 11.22 |  |  |  | Whole of network / organisation measure, not an individual asset measure. Move to financial schema? | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1
881 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.3 | 106 | Data Table 11 11.23 |  |  |  | Whole of network / organisation measure, not and individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1
882 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.7 | 107 | 1 |  |  |  | Differs from tables in the stormwater and wastewater specs. Most/all of these measures should be applicable across all three waters. | Service Performance | The differences between the three waters are due to the workshop participants describing each water slightly differently. We developed the service performance tables based on these workshop descriptions. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Tables are very similar, with the asset specific elements being applied when required. Tables have been normalised where possible | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 1
883 | Waste and Water Services | Dunedin City Council | Potable water | Vol 2 | 11.7 | 108 | Table 15 Reliable |  |  |  | Whole of network / organisation measure, not an individual asset measure. | Service Performance | Action required: Make clear what level data is collected | Vol 2 |  |  | noted |  |  | Included | Included | Network analytics are completed on individual asset analytical interogations - attributes hold the information required to do this | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Updated comment | 1
884 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 1.6 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | resolved in updated version 14/03/2017 | Included | Included | resolved in updated version | General | 1 | [8 empty] | 1 | [5 empty] | check done |  | n/a | n/a | done | n/a | [5 empty] | Change made document updated
885 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | resolved in updated version 14/03/2017 | Included | Included | resolved in updated version | 1.7 Heirarchy | 1 | [8 empty] | 1 | [5 empty] | check done |  | n/a | n/a | done | n/a | [5 empty] | Change made document updated
886 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | resolved in updated version 14/03/2017 | Included | Included | resolved in updated version | 1.7 Heirarchy | 1 | [8 empty] | 1 | [5 empty] | check done |  | n/a | n/a | done | n/a | [5 empty] | Change made document updated
887 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 2.1.5 | 10 | Attribute Name |  |  |  | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 2.1.7 Metadata Definitions | 1 | [8 empty] | 1 | [5 empty] | check done | change needed docs | done | done | done | done | [5 empty] | Change made document updated
888 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 2.1.5 | 10 | Data Type |  |  |  | 2.1.4 |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 2.1.6 Attribute Data Types Definitions 2.1.7 Metadata Definitions | 1 | [8 empty] | 1 | [5 empty] | check done | change needed docs | done | done | done | done | [5 empty] | Change made document updated
889 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Formation Instructions Net_Type |  |  |  | Does this code list include options for multiple networks? Or is each network to be recorded as an individual project? |  |  | Vol 1 | Either |  |  | Haydn | 2017-03-14 | Noted: no action required | Noted: no action required | Either | 2.1.9 Project Attributes |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
890 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Formation Instructions Design_Co |  |  |  | Some companies include a number in their name. Alpha/Numeric instead? |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | 1 | [8 empty] | 1 | [5 empty] | check done | change needed docs | done | done | done | done | [5 empty] | Change made document updated
891 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Formation Instructions Const_Co |  |  |  | See note regarding Design Company above. |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 2.1.9 Project Attributes | 1 | [8 empty] | 1 | [5 empty] | check done | change needed docs | done | done | done | done | [5 empty] | Change made document updated
892 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Formation Instructions Source |  |  |  | Should this not be a code list? |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | More information is needed for a way forward | 2.1.10 Common Attributes | 1 | [8 empty] | 1 | [5 empty] | check done | need to review what is being asked possible request for more information | [8 empty] | no action needed other than monitor other relevant entries | More information required for a decision
893 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 2 | 5.1 | 60 | 1 |  |  |  | Heading (see water and wastewater) | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [8 empty] | 1 | [16 empty] | No action |  |  |  |  | 1 | 1
894 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 2 | 9.5 | 89 | Data Table 9 9.09 |  |  |  | Length will not allow for KPa or l/s to be used. Either this should be extended or at code should be a single character as per the water measures. Should be consistent across all 3 waters | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Conistent across all standards, documents have undergone a full publishing edit | No Specific Reference | 1 | [8 empty] | 1 | [16 empty] | No action |  |  |  |  | 1 | 1
895 | Waste and Water Services | Dunedin City Council | Stormwater | Vol 2 | 11.7 | 113 | 1 |  |  |  | Differs from table in wastewater and water specs. Most/all of these measures should be applicable across all three waters. | Service Performance | Statement noted | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Conistent across all standards, documents have undergone a full publishing edit | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 1
896 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 1.6 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | Noted | resolved in updated version 14/03/2017 | Included | Included | resolved in updated version | General | 1 | [8 empty] | 1 | [16 empty] | Change made document updated
897 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | Noted | resolved in updated version 14/03/2017 | Included | Included | resolved in updated version | 1.7 Heirarchy | 1 | [7 empty] | 1 | [17 empty] | Change made document updated
898 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 1.8 | 1 | 1 |  |  |  | Page numbering out of sequence |  |  | Vol 1 |  |  |  | Noted | resolved in updated version 14/03/2017 | Included | Included | resolved in updated version | 1.8 Theme Structure | 1 | [7 empty] | 1 | [17 empty] | Change made document updated
899 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 2.1.5 | 10 | Attribute Name |  |  |  | ESRI is a propitiatory product. Is the intention here to 'force' councils to use an ESRI based product or something else? If not suggest removing this sentence |  |  | Vol 1 |  |  |  | Noted | Not the intention. The intention is to outline why the field is structured in this way 14/03/2017 | Noted: no action required | Noted: no action required | Not the intention. The intention is to outline why the field is structured in this way | 2.1.7 Metadata Definitions |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
900 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 2.1.5 | 10 | Data Type |  |  |  | 2.1.4 |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | Included | Included | Change "Please refer to Section 2.1.5 Data Type Definition." TO "Please refer to Section 2.1.4 Data Type Definition." 14/3/2017 | 2.1.7 Metadata Definitions | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
901 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Formation Instructions Net_Type |  |  |  | Doe this code list include options for multiple networks? Or is each network to be recorded as an individual project? |  |  | Vol 1 |  |  |  | George/Haydn | Good point 14/03/2017 | Sector Discussion | Sector Discussion | This is an operational question related to an organisations ability to import data into their asset management systems. For immature organisations likely to be project by project, for mature ones project agnostics | 2.1.9 Project Attributes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  | Project table changed to include multiple networks as part of one job we need to discuss further | done | done | done | n/a | [5 empty] | More information required for a decision |  |  | y | Not sure what's to discuss? It's systems dependant… If you have single systems, bring in project by project (roads vs waters). And if you have one system bring in all projects at once…. (3-waters)
902 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Formation Instructions Design_Co |  |  |  | Some companies include a number in their name. Alpha/Numeric instead? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Change as suggested Alpha to Alpha/Numeric 14/3/2017 | Included | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
903 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 2.1.7 | 13 | Project Attribute & Validation File Formation Instructions Const_Co |  |  |  | See note regarding Design Company above. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Change as suggested Alpha to Alpha/Numeric 14/3/2017 | Included | Included | Change as suggested Alpha to Alpha/Numeric | 2.1.9 Project Attributes | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
904 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Formation Instructions Source |  |  |  | Should this not be a code list? |  |  | Vol 1 |  |  |  | George/Haydn | Suggest we accept the suggestion 14/03/2017 | Included | Included | More information is needed for a way forward | 2.1.10 Common Attributes | 1 | [7 empty] | 1 |  |  |  |  | ok |  | make mention of change request | [9 empty] | request documented | More information required for a decision
905 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 2 | 4.5 | 56 | Code list 25 STORAGE |  |  |  | Not a valid measure for wastewater utilisation. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Updated | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
906 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 2 | 6.5 | 66 | 1 |  |  |  | Criticality varies across all three waters. for example, for wastewater a hospital would have a higher value than a data centre. while water could score differently | Criticality | No action required, based on the importance of the building as defined in the Buildings standard | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required, based on the importance of the building as defined in the Buildings standard | Code List 13: Facility Importance Rating |  |  |  | 1 |  |  |  |  | 1 | [22 empty] | 1
907 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 2 | 6.5 | 66 | Code List 29 |  |  |  | Heading is different from that used in water and stormwater documents. Suggest standardising for simplicity. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
908 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 2 | 9.5 | 87 | Data Table 9 9.09 |  |  |  | Length will not allow for KPa or l/s to be used. Either this should be extended or code should be a single character as per the water measures. should be consistent across all 3 waters. | QA | Action required - make edits | Vol 2 |  |  | noted |  |  | Included | Included | Documents have undergone a full publishing edit | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
909 | Waste and Water Services | Dunedin City Council | Wastewater | Vol 2 | 11.7 | 112 | 1 |  |  |  | Differs from tables in the stormwater and wastewater spec. Most/all of these measures should be applicable across all three waters. | Service Performance | Statement noted | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Conistent across all standards, documents have undergone a full publishing edit | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
910 | John Twentyman | Citycare | 3-Waters & Buildings | Vol 1 & Vol 2 | Executive Summary | [5 empty] | An obvious mistake in the Potable Water Metadata Std is that someone has put the Residential Executive Summary in it????. | QA | Action required - make edits. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  | This was not a mistake, but unfortunately a typo which we didn’t pick up before release of this first draft of Vol 2 Potable Water standard. The executive summary as it currently reads, was taken directly from the As- Constructed standard and is fairly generic across all 8 standards (Vol 1 & 2 for Buildings and 3Waters), but did have specific references to the assets that it covers later in the summary (in this case utilities/potable water networks). We have picked this up for the WW and SW standards to be issued this week and will correct in the next draft of the Potable Water standard, when we will also better tailor the Executive Summary to reflect the standard that it refers to. | Included | Included | Included in the draft Standards | Executive Summary | 1 | [7 empty] | 1 | [6 empty] | change needed | discuss with haydn for haydn to resolve | done | haydn to do | haydn to do | n/a | [5 empty] | Change made document updated |  |  | y | ?? The references have been updated in the editing rounds
911 | Samuel Cech | Tatras Consulting | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | You are asking for public to comment on missing attributes within meta data tables. Considering you have spent 12500 hours on this, could you please comment if all the attributes defined by Australian standard ADAC have been included? http://engicom.com.au/adac/government-organisations I appreciate your list of assets may be more comprehensive. If any of the asset attributes defined in ADAC are missing there are like to be areas where assets will miss vital information for future analysis. If you have used IPWEA in your decision making process it would be useful to include this information on your website so it doesn’t look like you are reinventing the wheel. Well done on sorting out the asset management data through the lifecycle of each asset. Local councils desperately need national standard for asset capture, storage and access to information. | NA | Statement noted. Action on volume 1. | Vol 1 - Vol 2 |  | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. |  |  |  | Included | Included | All asset attributes that are found within ADAC are included within these standards, and considerably more. ADAC does not have a standard for Buildings. ADAC does not have standards for Asset Management decision-making elements (Vol 2) for data analysis for asset management investment decision-making purposes. | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
912 | Duane Wilkins | LINZ | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | I’d like to provide feedback on the proposed standard. However I caveat this as coming from a hands on GIS Practitioner View, which may be different to my colleagues here at LINZ. I think it will be incredibly important to incorporate good practice guidance at some stage on how these standards are practically implemented. Ideally providing an empty or working dataset that a person can take, open with their system and populate. Generally when you go to create the schema in a system you’ll follow it and interpret changing the types, field lengths, column names etc. My request is based on recent experience. Often this step is left out, and implementation of the standard fails. This was my experience with the ANZLIC geospatial metadata standard, 10 years after its release 95% of GIS practitioners in New Zealand could still not easily implement the standard within the most common desktop GIS software. The Australian based tool provided did not support NZ requirements. We ended up shoving the required text into a single desc field in an inappropriate manner, ending up with a total mess. This may require getting software providers onboard with adding these into their pre-defined templates for users of the most common software providers. If you could imagine in the same way we create a LINZ letterhead letter in MS Word. My 2 cents from a GIS data capture perspective and I am happy to discuss this further if appropriate, otherwise happy to leave it as this. | Data | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. LINZ are talking with software providers to provide predefined templates as indicated. | N/A |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
913 | Erik Swart | New Plymouth District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | In each of these documents out for proposal, there is reference to standard codes for things like asset type and material (“the CODELIST”), but none of these are available yet – will this be available before consultation closes? | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Have the code lists been distributed? 26/3/2017 | Included | Included | Code lists are included Attributes to be discussed | General | 1 | [7 empty] | 1 |  |  |  | 1 | ok |  | change needed in docs |  | codelists added | codelists added | codelists added | codelist added | [5 empty] | Gauge input from next review |  | N/A
914 | Stuart Hamilton | Aurecon | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | This is a great initiative and will aid everybody involved in the area of Asset Management. I would ask is has there been any coordination with the Institute of Public Works Engineering Australasia as they have a system already in place called ADAC (http://www.engicom.com.au/adac). Could your framework be an extension to that so we can leverage what software companies have developed already to support that schema. It appears that a lot of the info you are capturing has already been covered, why reinvent the wheel? | Other standards | Statement noted. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Noted: no action required | Noted: no action required | IPEWA Australisia has representation around the table, and has had for 2 years | N/A |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
915 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Structure of the standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes. Further to the split of water sectors there is an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group has specified that a single document that focusses on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. In terms of usability our end users are expecting a data framework that is easy to understand and use. In the proposed layout we are expecting the standards will be met with cost burdens. | Volume Interaction | Statement noted. See HR comment. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. |  |  |  | Noted: no action required | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
916 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | 2. Applicability of volumes 1 and 2 The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was about creating an as-built data set for industry that can be used to collect field data, most of the workshops evolved around this input. Volume 2 for derived data has had limited industry input and we do not believe it is ready to be published. Further work on this volume is therefore required. | Volume Interaction | Data scientist. Action on volume 1 and 2. The outcome of the volume 2 document is a direct translation of the workshops. | Vol 1 - Vol 2 |  | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. |  |  |  | Noted: no action required | Noted: no action required | The functionality and derivative attributes requires interoperability primary keys between disparate data sets (for example as constructed data sets and condition data sets). The structure of this standard allows for the interoperability analytics that evidence-based investment decisions require. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
917 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | 3. Data hierarchy The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. As presented at the workshops, an example of how this could be applied to the tables is outlined below: Level 0 (system/layout specific data – master data. Typically assigned by organisational systems and numbering or coding rules - contains the common data set) -Inventory identification number / -Functional location i.e. Network type (water, wastewater, stormwater) / -etc. Level 1: Data categories, in example: “Technical/physical” i.e. Containment structures (available technical core classes) (or) Operational data (or) Financial data etc. Level 2: (attributes) Minimum required attributes, in example: -Function / -Depth / -Material / -etc. Level 3: (attributes) Conditional attributes, in example: -Diameter if circular / -length and width if not circular / -Joint type (if the structure has joints) / -etc. Level 4: (attributes) Optional attributes, in example: -Manufacturer / -Model/part number / -etc. | NA | Action on volume 1. Refer to HR comments. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards Tables are to be discussed at length | No Specific Reference | 1 | [7 empty] | 1 |  |  |  | 1 | ok |  | review against standard | discuss with haydn | [8 empty] | discuss with haydn | Sector discussion |  | N/A | y | happy to…. :) | 2
918 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | 4. Terminologies and definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need to be agreed. | NA | Agreed, refer comments HR. Action on volume 1. | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards |  |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
919 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | 5. Graphical representation and its accuracy This subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. Graphical representation should be removed from the document; the purpose of this standard is collecting metadata of asset physical properties. Geospatial requirements are a standard in its own right and even providing these as guidelines does not seem appropriate. | NA | Refer comments HR. Action on volume 1. | Vol 1 - Vol 2 |  | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH |  |  |  | Included | Included | Graphical representation was always part of the original scope of the development of these standards. Spatial analytics are essential consideration to any analytical consideration to the investment schemas these standards will enable. There are four 'Pillars' - WHO, WHAT, WHERE and HOW MUCH | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
920 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | 6. General content 1.“Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. 2. The units of measure have not been covered during the workshops. Further input may be required before the draft is ready for public release. 3. Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and the implementation may not be practical. 4. Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. In many instances data will be collected in-house. 5. Australian examples and photos should be replaced by New Zealand examples. Word choice such as “savvy” (used often) is not the best choice. Some of the language used needs to be reviewed in order to retain the standard’s professionalism. | NA | 1. Action on volume 1. 2. Action: to be made clear in document that code list are not exhaustive. 3. Action on volume 1. 4. Action: to be changed in In Summary. 5. Action on volume 1. | Vol 1 - Vol 2 |  | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included |  |  |  | Included | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards Code lists for example have now been included | General | 1 | [7 empty] | 1 | [6 empty] | change needed | discussion needed with workshop about mapping these to each organisations requirements. The abjective of the standards is 1. to standardise what is provided by the data service providers. 2. provide data servioce providers with a consistent view of what to capture anddeliver 3. provide certainty to aseet owners ion what they will receive enabling ease of incorporation into their systems. 4. not to provide constarints but to provide specific direction | codelists added | codelists added | codelists added | n/a |  |  |  |  | DISCUSS COMMENT WITH HAYDN | No action |  | N/A | y | We can discuss this, but it is what it is….. An immature understanding
921 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | 7. Implementation The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate has not been considered where organisations may choose not to collect certain information for low risk assets. An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard | Implementation | Business case. Action: Mandatory fields to be reconsidered. | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | N/A |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
922 | Jean DeVilliers | Watercare | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | We believe there is a reasonable amount of work that has not been completed, such as standard definitions, which may lead to inconsistencies between the water organisations. Without this work being completed the documentation that has been produced could only be used as a guideline or a code of practice. | Terminology | Statement noted. See comments HR. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | All definitions have been standardised and normalised | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 2
923 | Orapai Woon | City Waters | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | However, page 141 of Potable Water Volume 1 As-constructed/As-built references code lists for 3 waters assets that can be reviewed in a supplementary document called 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016 Is this document available for download or can it be emailed to me? I would like to cross-check what is in this code list against the attribute tables to assist with my review. | NA | Volume 1 | Vol 1 - Vol 2 |  | George |  |  |  | Included | Included | Code lists are included | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs | resolved in latest version | codelists added | codelists added | codelists added | codelists added | [5 empty] | Change made document updated |  | N/A
924 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | As-constructed schema should not be a separate document, and should recognize that many assets are created though term contracts not just greenfield build. We should not separate “as-constructed” from other elements of the standard because this perpetuates last century’s practice of asset management being about the asset whereas it is about the service enabled by the asset. We should modify the “as-constructed” schema to recognise that construction happens both in new builds and in renewal term contracts and the information should support both efficiently. I am not convinced of the value of separating the standards into two parts. While as constructed data is central to an asset information system there are few transactions that use it in practice. Most construction projects will use subsets of the inventory tables, performance based construction projects will also use the condition and performance tables, term PPP or BOOT contracts will use almost the entire standard. This means there is no one to one connection between projects and elements of the entire data schemas so the split of the source documents is artificial. I think there is a serious downside to separating the two documents that drives us towards a combined view. Asset management is all about delivering services that require significant assets. Separating as-constructed from performance data perpetuates past practice that asset management was about having assets in good condition, whereas it is about having assets in sufficient condition to deliver targeted services. | Service Performance | Statement noted. Unlikely to combine into 1 volume. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. |  |  |  | Noted: no action required | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
925 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Another challenge with this proposed separation and the associated “constructor” reference fields is that for roads and 3 waters, though to a lesser extent buildings, much infrastructure is created through renewal or replacement programmes. For example for State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. This means that we need to think seriously about replacing the “constructor” record in the “as-constructed” table with a reference to an “Asset Intervention” record as described elsewhere in my comments. Unless this is done there will be not be normalisation of records relating responsibility for modification of inventory, a ridiculous amount of duplicate records created from term contracts where much inventory is created, and a mismatch between the constructor records in the “as-constructed” schema and those of the maintenance schema, when in term network management contracts these are the same constructor. The same duplication will occur when the same constructor creates many inventory records as occurs in term contracts | data | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Interventions already recorded under the maintenance, repairs and operations schema. No Action Required. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
926 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The categories of data type should be simple, exhaustive and mutually exclusive so should vulnerability and resilience stand alone? The proposed “global meta data schemata” classifies data into several categories. This is a necessary and good thing because it help users appreciate the scope of the data and find the elements they may be interested in. To do this well the elements must be simple, described in commonly understood language, cover the field of interest, i.e. be exhaustive, and be mutually exclusive, i.e. not have definitions that overlap or require subtle nuancing. | vulnerability | Statement noted. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [17 empty] | No action
927 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Vulnerability - risk There is an open question in the document as to whether vulnerability should be drawn out as a standalone data category, when it influences risk. I do not think it should be standalone because this then makes “risk” become “risk other than vulnerability” and I think that is a bit silly. I certainly agree that vulnerability is important. I think it so important that we should draw it out in the risk or resilience categories. The high level approach to risk is to consider likelihood and consequence. Simplistically consequence conflates: • vulnerability of service, and • impact from reduction or loss of service and vulnerability of service conflates: • vulnerability of infrastructure (considering network effects), and • availability of alternate infrastructure or alternate services. I think we should draw out these or similar elements of risk for those elements of infrastructure type that potentially have a consequence greater than tolerable. This might mean (in the transport context) arterials and above in a transport world because of their importance to the economy and society. Effectively this creates a level of service gap around vulnerability, the very gap that rental companies advertise as being closed when they proclaim on their hoardings that a building to let is 85% EQ code compliant. | vulnerability | Action required. Vulnerability is developed as a separate schema. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | 4.2 Vulnerability Schema | Vulnerability Schema | [7 empty] | 1 | [7 empty] | check if done | [9 empty] | No action |  |  | y | completed | 1 | 1
928 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Resilience - performance Resilience is a service level, or a strategic goal. As a service level it should be within the performance elements of the data standard. I know that it has prominence because it is an important element of performance, but so too are accessibility and safety for transport, or availability of supply or health for water. As a strategic goal it is a driver of service levels. | Resilience | Statement noted. Resilience is to be developed. Resilience will be defined as "the assets ability to provide the service level', and not against the customer. No action required. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Resilience is a state and requires measurement The level of service is subject to the level of service any organisation seeks to apply, and an invetment plan to meet that level | 4.5 Resilience Schema | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
929 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Utilisation is multifaceted and requires enhancement The definition of utilisation given in the draft standard is the proportion of an assets available capacity that is actually being used. I think that there will need to be some clever messaging to ensure that the unit of capacity chosen is understood for infrastructure in different circumstances. Using a transport example provides an illustration of this. Over 60% of New Zealand’s roads are classified as access or low volume access roads. This means that they have less than 1000 vehicles using them per day. A single lane has a capacity of about 1400 vehicles per hour, depending on its configuration, i.e. on the proposed definition of capacity most roads have a daily utilisation of about 1.5% yet these roads represent the last and/or first mile of most trips and so are critical to our economy and society. The level of utilisation will always be low simply because there are rural and urban areas with low population that are connected to market or work place. Even with planned intensification of central urban areas daily utilisation might only rise to 5%. This is analogous to the smallest element of supply or removal for potable or waste water. Also, where there is suppressed demand because demand exceeds supply, e.g. on congested transport networks (whether roads or busses), we may report 100% utilisation, but that is bad because the potential benefit of suppressed trips is being lost or costing more. In a water example we may constrain the development of business when supply is inadequate for development yet fully used by current development. Together these factors mean that we have to be careful about the utilisation measure and how we use it alongside other measures at a local and network level, a simplistic approach won’t do. I think this section of the draft standard needs work to draw out these issues. In addition we need to consider how utilisation and performance metrics are used to optimise asset investment decisions. | Utilisation | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Make utilisation an optional field as utilisation cannot always be assessed. Granularity question . | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
930 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Inventory Interventions At the moment there are two types of works records, those recorded as maintenance and those associated with the as-constructed fields. I think we should consider what we want from the recording of “works” or inventory interventions because I expect that will lead to an improved data structure with one form of works interventions record. | Maintenance, Repairs and Maintenance | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
931 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | I think inventory intervention (or works most commonly) records should reflect or create: • Planned, current, completed or abandoned works so we can fuel the nationwide forward and current works viewer enabling better coordination of works and reduced disruption of customers whether the works are construction, renewal or maintenance. Interventions on inventory are a process that creates or modifies inventory. Much information is required about the process as much as of the fact that it creates inventory. E.g. the forward works viewer being developed to display proposed and current works have time, duration, and place elements of information as well as descriptive information about the constructor and infrastructure being modified or created as reflected in the proposed “as-constructed” schema. | Maintenance, Repairs and Maintenance | Statement noted. Already done in Repairs and Maintenance schema. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Statement noted. Already done in Repairs and Maintenance schema. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
932 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | I think inventory intervention (or works most commonly) records should reflect or create: • Responsibility for management of infrastructure, noting that ownership may pass to a client when inventory enters service, but responsibility for maintenance may extend beyond the transfer date | Maintenance, Repairs and Maintenance | No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Noted | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
933 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | I think inventory intervention (or works most commonly) records should reflect or create: • A hierarchy of works and tasks that distinguish a term contract (or work) from a work task within it so that the work identifies responsibility, type of work, stage of work etc, and the task the date and type of work done linked to the infrastructure impacted. I think this allows better alignment with supplier’s management systems, responsibility for work done, and supports many forms of contract from term based contracts to single task contracts. This also enables security to be built into system for data exchange. This is important because for most infrastructure networks (buildings aside) most new infrastructure arises due to renewal works and not due to greenfield construction. | Maintenance, Repairs and Maintenance | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Statement noted. Already captures type of work. Include responsibility/who carried out the works. Does not require stage of work, as not directly related to asset. | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
934 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Maintenance, Repairs and Maintenance | Statement noted. Asset creation is included under As constructed | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
935 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | I think inventory intervention (or works most commonly) records should reflect or create: • Works that may include either or both of asset creation and maintenance because term contracts do both, e.g. repair potholes and resurface roads using a transport example. | Maintenance, Repairs and Maintenance | Statement noted. Asset creation is included under As constructed | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Statement noted. Asset creation is included under As constructed | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
936 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | I think inventory intervention (or works most commonly) records should reflect or create: • Types of inventory intervention with appropriate records, including, but not limited to: o Physical works, probably the most common type o Waste or abandonment, associated with infrastructure being removed from the inventory and reflected in a valuation as a write-off o Inventory received from third parties, e.g. as a result of transfer from development of a new residential area to a council, or the transfer of responsibility of a road from a local authority to the Transport Agency as a State highway o Inventory transferred to third parties, e.g. the transfer of responsibility of a previous State highway to a local authority on completion of a State highway bypass. I acknowledge that “inventory interventions” is not the best term and that a better one should be found. | Maintenance, Repairs and Maintenance | Action: Abandonment should be included. Ownership etc falls under Volume 1 | Vol 1 - Vol 2 |  | George |  |  |  | Included | Included | Included in the draft Standards | Code List 19: Repairs, Maintenance and Operations Intervention – Workflow Response Type | 1 | [7 empty] | 1 |  |  |  | 1 | ok | [12 empty] | No action |  |  |  |  | 1 | 1
937 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Assessments There is an opportunity to introduce a concept of an intervention type of “Assessment”. This arises because there are many instances where responsibility for some parameter in many of the tables is explicitly referenced, yet is essentially the same information in each case. This information is who changed the parameter, when, why, as a result of what process…? This proposed approach will enable normalisation of data describing the assessment of condition or performance (whether current or forecast), valuation, risk or any other metric in a standard way. It will then identify the provenance and responsibility for each. This proposal is much the same as that for “inventory interventions” in that it suggests that the core information is about the process leading to the metric in the data and this should be recognised. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | Haydn & George Volume 3 is where this information is forecast to reside - yet to be developed But a placeholder code list is a good idea? |  |  |  | Noted: no action required | Noted: no action required | Assesments are (or interventions) are subject to the element being interrogated (e.g. condition). The standards have attributes which capture these. These will however be predominantly the focus of the work when develop-ing Volume 3 | Data Table 1: Condition Attributes & Code List 17: Condition Rating – Methodology |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
938 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Supply of as constructed data I think that we shouldn’t mandate the form for the supply of as constructed (or other data) but rather the relevant metadata describing its provenance, quality etc. If the form is mandated then it would require an absurd level of record keeping and compliance from term contractors who create many new assets. E.g. for State highways we use term contractors who create the vast majority of new surface infrastructure each year. For State highways about 1,100km of road surfaces are created each year through renewal programmes, whereas only about 200-300km are created through the new build programme. Suitably qualified and quality assured staff from contractors enter the as-constructed data directly into our inventory system, and this isn’t shown as an acceptable method of delivery yet it patently is. One of the purported benefits of meta-data standards is that it enables business to business transfer of data. Defining the transfer of data on a disc seems to fly in the face of these benefits and the advance of B2B technology. Similarly I would think that NIU doesn’t want to be involved in contractual requirements for each form of contract, rather whether information is being managed well and is fit for purpose. I think the supply of data section starting on page 1 of volume 1 needs review. | NA | Volume 1 | Vol 1 - Vol 2 |  | Data format (form here) is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | Data format (form here) is not within the scope of these standards | General |  |  |  | 1 | [5 empty] | 1 | [6 empty] | Don’t understand can you please explain to me? | [9 empty] | No action |  |  | y | Data is supplied in a range of formats - relative to the system owned by the organisation (some will use html), others won't - the standards are about the content (and syntax) of the data, not how it is delivered.
939 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset management I think the sections of the standard on asset management need a revision to better reflect: 1. That customer service at least long term cost is the goal, and not maintenance of asset condition, noting that the two are related. 2. Investment decisions made in a customer service centric world. | Front End | Statement noted. Recommendations to HR to clarify this in 1 and 2 in introductory sections. | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a service performance component which is designed to reflect the 'customer service centric world' | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
940 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Customer service focus The various diagrams, for example figure 3 on page 24 of volume 2 is written in very economic language around the return for investment of public funds. This is of course critical, but loses the narrative that relates providing customer service that is economic. | Front End | For Haydn to comment. | Vol 1 - Vol 2 |  | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. |  |  |  | Noted: no action required | Noted: no action required | Service Performance is as important as any f not the most important decision element. Unfortunately the fiscal (economic) lens is one which those who are responsible for often turn to first for a decision. It has been argued the most important interoperability analytic is one which defines the opportunity cost of benefit tension between the cost of a service at a specific level of service and the service provided at that level. Understanding the optimum customer satisfaction point for service and cost is as much about the essence of purpose of these standards as any other single insight enabled by them. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
941 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Customer service focus: I think the steps in the above referenced diagram, and the description on the preceding pages are missing an element and that is what is being targeted in terms of service levels and how this target is established. Or alternatively (as a poor second best) are missing the inputs describing the economic and social benefits of different service levels experienced by customers. If these were present then the analytics could do the required work. This step is required to establish the performance targets referenced in the performance elements of the standard. Eg what is the optimal economic service level for service outages considering investment to reduce the frequency, duration and impact of service outages against the social and economic impacts of these. This step is difficult and complex but needed none the less. It requires decisions about the relative weight to be given to quasi commercial models or economic models. It requires significant analytics to be undertaken to determine the relationships between costs and benefits of different levels of service for different types of customers in different circumstances. Much of these analytics are represented in the economic evaluation manual used to determine the economic value of transport proposals in New Zealand. | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
942 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Customer service focus: The service led approach enables a more informed discussion with customers about expectations of service level and the cost of these than a black box economic model. It essentially proposes a three stage approach: (See figure in word document) This recognizes that information is never perfect to enable ideal one off analytics because customers’ needs, systems and contexts change so what might be optimum now likely won’t be at another time. The aspect of service level target should be reflected in the analytics framework. | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. You will note, any one of the 4-wellbeings are able to be defined within these standards and have other no less important datasets applied to make socially constructed investment decisions that give context to the economic reality of any decision - for any asset. Ultimately that is for the decision-makers. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
943 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Investment decisions in a customer centric world I think that section 1.8 needs some rework though many aspects are worth keeping. There is significant reliance on the metaphor that as assets deteriorate and consequently the maintenance expense to sustain targeted service levels increases there is a sweet spot between condition and maintenance cost. I think we need to recast that metaphor in a customer centric world and recognize that the sweet spot is tautological because the definition used for condition grade 5 is that it has failed or soon will so it is no coincidence that replacement is needed there. | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. Also, condition grade is only one consideration to actual asset replacement, there are 10 others. It is the intention of these standards to use any one or number of them when making a decision. If the tautology is the decision, the tautological instruments are the evidence-based investment decision elements which give the decision context - including service performance (the standards descriptor for customer centric measures). | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
944 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Investment decisions in a customer centric world The proposed standard presents a theoretical approach to stochastic analysis. This style of analysis is becoming common place. The standard might reference the UK’s Highways Efficiency Maintenance Programme website, especially this url: http://www.highwaysefficiency.org.uk/efficiency-resources/asset-management/life-cycling-planning-toolkit.html That site includes standard tools for “stochastic analysis” of renewal programmes using the “5-step condition rating”. While the text is all about roads the processes are generic. With translation, or a babel fish (as Douglass Adams might say) they are as applicable to buildings as to roads. The tools on that site are of course single factor analyses as condition based analytics generally are. There is no single or multifactor customer service optimisation (e.g. skid resistance and ride comfort for roads) that assists planning in a constrained environment or in an environment where value for money matters, but it is a straight forward approach to estimating the works required to sustain performance. That reference, or a more applicable one, or a derivative of it, would go some way to making the theoretical text in the proposed standard tangible. | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. |  |  |  | Noted: no action required | Noted: no action required | These type of analytics are exactly what these standards have been developed for. And, is the exact intention of the analytical foundations set down for Volume 4. There are some who are already applying this level of complexity to decision-making. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
945 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Investment decisions in a customer centric world If the text were recast to be more customer service centric it might use the following approach. The two most important decisions to intervene with some form of monitoring or works when managing a network to provide customer service are: 1. When delivered service levels have or will drop below the targeted level or there is too great a risk that they will 2. When, despite the targeted service level being met, it is cheaper in the long run to intervene, or there is an unacceptable risk that costs will rise unless an intervention is made Intervention decisions can initially lead to a monitor, maintenance, renewal or improvement interventions, whichever is part of the least long term cost intervention strategy. A more colloquial way of putting this is only intervene if its broken, or cheaper in the long run. | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. |  |  |  | Noted: no action required | Noted: no action required | Agreed These standards will allow for the analytical endeavours to measure whether the service and service levels within them are being met and the long run opportunity cost of early intervention or not if you chose to - for the whole of life cost of the asset and the level of service not less. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
946 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Investment decisions in a customer centric world Transport examples of the two decision types are: Ensuring the service is delivered to target. • Replacing the tires on your car when the tread depth has reduced and become unsafe, or ahead of winter when risk is greatest when tread depth has almost become unsafe • Continuing to monitor the change in direction of a river beside a roadway that may ultimately risk scouring of the road formation in order that preventive works can be taken when necessary and most cost effectively to preserve the transport route • Water cutting the excess bitumen off a road to restore the prominence of the chips so tyres grip these rather than “float” on the water film when the road is wet in order to restore the skid resistance of the road surface. • Resurfacing a road when the skid resistance of a road is falling and is either unsafe or will become unsafe before the next opportunity to intervene because the stones have polished Ensuring that delivery of the service is at the least possible long term cost. • Replacing the oil in your car engine even though it is performing well in order to forestall engine damage • Monitoring the condition and maintenance expenditure on deteriorating roads so that and expected renewal works can be designed and timed to be cost effective long term • Sealing cracks in an asphaltic concrete road surface to reduce water ingress to the pavement which would cause the pavement to deteriorate rapidly and require more expensive repairs • Rebuilding or replacing the structural layers in a pavement when this is the cheapest long term cost because deterioration in pavement strength is leading to the need for significant and increasingly frequent and costly repairs and resurfacing treatments to maintain service levels | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | And, is the intention of the analytical foundations set down for Volume 4. |  |  |  | Noted: no action required | Noted: no action required | And, is the intention of the analytical foundations set down for Volume 4. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
947 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Investment decisions in a customer centric world If discussion of the type inferred in the above table were included then the standard would be more tangible to users and better focussed on customer service, the goal of asset management. I think it worth the discussion including reference to or guidance on the economic decision to continue to maintain infrastructure or to renew or replace it on a site specific basis. The IIMM might be suitably referenced. When funds can be used on other investments outside asset management of the infrastructure in question then we look for the sweet spot where the net present value of the renewal plus reduced subsequent maintenance stream is better than the present value of the continued and increasingly expensive maintenance stream. This should be included because it can be implemented site by site for significant investment, and needn’t rely on sophisticated network level analytics and data, though it requires some to describe the relationship between condition, time and maintenance cost. This analysis that maintenance costs typically increase as condition worsens is shown in the following indicative diagram as indicated in the draft standard metaphorical diagrams. This shows there isn’t a sweet spot from this relationship alone. Another factor is required for optimisation and that is the present value of the replacement cost option on a site specific basis, or long term budget on a network basis. (see figures in word document) | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. |  |  |  | Noted: no action required | Noted: no action required | Interoperability analytics are not within the scope of this document All diagrams are stylised schematics to demonstrate the principles of the elements and their relationships, as opposed to actual relationships. These are as variable as there are examples. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
948 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Global Schemata The global asset metadata schemata diagram on page 16 of volume 2 appears out of place with the prosaic listing of detailed data requirements. If it were fully developed as an idea in the text you would expect it to tell a story about why certain data elements are required. No such story is conveyed, so the inference is that whatever data is in the standard will enable such analysis, if that were true then the benefit of the advanced analytics would be small. That seems odd. Does this description add value? | Front End | For Haydn to comment | Vol 1 - Vol 2 |  | There are some who are already applying this level of complexity to decision-making. |  |  |  | Noted: no action required | Noted: no action required | The diagram provides context for the detail that follows There are some who are already applying this level of complexity to decision-making. | 1.4 Context of Asset Data and Analytics |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
949 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Network level performance targets The standard for service performance p101 vol 2 as proposed enables the measurement of performance against a target. This is good. However there is no reference to what good looks like so the measurements are just that. It may be useful to add records that: • Enables the categorisation of target service levels • Set service targets for each performance aspect for each category This would provide the data required to enable reporting of whether the service provided was good enough or not, in a situation where targets differ by category. The One Network Road Classification framework developed by REG for transport classifies roads into 8 categories and sets targets for each. | Service Performance | Statement noted. Outside of scope, Up to the organisation to decide about target service levels. | Vol 1 - Vol 2 |  | Levels of service are policy decisions, and are not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | Levels of service are policy decisions, and are not within the scope of these standards However, where organisatoins provide these levels, these standards will attribute them and analyse them for decision-making purposes | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
950 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Financial Performance The standard has sections on p88 vol2 and succeeding pages. It would be beneficial to review common good practice to understand what data elements should be here. The Australian Infrastructure Financial Management Guide is one such reference. Here as elsewhere the tables can be normalised by reference to an assessment record as proposed above, the type here being valuation. In addition I would have thought there would be considerable opportunity to normalise valuation approaches by assigning each asset a valuation type, and that type record containing the depreciation rates etc. applicable to it. I am not sure that the valuation section has been fully developed yet because some thought must be given to valuation components being different to asset register components. There is no need for them to be the same as they have different drivers. This sections contains data about construction cost that will be transferred to the “as constructed” tables. It asks that the cost of an asset be supplied and that supply is mandatory. However there is a challenge with this because almost all construction contacts cost elements at a higher level of aggregation than each asset. E.g.the construction of a sewage treatment plant does not lead to an estimated cost per inventory item created. Contracts with lump sum maintenance items likewise have no costs per maintenance work task. Therefore a review is required of how costs are acquired and stored and at what level. I suspect that it will be best to capture financial information at the financial/contractual transaction level and activity at the inventory affected level. The concept proposed above for having transactional records for works and tasks enables costs to be collected at that level. | Financial Performance | Statement noted. Needs further thinking. The level of detail of financial info will vary from org to org depending on how costs can be disaggregated. | Vol 1 - Vol 2 |  | Volume 3 is where this information is forecast to reside - yet to be developed |  |  |  | Noted: no action required | Noted: no action required | There is an opportuity to reflect on the tables and code lists provided in the standards. There are some analytical assumptions being addressed here, which are for the analytics in which will be unpacked in more detail in Volume 4. | 5.3 Financial Performance Schema |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 1 | 1
951 | David Darwin | NZTA | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Information required to manage well varies by criticality of network and context I expect that, as with roads, the information needs of managing a water network in a simple undemanding context differ from those of a demanding context. While the performance metrics around health and availability may be common the needs for sophisticated infrastructure and condition metrics would differ. Similarly the information needs for the critical elements in a complex network would be greater than for other elements. This would lead to a hierarchy of mandatory fields based on context. I think this should be considered. | Mandatory Fields | Action: Mandatory Fields to be looked at. | Vol 1 - Vol 2 |  | To discuss |  |  |  | Sector Discussion | Sector Discussion | To discuss | 5.4 Service Performance Schema |  |  | 1 | [7 empty] | 1 | [15 empty] | No action |  | ? |  |  | 1 | 1
952 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | pg 3: Validating the data submission: is this to go against each asset or an organisational process requirement? |  |  | Vol 1 | [5 empty] | Included | Included | Against each asset and against each attribute | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
953 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 1.8 They are requesting that “each asset type must be delivered on a separate level/layer and the files must be clearly labelled…” If this is in a CAD format this makes perfect sense, but then the attribute information that is being requesting won’t be able to put against the individual asset (when last I tried this, it can only be done with blocks, and blocks can be tricky to convert to a shape file). But if in a shape file format, it is a bit of an overkill, it is structuring back to the way we used to have it. And we will need to combine the information in order to import into Assetfinda. it is also implying that information from contractors will be to a High enough standard that we can suck it into our GIS and all points and lines will meet perfectly. In a perfect world that would be great, but from having a draughing background. I can guarantee you are going to get hydrants, valves etc. not matching perfectly with your pipes (this comes from the skill of the person doing the as built) and greater maintenance issues later. We would be relying on the project managers to insist on high quality as built. This then brings up the issue of disposals of existing infrastructure. Or the assigning of asset id numbers that have intelligence. |  |  | Vol 1 |  |  |  | Noted | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | Noted: no action required | Noted: no action required | The requirement of the contractors is that they provide data in accordance with the QA Validation requirements. | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
954 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 1.11 Projects will need to be on board with this. |  |  | Vol 1 |  |  |  | Noted | 26/3/2017 | Noted: no action required | Noted: no action required | Noted, but out of scope. | 1.11 Acceptance Testing |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | suggest you change your response to Noted as it doesn’t acknowledge the point | updated comment | [11 empty] | No action
955 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.1.1 Precision needs to be clarified on what is acceptable. |  |  | Vol 1 | [5 empty] | Included | Included | Precision is defined in the standards | 2.1.1 Accuracy Requirements for Locating Assets | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
956 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.1.5 In the proposed structure, the data Code list fields will be limited to 10 characters, this is not going to allow us to use unabbreviated materials e.g.: uPVC instead of PVC Unplasticised. We need to decide on this now as it affects the look up tables and associated finance. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the "Attribute Name-Full" field once the asset data is provided. | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from mapping this information to their systems using the "Attribute Name-Full" field once the asset data is provided. | 2.1.5 Attribute Data Fields |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
957 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.1.8 The attribute fields they are suggesting may impact on Assetfinda fields e.g.: they are the same but have different criteria. |  |  | Vol 1 |  |  |  | Under review | Please provide more detail about this. Is it that there are system fields that may be in cnflict or is it that there are attribute fields that are named differently? If it is the latter it is expected that asset owners can map these datya fields to their own system requirements. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
958 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.4.1 For Access chamber of valves they are requesting one location point, which is what we have and one polygon of the same area representing a plan view of the valve pit. We have over 2000 valves, that is a lot of additional files, and I feel a duplication of work, as the plan view can already been seen as a schematic when viewing the reticulation. - The same as above goes for Storm water |  |  | Vol 1 |  |  |  | Under review | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | Sector Discussion | Sector Discussion | It has been suggested that each valve is an asset in its own right and therefore asset owners would require specific information about it for analytics. Workshops will be held in May for further contribution. | General for Access Chambers and Valves |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | ok | [12 empty] | More information required for a decision
959 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.4.7 Says that pump stations should be a polygon feature and all attributes are to be attached to this polygon. Then in 2.5.2 which refers to Pumps it requires pumps to be a point feature with all attribute information attached to this point. So which is it. The Pump station, the pump, or both? - The same as above goes for Storm water |  |  | Vol 1 |  |  |  | Noted | The pump station refers to site specific information. The pump is the asset specific information. | Noted: no action required | Noted: no action required | The pump station refers to site specific information. The pump is the asset specific information. | General for Pump and Pump Station |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | ok | [12 empty] | No action
960 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.6.2 Cathodic Protection- I don’t know what that is. |  |  | Vol 1 |  |  |  | Noted | This refers to systems installed to protect water mains from corrosion. | Noted: no action required | Noted: no action required | This refers to systems installed to protect water mains from corrosion. | 2.6.2 Cathodic Protection |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | ok | [12 empty] | No action
961 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | 2.8.2 This puts all the responsibility on the contractor to provide all the specified information in the way the document wants it, with us only needing to import it. - The same as above goes for Storm water |  |  | Vol 1 |  |  |  | Noted | 26/3/2017 | Noted: no action required | Noted: no action required | It also puts the responsibility on the asset owner to specify it properly | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | suggest you change your response to Noted as it doesn’t acknowledge the point | updated comment | [11 empty] | No action
962 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | All the attributes that are being requested of us seems to me to be a lot more information than will ever be needed or used, but if supplied by a contractor as suggested, is achievable. |  |  | Vol 1 |  |  |  | Noted | 26/3/2017 | Noted: no action required | Noted: no action required | Noted, for analytical purposes | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | suggest you change your response to Noted as it doesn’t acknowledge the point | updated comment | [11 empty] | No action
963 | Howard Wilkinson - Michele McClure | South Taranaki District Council | 3-Waters | Vol 1 | General | [5 empty] | Waste Water seems to be a repeat of the above. |  |  | Vol 1 |  |  |  | Noted | 26/3/2017 | Noted: no action required | Noted: no action required | Repeat | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | suggest you change your response to Noted as it doesn’t acknowledge the point | updated comment | [11 empty] | No action
964 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | Executive Summary | v |  |  |  |  | In Summary The main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed potable water assets as defined by asset managers in New Zealand. While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant. It’s not clear who is meant by consultants here. |  |  | Vol 1 |  |  |  | Noted | Note added in glossary 9/3/2017 | Included | Included | Note added in glossary 9/3/2017 | In Summary | 1 | [9 empty] | 1 |  |  |  |  | change needed | add definition to glossary | done | done | done | done | [5 empty] | Change made document updated
965 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 |  | 1 |  |  |  |  | The objective of the specification in Volume 1 is to provide geospatially savvy potable water asset “As Manufactured” and “As-constructed / As-built” digital data. The objective of the specification in Volume 2 is to provide geospatially savvy potable water asset “As Managed” digital data. I don’t like the use of the word savvy |  |  | Vol 1 |  |  |  | George/Haydn | my response would be to say Noted 9/3/2017 | Included | Included | Reviewed and removed | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | suggest change your status to Noted: no action required suggest you change your response to Noted as it doesn’t acknowledge the point | updated comment | [11 empty] | Change made document updated
966 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | Table 1.8 doesn’t appear to include an allowed category or descriptor for “back-flow preventer” |  |  | Vol 1 |  |  |  | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | Sector Discussion | Sector Discussion | This can be added in the codelist of one of the relevant asset classes. Please review the asset tables and offer a recommendation for its inclusion. Decision to be made on which Code List for the new entry Is this also known as a Reduced Pressure Zone valve? | 1.8 Theme Structure |  |  | 1 | [7 empty] | 1 | [15 empty] | New Code List Entry proposed | Back-Flow Preventer
967 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | I presume in Table 1.9 that “N” stands for No. I’m sure there will be some exceptions to the rule per asset |  |  | Vol 1 |  |  |  | Noted | 2017-03-09 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 1.9 Data Principles |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
968 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.1.1 The explanations on pages 6 and 7 between absolute accuracy, relative accuracy and spatial precision are useful; however I think the sector needs to derive one preferred conceptual practice i.e. is absolute accuracy more important than relative accuracy? Whose data set has primacy? E.g. LINZ spatial data with asset data associated by relative accuracy? |  |  | Vol 1 |  |  |  | Noted | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | Noted: no action required | Noted: no action required | With respect to cadastral data - LINZ With respect to council asset data - council 9/3/2017 | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
969 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | I agree with the QA Validation field being a mandatory attribute in Table 2.1.5 |  |  | Vol 1 |  |  |  | Noted | 2017-03-09 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.1.5 Attribute Data Fields |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
970 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | Not all fields in the project attribute table in 2.1.7 are practical. What about a project that is geographically separated (relining different pipes) or across different asset classes? (e.g. water mains and sewers) |  |  | Vol 1 |  |  |  | Noted | 2017-03-09 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.1.9 Project Attributes |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
971 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.1.1 Pg 17 . Ditto for “Area of Work” extent. |  |  | Vol 1 |  |  |  | Noted | 2017-03-09 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.2.1 Area of Work Extent |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
972 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.3.1 How will an open civil structure be represented? E.g. a settlement pond |  |  | Vol 1 |  |  |  | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | Sector Discussion | Sector Discussion | Settlement ponds are covered in another volume - however are there settlement ponds for potable water? | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
973 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | The repetitive use of the generic term “Health & Safety Issues” in the respective attribute tables should be revised to documented Health & Safety Risks. Or similar |  |  | Vol 1 |  |  |  | George/Haydn | Commented on this previoulsy but as its been raised again lets discuss any difference? Is it a risk or something to take note of eg how to access something? | Sector Discussion | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure trigger there are 'special circumstances'. A code list is proposed | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision | Health & Safety Type
974 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | I’m unsure what the use of a “Resilience field (as an open text field?) is in these tables. Too much variability and not enough guidance around what data and format to enter. This is an AM (Vol 2) derivation anyway and not an “As-Built” attribute in my view. Whereas “Design Life” is. |  |  | Vol 1 | Reslience is a Resilience Grade Score |  |  | Haydn | 2017-03-09 | Noted: no action required | Noted: no action required | Resilience Rating is a measured a6ttribute | 4.5 Resilience Schema |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 1 | 1
975 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.3.4 The term Well should be changed to “Bore” |  |  | Vol 1 |  |  |  | George/Haydn | Commented on this previoulsy | Sector Discussion | Sector Discussion | Commented on this previoulsy | 2.3.4 Well |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | ok | [12 empty] | More information required for a decision
976 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.4.3 The point feature is to be “snapped” to the pipe asset it is associated with. Does the spatial representation snapped to the polyline create a node? If not then this creates problems when modelling. |  |  | Vol 1 |  |  |  | Noted | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed 9/3/2017 | Noted: no action required | Noted: no action required | The volume 1's specify how to do the initial capture for councils to then incorporate into their specific systems. The volumes do not stipulate that this is how asset owners must store their data or how to organise it for their works practices. Typically it is expected that councils will align the data received into their systems as needed | 2.5.3 Valve |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
977 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.4.5 How is a locator cable or Intrinsic Protection (IP) cable for anti-corrosion ruining with a pipe (e.g. taped to the pipe) to be represented? Why in the table do we have to submit pipe diameter, nominal diameter, external diameter and nominal bore? This is overkill and one wrong piece of information will lead to confusion i.e. which one is the correct one? |  |  | Vol 1 |  |  |  | George/Haydn | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | Sector Discussion | Sector Discussion | Separarte issues locator and IP - can this be covered by cathodic protection? Diameters required for analytical purposes | 2.4.5 Pipe & 2.6.2 Cathodic Protection |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | ok | [12 empty] | More information required for a decision
978 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.4.7 Should the spatial representation include and ancillary works e.g. dry wells, wet wells, filters, air scrubbers or bio-filters (more applicable to wastewater PS I realise) |  |  | Vol 1 |  |  |  | Noted | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. 9/3/2017 | Noted: no action required | Noted: no action required | The individual assets are captured as per the specific asset class data requirements. This feature only represents the site and is a summary of what is in the site. | 2.4.6 Pump Station |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
979 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.5.2 Pumps, can take many types and forms. I trust the fields in the table are flexible enough to accommodate the variety to be expected. |  |  | Vol 1 |  |  |  | Noted | We hope so. This will be tested during the pilot phase 9/3/2017 | Noted: no action required | Noted: no action required | We hope so. This will be tested during the pilot phase | 2.5.2 Pump |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
980 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | Is a backflow preventer to be considered a mechanical equipment asset or a valve? |  |  | Vol 1 |  |  |  | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | Sector Discussion | Sector Discussion | Your suggestion please. Please review the respective tables to see which one is fit for purpose. Is this also known as a Reduced Pressure Zone valve? | 2.5.1 Equipment & 2.5.3 Valve |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision | Back-Flow Preventer
981 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.6.1 Electrical asset – table doesn’t look accommodating enough for the variety of electrical fittings and assets to be expected |  |  | Vol 1 |  |  |  | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | Sector Discussion | Sector Discussion | We hope so. This will be tested during the pilot phase Happy to receive recommnedation for consideration. | 2.6.1 Cabling |  |  | 1 | [6 empty] | 1 | [16 empty] | More information required for a decision
982 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.6.2 Good to see Cathodic Protection systems included. |  |  | Vol 1 |  |  |  | Noted | 2017-03-09 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.2 Cathodic Protection |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
983 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | 2.8.2 reporting Mismatches could be problematic depending upon the spatial base used – see 2.1.1 above. |  |  | Vol 1 |  |  |  | Noted | 2017-03-09 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.8.2 Matching to Existing Infrastructure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
984 | Howard Wilkinson - Brent Manning | South Taranaki District Council | Potable water | Vol 1 | [6 empty] | There are a heap more Definitions that could be added to the Glossary e.g. “trunk main” for starters. |  |  | Vol 1 |  |  |  | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Sector Discussion | Sector Discussion | Please do not hesitate to provide. The Glossary will be dynamic in nature. | Glossary |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
985 | Emma Duncan | Central Otago District Council | Potable water | Vol 1 | [6 empty] | Request for code lists: On page 158 of volume 1 of the potable water standard there is mention of supplementary document 3Waters Assets Metadata Code lists V1.2 Draft A, 14 July 2016. Even though this document is in draft, I’d really like to take a look at it. Can it be made available for download, or am I to a copy emailed to me? |  |  | Vol 1 |  |  |  | Sector Discussion | Code lists now incorporated into document | Sector Discussion | Sector Discussion | Code lists now incorporated into document | General |  |  | 1 | [5 empty] | 1 | [6 empty] | check done |  | codelists added | codelists added | codelists added | n/a | [5 empty] | Change made document updated
986 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | We appreciate the work put in by your team and the various working groups in developing these documents. The process of evaluating the standards has also been useful for Education as an agency, in promoting a review of our data collection processes and considering how these align with a potential implementation of the standards. Our comments on the standards focus at the strategic level. For our organization, with over 30,000 buildings, the cost of changing data collection are high. We therefore need to consider very carefully what information we capture, what decisions we will need to take with information, how we control the quality of information and how it is updated. For that reason it is important to us that we understand the proposed benefits and implementation uses of the standards before taking firm decisions on data collection for their use. We look forward to further discussion on implementation. Your presentation at the last governance group was a helpful insight into your team’s thinking: we want to ensure that agencies understand each other before committing to implementation or advancing a business case with Ministers. For that reason our comments are interim, subject to these further discussions. | General | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
987 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Overview of the Metadata Standards Education recognises the importance of asset information in protecting New Zealand’s ability to provide services in a fast-changing national economy. We also endorse a commitment to standardising and sharing information between public agencies. However, we have concerns about the detail and structure of the data proposed in the metadata standards. A challenge in commenting on the proposed metadata standards is understanding the objectives of the data collection process. It remains unclear how this information will be used, what elements of the process will be compulsory and how the comparison between agencies will work. Education is concerned that the costs of collecting the information outlined in the metadata standards will exceed the benefits. Understanding the benefits derived from these comparisons is critical to determining what data should be collected and how it should be categorised. For instance, the data that is needed to promote All-of-Government procurement is very different from the data needed to identify major network risks within New Zealand | Implementation | Statement noted. Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Business case. | General |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
988 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Education is also concerned that the focus on the physical condition of the assets may be poorly targeted. Rapid changes in demographics profiles, technology and consumer preferences will also have a major impact on the ability of the current asset networks to meet the future needs of communities. We think that the metadata project should place as much emphasis on the ‘fitness for purpose’, as it does to the physical condition. | Implementation | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | What's fit for purpose will vary as orgs change their future focus. Fitness for purpose is captured in Service Performance. | General |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
989 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | In addition, the metadata standards assume that decisions on asset maintenance are made centrally. Where maintenance decisions are made is a policy choice that is influenced by broader factors than asset management. In the case of Education, asset maintenance decisions are largely managed at a school level. This is a fundamental premise of how the management of schools is devolved to local communities. This is more responsive to the needs of local communities, as well as meaning minor maintenance decisions can be made in the context of education delivery. However, this also means that, while we fund schools for maintenance, we do not specifically control how that funding is spent. This limits the extent to which Education is able to track maintenance expenditure. | Implementation | This suite of standards should allow oversight of whether funding for maintenance is adequate to allow the assets to deliver the required services. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | This standard does not assume where or how decisions are made, it is a set of metadata standards that define decision elements for analytics to support those decisions - in a standard way | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 2
990 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Broad strategic issues: Education’s documentation for new construction includes much of the data outlined in the Metadata standards. However, while we collect and hold this information for each project, we do not capture this data into a central database. The nature of this information is useful when looking at the details of potential redevelopment of an asset but not for evaluation at a portfolio level. As with our response to the overall project, Education believes that clearly articulating the benefits of the process will better inform how and what information needs to be collected. |  | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | Vol 1 |  |  |  | Noted | Workshops will be held in May for further contribution. 26/3/2017 | Noted: no action required | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | ok | [12 empty] | No action
991 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Broad strategic issues: We are aware that much of the information for as-built projects will be provided by the contractor. However, we have concerns that the rigorous specification of data may limit the pool of contractors to larger firms with the resources to provide information in a metadata standard. There is a risk that this reduces competition in the industry, and creates price increases especially in provincial centres where Education operates. Education’s exposure to price increases with small building firms is more pronounced than other government agencies who may build a smaller number of more complex facilities (e.g. Courts, Corrections, Defence). |  | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | Vol 1 | [5 empty] | Included | Included | BIM processes should ensure that data is collected through the design and build phases. This should not fall only on the contractors shoulders. | N/A | 1 | [7 empty] | 1 |  |  |  | 1 | ok | [12 empty] | No action
992 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. |  | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | Vol 1 |  |  |  | Noted | Workshops will be held in May for further contribution. 26/3/2017 | Noted: no action required | Noted: no action required | BIM presents the opportunity to collect this data for "free" and continue to gain benefit from it through the asset lifecycle. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | ok | [12 empty] | No action
993 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: Much of the information outlined in the as-built specification may be available for projects Education is currently undertaking. However, the information Education captures is not held in a centralised data base and may not be held in an electronic format. Given the number of projects Education is operating the cost of loading and maintaining the data centrally may exceed the benefits. |  | Repeat | Vol 1 | [5 empty] | Noted: no action required | Noted: no action required | Repeat | N/A |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
994 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: Education’s ability to maintain the quality of data is also limited by the devolution of maintenance and minor capital works to schools. Most of the subsequent alterations to buildings are controlled by the schools. Reconfiguring teaching spaces is a regular occurrence across the portfolio but it is unlikely that these changes will be updated in as-built records. |  | Internal MoE problem | Vol 1 |  |  |  | Noted | Workshops will be held in May for further contribution. 26/3/2017 | Noted: no action required | Noted: no action required | Implementation considerations are out of scope | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
995 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: The detail of components specified in the metadata standards appear to be very granular for many of Education’s buildings – for instance there are about 200 fields to describe a building ceiling. The majority of Education’s building will be a simple domestic-scale or light industrial structures, where there is little benefit in collecting this level of detailed information. |  | Action on Volume 1 | Vol 1 |  |  |  | Noted | Workshops will be held in May for further contribution. 26/3/2017 | Noted: no action required | Noted: no action required | Implementation considerations are out of scope | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
996 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: Education would recommend that different levels of information are collected for different types of assets. For instance, complex multi-storey buildings with lifts, fire protection and science laboratories, would require more extensive data to be collected than single-storey wooden-structure school buildings. |  | Action on Volume 1 | Vol 1 |  |  |  | Noted | Workshops will be held in May for further contribution. 26/3/2017 | Noted: no action required | Noted: no action required | Implementation considerations are out of scope | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | ok | [12 empty] | No action
997 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: The information Education collects on underground services varies greatly depending on the scale and nature of the development. Many of Education’s developments are additions or small schools in provincial locations, with work undertaken by local building firms. The ability of small contracting firms to record in detail where underground services are located is poor, and records are unlikely to be available in an electronic format. Detailed collection of this data may be appropriate for major assets. However, we recommend that collection of geospatial information on underground services is restricted to the larger or more complex developments. |  | Action on Volume 1 | Vol 1 | [5 empty] | Included | Included | Implementation considerations are out of scope | N/A | 1 | [7 empty] | 1 |  |  |  | 1 | ok | [12 empty] | No action
998 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Detailed data collection issues: The risk assessment analysis in the proposed standards is difficult to interpret and evaluate especially for the type of assets being developed by Education. The scale of Ministry buildings tends to be domestic or light industrial in scale. The risk implications for different components of the assets (such as the roof) cannot be easily separated from the risk profile of other components of the building. We recommend this aspect of the risk criteria of the Metadata standards be critically reviewed. |  | Risk would be defined at this case sat the building or school level not the component level. | Vol 1 | [5 empty] | Sector Discussion | Sector Discussion | The standards make the separation of components and the analysis of risk at a component level of granularity possible. There will be a further discussion about this level of recording with the technial working group. | No Specific Reference |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | ok |  |  |  | n/a | n/a | n/a | n/a | [5 empty] | More information required for a decision |  |  |  |  | 2
999 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Broad comments The focus of the data collection is around the building envelope (walls, roof) with significantly less focus on the interior assets. However, building interiors represent a large component of the total cost of providing assets and are the components with the shortest life expectancy. The interior configuration has a major influence on the ability of school buildings to generate positive educational and social outcomes. For these reasons, Education believes the metadata standards should have a greater focus on the interior assets and configuration. | Buildings | No Action Required. The data collection for interior elements is not limited and can be taken to whatever level works for the orgs. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | All components are collected, including interior components | No Specific Reference |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action |  |  |  |  | 2
1000 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Broad comments As well as the definition of the data held, the metadata schema will need to outline the data structure and hierarchy. If information is not collected at a consistent level in the asset hierarchy it makes comparisons between entities difficult. For instance, it is difficult to compare what proportion of the portfolio has fitted wall insulation, if one agency collects the information by building and another by facility. This aspect of the standards should be reviewed. | data | Every org will have its own data hierarchy. It is not intended to mandate it as this would require many orgs to reorg their AM systems | Vol 2 |  |  | This standard defines the heirarchies of best practice. And, is an opportunity for any new AMIS to adopt as a standard for that AMIS |  |  | Noted: no action required | Noted: no action required | Data Classification, Heirarchy and Structure are all outlined in the Draft Standards | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1001 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Broad comments The amount of information collected about the assessor for each data category is unnecessary. It is always useful to know who undertook the assessment but the collection of qualification and experience against each asset is excessive. This detail should be replaced with a measure of confidence around the measures, such as whether it was the result of an exhaustive analysis or a desk-top assessment. | Confidence | Statement noted, no action required. Confidence in the assessment is included as an element | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Each organisation will decide at what level of granularity (detail) it collects tdata to manage its assets. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1002 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Detailed comments on categories of data The metadata standard outlines the format and categorisation of data on the assets. The following considers each of the categories individually. It discusses these in broad terms and then outlines how Education collates and reports of these asset categories. | General | Statement noted, no action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Statement noted, no action required. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1003 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Condition: The metadata standards propose that condition measures categorise assets by: structure; external; interior; services; and fittings. Separating external cladding and structure is a useful differentiation for some of the housing and light commercial categories. The detail captured on the interior is overly simplistic. The proposed metadata standards focus on cosmetic issues such as the quality of the paint finish, rather than configuration and functionality which is of greater importance for Education. As noted above, interior components represent around one-third of the total building cost and have the highest depreciation rates/shortest lives. Ministry measures: The broad asset categories used by Education are: external; interior; services; and roof. More detailed condition data is held for individual schools but the revaluation and portfolio reporting for Education uses these four categories. Education is currently reviewing options to measure how different building design and fabric choices impact on the light, air quality, temperature and noise levels in teaching spaces. | Condition | No Action Required. The data collection for interior elements is not limited and can be taken to whatever level works for the orgs. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Condition Elements are covered in detail in the standards They do not differentiate buildings by type, beyond the Building Code definition of Facility Importance (which is not building type) These are asset metadata standards, not portfolio form / function and mix standards | 2.2 Condition Schema Code List 13: Facility Importance Rating |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1004 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Repairs and Maintenance The definitions of repairs and maintenance defined in the metadata standards are reasonable and workable. 1. However, collecting data on deferred maintenance items is too complex and unproductive. Part of the issue is that subsequent work may override the maintenance items, but be difficult to identify and measure. Under-maintaining an asset may be best reflected in the condition assessment process. 2. Ministry measures: Education currently identifies programme maintenance items to be undertaken on a building, including recurrence timeframes. Education also categorises the reason for maintenance according to priority (i.e. health and safety, protection of building etc). While Education has a good knowledge of the budgeting for repairs and maintenance, it does not track specific expenditure, accountability for which has been devolved to schools. This means that the explicit scope of work that has been undertaken is not available in Education’s information systems. | Maintenance, Repairs and Maintenance | 1. Deferred maintenance attributes to made optional. 2. Some of these classification could be made optional. | Vol 2 |  |  | noted |  |  | Included | Included | Organisations will determine and record the level of granularity (detail) as required | No Specific Reference | 1 | [8 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1005 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Utilisation: The utilisation measures by nature need to be specific to the industry in which the agency operates and would tend to be for internal reporting only. There is limited advantage in establishing utilisation standards for comparison between entities with very different objectives. This is more appropriately a component of the annual reporting to stakeholders rather than a metadata measure. Ministry measures: Currently Education has a formula for entitlement of classrooms and other space based on school enrolments. Education measures schools’ provision of space compared to entitlement with an optimal target range of 85% to 105%. | Utilisation | Statement noted. No action required. Treasury would likely want to be able to objectively compare asset utilisation when making investment decisions. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Agreed, but the standards apply across all Sectoirs (e.g. Housing Providers) | 3.2 Utilisation |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1006 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Demand There are several problems attempting to identify demand for an asset. These are compounded for school assets, which provide free and compulsory services. Commonly residential and light commercial facilities have a variety of different demand parameters. For instance a school hall will support school assemblies, indoor sports activities and community events. Each of these demands has different physical requirements. Measures of demand are therefore difficult to establish. Ministry measures: Education regularly needs to address circumstances where the demand for a school exceeds its capacity. This would commonly be dealt with by strategies such as the application of enrolment zones. Education uses local and regional demographic trends amongst other inputs to identify demand for additional learning spaces and/or new schools. | Demand | Statement noted. No further action required. Demand is variable across building types but not overly complicated to determine. Attribute is optional. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Demand Section has been updated in Volume 2 And, there are many examples of useful demand analytics for schools | 3.3 Demand Schema |  |  |  | 1 | [5 empty] | 1 | [16 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2
1007 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Criticality Applying criticality to residential and light commercial buildings is more difficult than with infrastructure. The metadata approach to defining communities being serviced by public sector buildings is not viable. Communities which use public sector buildings tend to be complex and overlapping and criticality dependent on other assets within the network. The definitions of criticality should therefore be limited to explicit requirements in supporting post-disaster response or recovery i.e. identifying assets which have an explicit function defined by Ministry of Civil Defence and Emergency Management plans. Ministry measures: The criticality for the school as a civil defence centre is an agreement between Civil Defence and the Board of Trustees. This will partially be dependent on other community infrastructure in the location. Schools which are Civil Defence centres are not identified within Education’s central information systems. | Criticality | Statement noted. This chapter has been re-addressed in the risk, vulnerability and criticality cohort. No further action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Critciality will be closely linked to Faclity Importance per the Building Code | Code List 13: Facility Importance Rating |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1008 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Risk The metadata schema for risk measurement works to associate risks with asset components. For most of the risks (e.g. earthquake, flooding) it is more appropriate to associate the risk with a building or site, rather than individual component (e.g. roof). Ministry measures: Education has risk registers at a portfolio level and each school has a risk register. Some of the risks associated with the assets relate to the use of materials (e.g. asbestos). These are also logged on the school risk register but not captured centrally. | Risk | Statement noted. This chapter has been re-addressed in the risk, vulnerability and criticality cohort. No further action required. | Vol 2 |  |  | noted |  |  | Included | Included | Risk can be applied at any level of granularity Analytics enable Portfolio level of risk to be established | 4.4 Risk Schema | 1 | [8 empty] | 1 | [16 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2
1009 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Resilience The resilience measures have yet to be developed within the metadata standards. The focus of the resilience measures appears to be around major civil defence and emergency events, such as earthquakes. It will be useful to identify the ‘Importance Level’ as defined in building legislation. A sole focus of the civil defence component of resilience is too narrow. We believe the issues should also encompass the ability to change the use of assets or to reconfigure them for different demand or purposes such Ministry measures: When Education developed the business plan for transportable modular classrooms it aimed for these to constitute a proportion of the network to allow flexibility to respond to demographic changes. | Resilience | Statement noted. This chapter has been re-addressed in the risk, vulnerability and criticality cohort. No further action required. | Vol 2 |  |  | noted |  |  | Included | Included | Resilience has been updated in the standards | 4.5 Resilience Schema | 1 | [8 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1010 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Design Performance The majority of the design performance schema appears to relate to items of equipment, such as pumps and piping. This represents a relatively small proportion of the assets within Education’s network. The majority of the network is relatively uncomplicated, one and two storey buildings, with limited HVAC or specialist facilities. Collecting design performance at the level of individual items is therefore of limited value. Ministry Measures There are some specialised assets within Education’s portfolio, such as lifts in multi-storey buildings. However, these are few in number and are managed under a national contract. Details on the design performance of smaller components, such as heat pumps are typically held by the school. | Design Performance | Statement noted. The organisation can determine level of granularity themselves. It is recognised that design performance is only applicable to certain asset types. | Vol 2 |  |  | noted |  |  | Included | Included | There are also mant examples of building design perfomance (Earthquake Rating, Energy Rating etc.) | Table 14: Design Performance Examples | 1 | [8 empty] | 1 | [16 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2
1011 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Financial Performance There has been significant effort to develop measures for financial performance within the standards. The proposed standards outline a detailed basis for the collection of valuation, depreciation, time of payment information. Rather than replicate data held elsewhere, it would be more useful to ensure that there are linkages with the agency’s broader financial system. This has the advantage of enabling association of asset measures with other agency performance measures, for instance measuring the asset cost per visitor or student. Ministry Measures Education has recently established a new asset management system (Tribal K2) which tracks budgeting for maintenance and other property costs. The system links to Ministry’s property data warehouse system. This allows analysis and development of a broad range of performance measures. The result is the ability to compare asset performance measures to aspects such as student numbers (e.g. the percentage of students learning in buildings that fall into each asset condition category). | Financial Performance | Statement noted. No action required. Organisation specific and cannot be addressed in this standard. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Organisation specific financial analytics will be supported by attribution within this standard. | 5.3 Financial Performance Schema |  |  |  | 1 | [5 empty] | 1 | [16 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2
1012 | Julie Keenan | Ministry of Education | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Service Performance The service performance schema appears to be a raft of unrelated criteria, which individually may be critical to the functionality of the asset, but do not belong in the same category. The result is measures which relate to different levels of assets from components (e.g. disabled access) through to facilities (e.g. iwi interest). A number of the proximity measures, such as kilometres to communities are difficult to establish without further definitions of community. The result is a wide range of criteria which does not allow comparison between different agencies. Similarly, the raft of measures around district plan criteria, such as provision of car parks, is difficult to update. For many public service assets the land will be designated so underlying zonings will be poor indicators of the use of the site. Some aspects of the data, such as iwi values, heritage considerations or community interests, cannot be easily summarised into a data base. It would be better to include an identifier which would highlight whether more detailed analysis is available on file. Overall Education would advocate for service performance to be restructured into a number of separate themes. Ministry measures Education has a basis for evaluating the service levels called the Innovative Learning Environment (ILE) assessment tool. The information is currently collected at a building level and is a requirement of the five yearly capital and maintenance planning process. Education is evaluating ways of standardising the capture of the information. The ILE assessment tool also has facility to include a range of qualitative measures such as ‘how well the design reflects the needs of the local community’ which may be developed in future. | Service Performance | Statement noted. No action required. Business case. The standard is intended to system and organisation agnostic. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required with regards to comment son the business case. The standard is intended to system and organisation agnostic. | 5.4 Service Performance Schema |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1013 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Introduction The Auckland Council family fully supports of the intention behind this standard and has actively contributed in the working groups for roads, residential housing and light commercial buildings and the three waters. The Auckland Council family welcomes the opportunity to provide feedback at this time, and the opportunity to participate in the further development of the standard. The metadata standard is a great opportunity to gain national consensus of what minimum level of data capture is required. This initiative will enable us to ensure that data can be applied in a consistent and repeatable way to make good asset management decisions based on acceptable levels of service, replacement and growth strategies. | General | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1014 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Summary Feedback is currently sought with specific regards to the three waters and the residential housing and light commercial buildings standards. We have found it difficult to provide meaningful feedback in the absence of a clear strategic message, an understanding of which is shared by all reviewers. That message needs to link the standards to the business case and to recently held discussions with the Minister of Finance. A further opportunity to work on and develop the standard from the ground up, in the way that the transport group has developed the roads standard, would also help the Auckland Council family to feel more confident about the result. To that end we suggest that it would be useful to incorporate such an opportunity into the process from here. We would like: • To present our feedback to the combined governance group • The working groups to review and address all feedback on the standards • The resulting outputs to be made available for consideration by the governance group prior to any public release of the standards | General | Statement noted. Haydn to provide feedback on the process moving forward. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Discussions will continue across the Infrastructure Sectors (Core and Social) | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1015 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Volume 1 – As-built metadata standard What we like: • Provides reasonable coverage of possible data fields • As a collection of possible attributes it will help to drive a culture of good practice to capture metadata • It brings attention to the need for good base data What we consider could be further developed: • In its current format the standard is not adoptable due to the constraints it will place on systems and business processes this needs to be addressed before it can be adopted. |  | Action on volume 1. Further understand why considered not adoptable. | Vol 1 |  |  |  | Under Review | Please provide further information relating to your constraints. 7/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  | 1 | ok |  |  |  | NOTED | NOTED | NOTED | NOTED | [5 empty] | More information required for a decision
1016 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | What we consider could be further developed: • The layout should be modified to clarify the distinctions between master data and metadata. |  | Action on volume 1. Check if there is a statement clarifying this. | Vol 1 |  |  |  | Under Review | Please provide an example where this has occurred. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | NOTED | NOTED | NOTED | NOTED | [5 empty] | More information required for a decision
1017 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | What we consider could be further developed: • A number of elements have been included but are not complete, and an understanding of industry definitions, hierarchies and processes is required to complete this volume. We would welcome the opportunity to assist with this. |  | Action on volume 1. Specifics addressed in excel sheets attached. | Vol 1 |  |  |  | Under Review | Please provide examples for consideration for icnlusion. Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | COMMUNICATION | COMMUNICATION | COMMUNICATION | COMMUNICATION | [5 empty] | More information required for a decision
1018 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 2 | General | [5 empty] | Volume 2 – Asset management performance standard What we like: • Recognition of the notion that data is only useful if it is used • An approach that recognises the value of rigorous analysis to inform decision making What we consider could be further developed: • In general, we consider that this volume is under developed with inconsistencies and cross-overs to Volume 1. We would welcome an opportunity to further input into its development, as we recognise that it can provide a useful tool, particularly for organisations with limited capability in this area. | General | Action: Can Auckland family provide specific inconsistencies. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Volume 2 is now a comprehensive document | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1019 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 2 | General | [5 empty] | What we consider could be further developed: • This volume assumes generalist practices that are inadequate for non-linear assets and includes operational and derived data that is not suitable for inclusion in an AMIS system. | General | Every org will have its own data hierarchy. It is not intended to mandate it as this would require many orgs to reorg their AM systems | Vol 2 |  |  | To discuss |  |  | Noted: no action required | Noted: no action required | This volume is spatially aware, and will attribute point, line, ployline and 3D objects. It is also agnostic to any AMIS and GIS system | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | This will be discussed at the technical workshops |  |  |  |  | 2
1020 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 2 | General | [5 empty] | What we consider could be further developed: • Needs to be carefully framed for the asset types that it relates to. | General | Statement noted. Action required. The aim of the standards is to be able to compare the cost of ownership of different asset types. We only need to capture the level of detail about the assets to allow us to capture this. Action: Need to be more clarified in the standard. | Vol 2 |  |  | To discuss |  |  | Noted: no action required | Noted: no action required | Asset types are specifically defined within the standards - See Volume 1 of each Group of Assets | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1021 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 2 | General | [5 empty] | What we consider could be further developed: • Replacement trigger points should be broadened from reliance on subjective visual condition to incorporate best practice for optimal replacement, that is, based on objective measurement and sound engineering judgement. | Condition | Action: To be clarified in document the condition is one method of determining remaining useful life. Other factors may affect the replacement date. | Vol 2 |  |  | noted |  |  | Included | Included | Visual inspections are only one type of condition assessment to trigger an interventi. Capacity could be another (at Very High > 95%) | Code List 31: Demand – Capacity Unit of Measure | 1 | [8 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1022 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 2 | General | [5 empty] | What we consider could be further developed: • Reference should also be made to failure mode effects analysis (FMEA/FMECA) as a means to support optimal replacement points. Our feedback does not further consider this volume due to the large disparity with practice and limited workshops to fully capture industry needs. | Condition | Statement noted. No action required. FMEA are more useful when you have multiple identical assets. | Vol 2 |  |  | noted |  |  | Included | Included | The standards do not preclude failure mode analysis of any type. The standard captures some of the attributes for this analysis. | 2.3.5 Code Lists | 1 | [8 empty] | 1 | [16 empty] | This will be discussed at the technical workshops - mor ework is required here with the sector |  |  |  |  | 2
1023 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations: 1. Create a separate volume that covers strategic fit and business needs across all asset categories. | Volume Interaction | Action: This separate volume will be covered in the business case. Information to be transferred to HR. | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | N/A |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1024 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations: 2. Focus on a business standard for assets including improving the hierarchy to cover both asset and data hierarchies and outline the relationship between them. | data | Statement noted. Hierarchy to be decided by individual organisations. Not all organisations use the same hierarchy. | Vol 1 - Vol 2 |  | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. |  |  |  | Noted: no action required | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1025 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations: 3. Review publishing formats to maximise the impact of the standard. | QA | Action: editors. | Vol 1 - Vol 2 |  | The drafts have now had a full publishing edit |  |  |  | Included | Included | The drafts have now had a full publishing edit | General | 1 | [8 empty] | 1 | [16 empty] | No action
1026 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations: 4. Remove content that is not related to the business standard including those referring to implementation paths, delivery mechanisms and quality control rules. | Implementation | Action on HR. | Vol 1 - Vol 2 |  | To discuss - for example? |  |  |  | Sector Discussion | Sector Discussion | To discuss - for example? | General |  |  | 1 | [6 empty] | 1 | [7 empty] | COMMUNICATION | COMMUNICATION | COMMUNICATION | COMMUNICATION | [5 empty] | More information required for a decision |  | ?
1027 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The Workshops The working groups were presented with A-Spec as a straw-man and tasked to focus on the possible data that could be captured for individual asset types. The working groups started with limited traction and concern was raised early on as to the purpose of the workshops in diving into attribute detail that is quite easily obtainable from various sources. A basic data hierarchy was established that allowed the attributes to be tackled in a constructive manner. In hindsight, it would have been useful to consider other industry standards as part of the process. We feel that such consideration could still be undertaken as part of the follow on from this feedback. Despite the concerns mentioned above, the workshop groups generally worked well and came to agreement on the things that were required. It would be extremely useful for the working groups to go over the feedback and address it as appropriate. Strategic, governance and procedural feedback should also be reviewed by the governance groups. | General | Statement noted. Hierarchy to be decided by the organisations. Action on Volume 1. | Vol 1 - Vol 2 |  | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. |  |  |  | Noted: no action required | Noted: no action required | There area number of internationally recognised data hierarchies already, we should recognise these where appropriate. | General |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1028 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • Definitions of industry terminologies and attributes. | Terminology | Examples required | Vol 1 - Vol 2 |  | noted |  |  |  | Sector Discussion | Sector Discussion | Examples required | General |  |  | 1 | [6 empty] | 1 | [7 empty] | COMMUNICATION | COMMUNICATION | COMMUNICATION | COMMUNICATION | [5 empty] | More information required for a decision |  | ?
1029 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • Identification of business needs. | Implementation | Business case will outline / describe benefits | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business case will outline / describe benefits | N/A |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1030 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • An assessment of “fit for purpose” data capture. A matrix and understanding of the minimum data capture required based on organisational needs. | Mandatory Fields | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | N/A |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1031 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • Exploring the origin of the data and identifying whether it belongs to volume one (As constructed) of these standards or is better suited with other data sources, for example geotechnical data. | NA | These data sets are what are required for asset management purposes | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | These data sets are what are required for asset management purposes | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
1032 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • Validation of the Codes list or optional pick lists. | Code List | Reviewed and implemented | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Reviewed and implemented | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
1033 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • The standard is required to be system agnostic. Identifying how the standard will be implemented has an effect on the data capture requirements. To enable this we need to understand what the systems and processes look like. The standard needs to be reconciled with these systems and processes at organisation level. | Implementation | Updated | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Updated | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
1034 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The following work that is fundamental to the success of the standard: • Comparison to international practice and other complimentary standards. | Other standards | Information to be provided for discussion | Vol 1 - Vol 2 |  | noted |  |  |  | Sector Discussion | Sector Discussion | Information to be provided for discussion | General |  |  | 1 | [5 empty] | 1 | [7 empty] | is this OUT OF SCOPE ? | [9 empty] | More information required for a decision |  | ? | y | Not out of scope , we have a review completed - but a moving feast
1035 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Format of the standard and target audience • There is a logical split between roads, buildings and three waters; however there is less logic to further splitting up the three waters when the majority of the components and attributes are the same. It would be sensible to consider consolidating these. | Volume Interaction | Statement noted. Action on HR. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. |  |  |  | Noted: no action required | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
1036 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Format of the standard and target audience • Rather than repeating the introductory statements in both volumes of each version of the standard a covering or base document (as seen in most other standards) should be considered, as the principles of data collection are the same. This would also have the advantage of slimming the volumes down. | Volume Interaction | Format based on technical differentiation | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Format based on technical differentiation | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
1037 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Format of the standard and target audience • Common data sets are repeated at every asset class adding unnecessary volume. | data | Action on data scientists. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action on data scientists. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
1038 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Format of the standard and target audience • The standard seems to reference the manner in which data will be collected. This is the responsibility of the various organisations and should not form part of the standard. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | General |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1039 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • The document will benefit from a better structure around the rationale, strategic drivers and added benefits, of the standard. Some of this information is scattered across the introduction section but it could be strengthened and focused on the purpose of the standard, which is about agreeing on common classifications and definitions. We think there is general agreement that data standards are needed and this doesn’t need to be emphasised. | Front End | Action on HR. | Vol 1 - Vol 2 |  | There is no sense from this, what is meant by this. There are no examples or any amended text to support the observation. |  |  |  | Noted: no action required | Noted: no action required | This is not a policy report, an asset management plan, nor a 30 Year Infratsructure Plan (where you would find this requirement). This is a metadata standard for assets at an assetID level of granularity. It does however capture the context of the analytics which inform these types of documents which support organisations asset management | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1040 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • We believe that the key purpose of this standard should be to outline data requirements that enable organisations to compare their performance and share asset lifecycle knowledge while continuing to measure their performance in a meaningful and cost effective manner in the context of their strategic objectives. | General | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1041 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • The intention of this standard development was to produce a metadata capture culture and identify the appropriate level of capture. This intention has been somewhat obscured by the very much “field-base” information that is supplied by suppliers and contractors on the physical attributes of assets. We believe that it would be useful to reconsider the audience of this standard and review it to ensure that the audience is appropriately targeted. In that way the business strategy can direct appropriate attribute fields, which will then be common sense as long as common definitions are understood. | Implementation | Business case. And action on volume 1. | Vol 1 - Vol 2 |  | This observation describes on audience, this is not the only audience, for example design engineers. |  |  |  | Noted: no action required | Noted: no action required | This observation describes on audience, this is not the only audience, for example design engineers. | General |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1042 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • Data capture, as acknowledged in the standard is but one component of good asset management and the ways in which this initiative will support organisational challenges such as achieving ISO 55001 accreditation could be made clearer within it. | General | Statement noted. This standard is not intended to define an Asset Management standard. | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | N/A |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
1043 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • The standard strategic goal is to enable organisations and the country “to collect locally and use globally”. It is unclear how this standard compares and incorporates international best practice. There are examples of other international metadata standards however only A-Spec was examined. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | A number of other standards have been investigated. The strategic goal is to enable organisations and the country “to collect locally and use nationally” |  |  |  | Noted: no action required | Noted: no action required | A number of other standards have been investigated. (Uniclass, Cbi, Omniclass, Master Spec etc. etc.) The strategic goal is to enable organisations and the country “to collect locally and use nationally” | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
1044 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • The way in which the standard is currently written presents the data capture requirements in a set manner and format thereby requiring business needs to be moulded for the data specific needs. These limitations are likely to prevent users from taking opportunities in system and process advances that may become available. Some of these initiatives already exist such as open data sources from product suppliers. We expect these advances to become more readily available in the future. It is not clear how the static two-dimensional model presented by this standard will allow business to incorporate these changes. | data | Statement noted. | Vol 1 - Vol 2 |  | Data capture is not within the scope of these standards, this standard is about data delivery. Data capture will be the defined purpose of Volume 3 |  |  |  | Noted: no action required | Noted: no action required | The standard does exactly the opposite to what this is suggesting. The question is not so much about how it is collected but how the data is manipulated into a common format when it is (see FME) | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2
1045 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • Existing systems have been heavily invested in and are very diverse, even in the Auckland council family, to tailor for specific needs. With the possibility of the standard purely becoming a mapping exercise; it then does not support the need to prescribe data fields to intricate detail. The level of data capture required to complete the national level analytics is not identified. Anything else is considered optional and does not support the reason for capturing data at every level. | Mandatory Fields | Action: Mandatory, optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. |  |  |  | Noted: no action required | Noted: no action required | The standards have harmonised and standardised data and hierarchies across the standards. The implementation of how these fit into disparate, non-harmonised and standardised ICT solutions within any organisation are not within the scope of these standards. The purpose of the standards are to enable any specific analytical need, either currently in use, or not. But Note use of tools like FME. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [6 empty] | Haydn please note - harmonid=sation has not occurred across Vol 1's and Vol 2's | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  | y | Yes there has….. They are harmonised by the primary key fields of each of the decision elements and the tables 'nested' within them No need to standardise across Vol 1 & 2 | 2
1046 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Strategic fit of the standard • In order to address the matters referred to in the point above, the standard could be reconfigured to provide the required performance outcome and guidance on how these requirements may be met, while allowing flexibility in means and methods of demonstrating compliance. | Mandatory Fields | Action: Mandatory, optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. | Vol 1 - Vol 2 |  | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. |  |  |  | Noted: no action required | Noted: no action required | The implementation of the standards are not within the scope of these standards. There are known tools which any organisation might like to use to examine the competency of their data once adopted (for example data completeness, or data stochasticity). And analyse any identified use for analytical competency that would naturally follow. And, there are many analytcal options on the same data sets depending upon he problem being solved. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2
1047 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Language and definitions • As has been mentioned previously, the document uses terminology and jargon that is not consistent with those used in NZ. This is an easy fix, and appropriate language is a great factor in the ease of adopting new things. | QA | Action: language to be reviewed. | Vol 1 - Vol 2 |  | The drafts have now had a full publishing edit |  |  |  | Included | Included | The drafts have now had a full publishing edit | General | 1 | [8 empty] | 1 | [16 empty] | More information required for a decision
1048 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Language and definitions • There are plenty of NZ examples of assets of each class and type, and we will be happy to provide some if required. Using Australian examples in a NZ standard is not appropriate where there is a suitable local example available. | NA | Action on Volume 1 | Vol 1 - Vol 2 |  | George |  | Under Review | Please provide examples for consideration for icnlusion. Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | COMMUNICATION | COMMUNICATION | COMMUNICATION | COMMUNICATION | [5 empty] | More information required for a decision |  | N/A
1049 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Language and definitions • It is also important that the examples used are relevant to the asset type contemplated in the standard. Building examples for the residential housing and light commercial standard will make the logic of the approach more apparent. | QA | Action: examples to be reviewed. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | A full publishers edit has been completed on the standards | General | 1 | [7 empty] | 1 |  |  |  | 1 | ok | [12 empty] | More information required for a decision
1050 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Language and definitions • Most of the terminology used in the attribute fields is not defined. Without these definitions data cannot be accurately mapped and the data collector will be left to assumptions that will compromise data integrity. | data | Action: Volume 1 and 2 | Vol 1 - Vol 2 |  | Haydn & George Defining the attributes of the attributes defining the data. |  |  |  | Included | Included | A full publishers edit has been completed on the standards | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  | refer to column "Contents" | [10 empty] | More information required for a decision
1051 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • At the beginning of the working group workshops we agreed that these are business standards – hence system agnostic; this is even mentioned in the document. At the same time the proposed standard – language, data formats and terminology – has been prepared for an easy input to a functional specification for a GIS application. It is evident that the asset classification and the attributes were “flattened” to fit this particular implementation. This has detrimentally affected the business value of the standard – we have a number of attributes that do not belong to the asset class they are listed against. An example: in stormwater, swale only attributes are elevated at channel level, at which level they are meaningless. |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | DEFINITION OF BUSINESS STANDARD REQUIRED ARE THE DATA STANDARDS THE BUSINESS STANDARDS? | DEFINITION OF BUSINESS STANDARD REQUIRED ARE THE DATA STANDARDS THE BUSINESS STANDARDS? | DEFINITION OF BUSINESS STANDARD REQUIRED ARE THE DATA STANDARDS THE BUSINESS STANDARDS? | DEFINITION OF BUSINESS STANDARD REQUIRED ARE THE DATA STANDARDS THE BUSINESS STANDARDS? | [5 empty] | More information required for a decision
1052 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • The current format of data requirements as a mix of business standard and specification is of particular concern. On one hand it makes the business part of the standard logic hard to follow, while on the other hand the document is not sufficiently detailed to be effective as a functional specification. As a consequence standard does not show the business what it needs to collect and the application vendors will not understand what they need to build. |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | Comment noted. Further discussion needed with Auckland for specific examples | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | AS PER COMMENT FOR ID1051 | AS PER COMMENT FOR ID1052 | AS PER COMMENT FOR ID1053 | AS PER COMMENT FOR ID1054 | [5 empty] | More information required for a decision
1053 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • The asset data hierarchy needs to be completed. Most importantly the way assets have been grouped for data capture needs to be reconsidered in order to represent the business asset hierarchy. Business hierarchy is of great importance for FMEA, operation and maintenance of complex assets, for example. The exclusion of business hierarchies from the standard will require every organisation to create another set of rules outside of the standard in order to maintain these relationships. |  | Action on volume 1. | Vol 1 |  |  |  | Noted | Haydn this is a good point being raised. Important to differentiate between an organisations hierarchy and what is intended in these documents - i.e. a classification. At this stage I am only interested in the impact to Auckland as cannot speculate what impact of others. Suggest the following response. "The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers. As each organisation hss their own hierachy it is expected that they will categorise the data being provided according to their needs. 26/3/2017 | Sector Discussion | Sector Discussion | The requirement will be for a uniform method of data supply to each and every asset owner. The classifications (identified as hierarchies) listed is to provide specific direction for the data service providers that in turn will provide consistency to the asset owners. As each organisation has their own hierachy it is expected that they will categorise the data being provided according to their needs | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | CATEGORISE DATA ONCE DELIVERED INTO ORGANISATIONS SYTEMS COMMUNICATION | CATEGORISE DATA ONCE DELIVERED INTO ORGANISATIONS SYTEMS COMMUNICATION | CATEGORISE DATA ONCE DELIVERED INTO ORGANISATIONS SYTEMS COMMUNICATION | CATEGORISE DATA ONCE DELIVERED INTO ORGANISATIONS SYTEMS COMMUNICATION | [5 empty] | More information required for a decision
1054 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • We strongly recommend that all implementation related fields be removed from the document, as outlined below: o Attribute abbreviations – these are in many cases system related setup and for instance instrumentation may be adopted by numbering systems such as ISA55 that is international practice. The purpose of these abbreviations is not clear. o Character length – This serves no purpose and is not supportive of being system agnostic. By providing full and proper definitions to the attribute field data may be mapped correctly, regardless of character lengths. o Comments – This filed has no purpose that cannot be fulfilled by either the unit filed or description fields o QA validation – These are rules set by business and specific software systems. It also does not serve any purpose to identify minimum capture level. This could be done in a better way through a developed hierarchy that identifies, master data from metadata and compulsory fields from conditional or optional fields |  | Action on volume 1. | Vol 1 |  |  |  |  | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | Included | Included | The primary purpose of these standards is twofold. 1. to provide direction to the data service providers to the asset owners (government agencies) as to what is expected for delivery. System requirements are required so that the data service providers can establish a common business practice to service the many agencies. 2. provide the asset owners with a common practice for their consideration and adoption. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. Workshops will be held in May for further contribution. | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
1055 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • To date geometrical and topology rules have not been discussed. Currently there are different requirements governing the way geospatial data is captured. As with the asset management systems, investment has been made in maintaining systems to these rules. From an analytics point this does not seem to have any impact on the analytic output. Development of such a standard is considered to be a separate endeavour in its own right and has the potential for having great cost impacts to organisations. In the same way one could argue other data sets must then be prescribed – such as geotechnical information, drawings and so on. Flexibility is key, as planning for known technology, given the pace of technological change, will mean that the standard is out of date before it is published. |  | Action on volume 1. | Vol 1 |  |  |  | Noted | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | Included | Included | Generic topology has been incorporated as part of the method of data capture. It is acknowledged that this varied by organisation. Flexibility has been built into these standards so that the data can be incorporated into each asset owners systems as they deem appropriate. | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
1056 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • Attribute sets are not normalised across the asset classes. An example of this is the repetitive material types in the codes lists. (Note. Watercare, Wellington Water and Christchurch City Council were the only parties to receive the codes lists later on request. This was never published. |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | It is acknowledged that codelists will need to be dynamic in nature and will be open to continuied contribution from the sector. The code lists are now incorproated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | Included | Sector Discussion | It is acknowledged that codelists will need to be dynamic in nature and will be open to continuied contribution from the sector. The code lists are now incorproated into the documents The standards have harmonised and standardised data and hierarchies across the standards Workshops will be held in May for further contribution. | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action
1057 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 | General | [5 empty] | Scope and content of Volume 1 • As-built data versus operational data versus derived data is crossed over between the volumes. Separation is required through the data hierarchy. |  | Action on volume 1. | Vol 1 |  |  |  |  | Not certain how to anser this - obviously interested in your view. Ithink the general answer is - yes there are elements of each - however do not support the view about the hierarchy as that is organisation specific. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  |  |  | NOTED COMMUNICATION | NOTED COMMUNICATION | NOTED COMMUNICATION | NOTED COMMUNICATION | [5 empty] | More information required for a decision
1058 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 1. Create a separate volume for strategic fit and business needs | Implementation | Business case. | Vol 1 - Vol 2 |  | To discuss |  |  |  | Noted: no action required | Noted: no action required | To discuss | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | More information required for a decision |  |  |  |  | 2
1059 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 2. Focus on business standard for assets: • Improve the Asset Hierarchy section to cover both asset and data hierarchy and to outline the relationship between them. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
1060 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 2. Focus on business standard for assets: • Review and simplify attributes specifications; all attributes that do not belong to the As Built standard, such as demand, repair and maintenance, health and safety issues, service and financial performance should be removed. These are time related measures and events that are covered by other parts of the standard. Connecting these events and measures to assets is the subject of asset analytics, not the as built standard. | NA | Agreed and action on volume 1. | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. This includes a financial performance component which is designed to reflect the 'customer service centric world' | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 2
1061 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 2. Focus on business standard for assets: • Review and clean the attribute tables – remove all values that are included as they are not relevant. | data | Action on both volumes with feedback from data scientists. | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards |  |  |  | Sector Discussion | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | 1 | [7 empty] | 1 | [17 empty] | More information required for a decision
1062 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 2. Focus on business standard for assets: • Clean the relationship between asset classes, attributes and values. One asset class has to belong to one asset category. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
1063 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 2. Focus on business standard for assets: • Outline a list of core asset characteristics – the whole concept of the standard as vehicle for comparability becomes meaningless if we don’t agree on a few critically important attributes that must be collected. | Mandatory Fields | Optional and industry best practice attributes to be reviewed. This will differ between organisations needs and the granularity of the data available to them. Mandatory will be a minimum for best asset management functions | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Mandatory, Optimal, Optional will be discussed with the sectors | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | More information required for a decision |  |  |  |  | 2
1064 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 2. Focus on business standard for assets: • Our recommendation is to add a section on asset geometry and topology for water networks – but not one that could be mistaken for a specification for GIS applications. This section needs to address the core rules for creating geometric networks and outline the participation of all assets in these networks. | NA | Sufficient info needs to be collected to allow each asset to be identified at the level appropriate for each organisation. No action required. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [17 empty] | No action
1065 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 3. Review publishing formats: • Since all standards are related and are part of the same suite of documents it would make sense for them to be published as related volumes (chapters?) rather than independent books. | Volume Interaction | Statement noted. Action on HR. | Vol 1 - Vol 2 |  | To discuss |  |  |  | Included | Included | This has been reviewed, and a decision to keep as separate documents made - at this time (the documents would be 300+ pages if combined | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 2
1066 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 3. Review publishing formats: • Another approach to publishing standards which would be effective is by using links to look up the list of attribute values. | Volume Interaction | Statement noted. Action on HR. | Vol 1 - Vol 2 |  | The drafts have now had a full publishing edit |  |  |  | Included | Included | Other access toolss will be reviewed before release in July 2017 | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 2
1067 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 3. Review publishing formats: • Think about publishing the data tables in a data view in addition to the document | Volume Interaction | Statement noted. Action on HR. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [17 empty] | More information required for a decision
1068 | Dukessa Blackburn | Auckland family | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Recommendations 4. Remove content that is not related to the business asset data standard: • We strongly recommend that all references to implementation paths, delivery mechanisms and quality control rules be removed from this document. This should be a subject to a separate project/ research due to the variety of business models that can be applied. Unless there is a directive for a centralised implementation of these standards, they remain the responsibility of each organisation and have to be adapted to the particular technology platform. | Implementation | Action on data scientists. | Vol 1 - Vol 2 |  | This is not within the scope of these standards Need to identify where this is being referenced |  |  |  | Noted: no action required | Noted: no action required | Unclear of where there are examples of this | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 2
1069 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | See excel sheet with specific feedback. |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | there is a whole other spreadsheet here for consideration | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
1070 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | Asset class definitions needed: Need clear definition of asset classes. Channels are particularly bad examples; they cover a range of assets with various function and purpose - and badly. Under current structure there is no way to describe sw treatment devices. |  | Action on volume 1. | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be appropriate. Further input will be welcomed Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Noted: no action required | Classifications and types defined in the standards Refer to code lists | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you change your response as it doesn’t acknowledge the point |  |  | updated comment Stormwater treatment devices added in consultation with Auckland City Council during workshops | [9 empty] | More information required for a decision
1071 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | Attribute definitions needed: Many definitions are unclear or missing. Some appear to be database oriented - need to be business meaningful. |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | Please provide specific examples. Further input will be welcomed Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
1072 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | Standard is about structured data, not any information about assets: This standard should cover the data that needs to be captured in as structured way for further analytical and reporting use. Hence all data that has no such value needs to be removed. In complex assets most of the asset specific data is kept in operation manuals and other operation related documentation. |  | Action on volume 1. | Vol 1 |  |  |  | Noted | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | Noted: no action required | Noted: no action required | Volume 1 provides details to the data service providers as well as the asset owners about the specific data required to be captured and provided abouit each project undertaken. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | ok | [12 empty] | No action
1073 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | This is volume one - as constructed assets. Remove all data that is not relevant to as constructed - there are other volumes that this data is described |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | Please provide specific examples. Further input will be welcomed Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
1074 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | Huge number of attributes that are not relevant and not agreed. Need to go back to the workshop discussions and agree how feedback following working sessions will be captured - cannot afford to continue like that. |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | Please provide specific examples. Further input will be welcomed Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
1075 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | Renewal material in pipes. This should be relabeled to say lining material. |  | Action on volume 1. | Vol 1 |  |  |  | noted | Pipes may be renewed by other means than lining as they may be replaced. | Included | Included | Attributes included, lining material included in standards see code lists | General for Pipes | 1 | [7 empty] | 1 |  |  |  |  | suggest you review your response as it doesnt answer the question | we should have a code list for linings? Not answered | [11 empty] | No action
1076 | Stormwater team - Auckland council | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | Missing attributes. Lining material installation data is critical |  | Action on volume 1. | Vol 1 |  |  |  | Under Review | Please provide specific examples. Further input will be welcomed Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
1077 | Watercare | Auckland family | 3-Waters | Vol 1 | General | [5 empty] | See excel sheet with specific feedback. |  | Information to be provided for discussion | Vol 1 | [5 empty] | Noted: no action required | Noted: no action required | Information to be provided for discussion | General |  |  |  | 1 | [8 empty] | 1 | [13 empty] | More information required for a decision

## All Cells (hidden)
Final Version for Review V17 | [23 empty] | 358 | 10 | 179 | 522 | 0 | 0 | 0 |  | 599 | 241 | 231 | 0 | 50 | [18 empty] | 1069
ID | Respondent | Organisation | Standard | Volume | Section nr. V6 | Page number V6 | Paragraph / table V6 | Section nr. V8 | Page number V8 | Paragraph/table V8 | Feedback | Topic | OPUS Comments | Volume | Review Haydn Vol 1 | Review Haydn Vol 1 & 2 | Review Haydn Vol 2 | Review GISSA | Response (GISSA response date) | Status Included, Excluded, Sector discussion, Noted: no action required | Status Included, Excluded, Sector discussion, Noted: no action required from GISSA sheet 11-2 | Final Comments for Publication | Section Reference in Final Version - per Contents page | Included | Excluded | Sector discussion | Noted: no action required | HAYDN | GEORGE | GEORGE & HAYDN |  | Vol 1 | Vol 1 & 2 | Vol 2 |  | Haydn | question for haydn | Haydn Action | action for gissa | gissa comment | pw V1 | ww V1 | sw V1 | Build V1 | pw V2 | ww V2 | sw V2 | Build V2 | follow up action by gissa | Additional Work | Proposed Codelists / Attributes | MW_edits_V2 | HR_edits_V15 | HR_edits_V15 Notes for George
1 | Nic Donnelly | LINZ | Potable water | Vol 2 | Use of spec | III | 3 |  |  |  | a. General feedback from the Stormwater and Potable Water sections should be treated as relevant to Wastewater. | NA | Statement noted, no action required. | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
2 | Nic Donnelly | LINZ | Potable water | Vol 2 | 3.4 | 43 | Data table 3 / 3.10 |  |  |  | The structure of The standard should be “normalised” to take into account common data attributes across all asset classes | Normalisation | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
3 | Nic Donnelly | LINZ | Potable water | Vol 2 | 3.5 | 47 | Code list 13 / A |  |  |  | A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. | Normalisation | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
4 | Nic Donnelly | LINZ | Buildings | Vol 2 | Use of spec | III | 3 |  |  |  | We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. | Data | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [8 empty] | n/a | n/a | n/a | NO ACTION | [5 empty] | No action |  | N/A
5 | Nic Donnelly | LINZ | Stormwater | Vol 2 | Use of spec | III | 3 |  |  |  | The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Normalisation | Data scientist to investigate | Vol 2 |  |  | Completed with Metaconnect |  |  | Included | Included | Completed with Metaconnect | No Specific Reference | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
6 | Nic Donnelly | LINZ | Stormwater | Vol 2 | 3.5 | 50 | Code list 13 / A |  |  |  | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Spatial | Users to decide most appropriate system. | Vol 2 |  |  | George |  |  | Included | Noted: no action required | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  | there is a difference when working with accuracies of 0.00-0.20m suggest this adopt LINZ suggestion possible sector review | [9 empty] | No action |  |  | y | completed | 1 | 1
7 | Nic Donnelly | LINZ | Wastewater | Vol 2 | Use of spec | III | 3 |  |  |  | Should be "coordinate reference system" as in ISO 19111 | Spatial |  | Vol 2 |  |  | George |  |  | Included | Included | Standards are OGC spatial attribution compliant | Use of the Specification | 1 | [9 empty] | 1 |  |  | ok | [12 empty] | No action |  | N/A
8 | Nic Donnelly | LINZ | Wastewater | Vol 2 | 3.5 | 49 | Code list 13 / A |  |  |  | Suggest this is replaced with NZGD2000. WGS84 is not suitable for accurate spatial data as coordinates change with time due to tectonic motion. See http://www.linz.govt.nz/data/geodetic-system/datums-projections-and-heights/geodetic-datums/world-geodetic-system-1984-wgs84 | Spatial | Users to decide most appropriate system | Vol 2 |  |  | George |  |  | Included | Noted: no action required | Adopt LINZ suggestion - to include in standards | Code List 4: Location – Coordinate System |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  | change needed in Vol 2 specs | there is a difference when working with accuracies of 0.00-0.20m suggest this adopt LINZ suggestion possible sector review | [9 empty] | No action |  |  | y | completed | 1 | 1
9 | Nic Donnelly | LINZ | Potable water | Vol 1 | Use of spec | v | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | Noted | not required in this section, covered in later sections 28/2/2017 | Included | Included | not required in this section, covered in later sections 28/2/2017 | Use of the Specification | 1 | [7 empty] | 1 | [17 empty] | No action
10 | Nic Donnelly | LINZ | Potable water | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Horizontal Coordinate System" to distinguish it from the vertical |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed 28/2/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
11 | Nic Donnelly | LINZ | Potable water | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Vertical Datum" since datums can also be horizontal |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed 28/2/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
12 | Nic Donnelly | LINZ | Potable water | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | or vertical datum |  |  | Vol 1 |  |  |  | Under Review | further explanation required 28/2/2017 | Included | Sector Discussion | Updated in draft standards | 1.5 Deliverables |  |  | 1 | [5 empty] | 1 |  |  |  | 1 |  |  | change needed | sector discussion not needed response changed to Included | not needed | not needed | not needed | not needed | [5 empty] | Change made document updated
13 | Nic Donnelly | LINZ | Potable water | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | changed 28/2/2017 precision changed to 3 dec places, will need to ensure spec alignment with this | Included | Included | changed 28/2/2017 precision changed to 3 dec places, will need to ensure spec alignment with this | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
14 | Nic Donnelly | LINZ | Buildings | Vol 1 | Use of spec | 4 | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | Included - addressed from previous comments | 2017-03-20 | Included | Included | Reviewed and Noted for Inclusion | Use of the Specification | 1 | [7 empty] | 1 | [6 empty] | check done |  | not needed | not needed | not needed | not needed | [5 empty] | No action
15 | Nic Donnelly | LINZ | Buildings | Vol 1 | 2.1.2 | 7 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | Included - addressed from previous comments | 2017-03-20 | Included | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 | [6 empty] | check done |  | n/a | n/a | n/a | done | [5 empty] | Change made document updated
16 | Nic Donnelly | LINZ | Stormwater | Vol 1 | Use of spec | v | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | Use of the Specification | 1 | [7 empty] | 1 | [6 empty] | check done |  | not needed | not needed | not needed | not needed | [5 empty] | No action
17 | Nic Donnelly | LINZ | Stormwater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Horizontal Coordinate System" to distinguish it from the vertical |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | 1 | [7 empty] | 1 | [6 empty] | check done |  | done | done | done | done | [5 empty] | Change made document updated
18 | Nic Donnelly | LINZ | Stormwater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Vertical Datum" since datums can also be horizontal |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | check done |  | done | done | done | done | [5 empty] | Change made document updated
19 | Nic Donnelly | LINZ | Stormwater | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Included | Included | Reviewed and Noted for Inclusion | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 | [6 empty] | check done |  | done | done | done | done | [5 empty] | Change made document updated
20 | Nic Donnelly | LINZ | Wastewater | Vol 1 | Use of spec | v | 2 |  |  |  | Should be "coordinate reference system" as in ISO 19111 |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | Use of the Specification | 1 | [7 empty] | 1 | [6 empty] | change needed |  | not needed | not needed | not needed | not needed | [5 empty] | No action
21 | Nic Donnelly | LINZ | Wastewater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Horizontal Coordinate System" to distinguish it from the vertical |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
22 | Nic Donnelly | LINZ | Wastewater | Vol 1 | 1.5 | 3 | Validating data submission table |  |  |  | Should label this "Vertical Datum" since datums can also be horizontal |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | 1.5 Deliverables | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
23 | Nic Donnelly | LINZ | Wastewater | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | There is now a new official datum, New Zealand Vertical Datum 2016, which is more accurate and should be used instead of NZVD2009. |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | 2.1.2 Projections and Datums | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | change needed |  | done | done | done | done | [5 empty] | Change made document updated
24 | Nic Donnelly | LINZ | Wastewater | Vol 1 | Glossary | 112 | Glossary table |  |  |  | Update to NZVD2016 |  |  | Vol 1 |  |  |  | Noted | Commented in potable water section 10/3/2017 | Included | Included | Updated in draft standards | Glossary | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
25 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Our first point of submission is that in our opinion the standards should be titled "Asset Data Standards" not metadata standards. We feel that metadata is information about data while these standards are defining the actual data requirements. | Metadata terminology | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Many participants have raised the point. IIMM defines metadata in both ways i.e.. "metadata goes in two forms. Structural metadata is detail particular to the asset in question, the physical attributes. Descriptive Metadata is particular to describing the content of the asset. Metadata standard when applied, are used to impose uniformity and quality standards on data | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action
26 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The Standard is written as a standard in some places and a specification in others. Our opinion is that the standard should be a standard and specifications about water suppliers' implementation of the standard (within the context of asset management maturity and aspirations) should be decided by themselves within the framework of the Asset Data Standard. As an example, the document is very prescriptive in the way data is to be submitted. In our opinion, this is not in line with the intent of the standard and in our case the data submission methods prescribed are a step backwards, as we have far more sophisticated systems for receiving and validating submitted data. How data is submitted by consultants should be the subject of a separate document (or Appendix) in the form of draft or default/minimum specification for water suppliers who are looking for this level of detail. | Implementation | Statement noted. It is suppose to be a standard and not a specification. Vol 1 to be reviewed. No action required for Volume 2. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action
27 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Although specifically excluded from the submission request, it is important to understand how these standards will likely be implemented, in particular whether the standards are to be mandatory. If the standards in their current form (as published) were to be adopted as mandatory, our opinion is that they would potentially result in more confusion and ambiguity in the water industry than they are trying to solve, and our submission includes numerous suggestions that would improve this. | Mandatory Fields | Statement noted. To be considered in business case. No changes required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. To be considered in business case. No changes required. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action |  |  |  |  | 1 | 1
28 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | There is evidence of quality assurance checking omissions in some of the documents. This submission does not attempt to deliver this level of basic quality assurance checking. For example: generic text "cut and pastes" not corrected for the relevant activity e.g. inappropriate references to wastewater in the stormwater metadata standards disjointed page numbering identified in the stormwater metadata standard | QA | Agreed. Action: Quality assurance will be undertaken in following releases | Vol 1 - Vol 2 |  | The drafts have now had a full publishing edit |  |  |  | Included | Included | The drafts have now had a full publishing edit | General | 1 | [7 empty] | 1 | [17 empty] | Changes made documents updated |  | N/A
29 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission While a very positive start, we believe that the draft standard has not fully addressed the intent as outlined above. In particular, recognition of the various levels of sophistication are not adequately addressed, with too many data fields identified as mandatory, and little attention given to discretion or guidance based on the level of asset management sophistication being targeted. | Mandatory Fields | Action. Mandatory fields to captured at a minimum levels. Mandatory fields to be looked at to remove non-essential attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The adoption of extents of fields is determined ny each organisation | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  | change comment as this is not the intent to allow variations more importantly need to address level of attributes to be collected | [9 empty] | No action
30 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Has the cost of data acquisition and management vs. benefit been considered? There are a large number of "Mandatory'' fields. This links back in to a common theme in this submission that the data requirements need to link back to the level of asset management maturity targeted. To back populate all the data fields that are noted as "Mandatory'' will have significant national cost implications, and will need to be associated with specific improvement plans and prioritised cost I benefit investment plans. Even as a relatively advanced asset management practitioner Tauranga City Waters would approach the mandatory population of "missing" data fields with caution, noting that even the scoping of such a data collection effort is in itself a reasonably large undertaking. | Mandatory Fields | Action. Mandatory fields to captured at a minimum levels. Mandatory fields to be looked at to remove non-essential attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The extents of attribute fields collected will be determined by each organisation | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  | change comment as this is not the intent to allow variations more importantly need to address level of attributes to be collected | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action |  |  | y | completed
31 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission The summary of the introduction to the Wastewater Vol. 1states the main objective of the standard is "to provide information to the consultants who will be dealing with any public asset owner. This document outlines the specific requirements for the submission of all digital data that relates to any newly constructed". In this regard we believe that: Providing information to consultants is not the main objective, but is a positive secondary objective of the standards. If the standard in its current form were given to 10 different consultants, asset owners would receive 10 different and inconsistent datasets due to differences of opinion or interpretation. This is are outcome that standards should try to avoid. The standards need to consider and explain the degree of aggregation of data that is being targeted, and how this is achieved, by suitably fully detailed defined asset grouping and asset class I type definitions (the as yet unpublished Code lists may provide further guidance). | General | Agreed. Rewrite "In Summary", to reflect public asset ownership. Action on volume 1. | Vol 1 - Vol 2 |  | George |  |  |  | Noted: no action required | Noted: no action required | These stadards are set at the lowest level of granularity for analytical purposes. The sector / organisation will determine the level of aggregation required for each circumstance | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [13 empty] | No action
32 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | STANDARDS OBJECTIVES We understand the intent of the standards are to: Provide a standard for asset data to support data creation, capture, storage and analytical capabilities for evidence based decision making Create a basis for standardised and harmonised data for evidence based investment decision making across public assets in New Zealand Recognise various levels of sophistication in data and provide relevant attribute guidance in this regard Submission Certain sections of the standard allude to future sections that will outline intervention methodologies, decision making analytics and asset management frameworks. This would appear to be outside the scope of a metadata standard, and in our opinion requires further scope discussion with the industry prior to proceeding. | NA | No action required, refers to future volumes. Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Future work is yet to be determined | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
33 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | CONSISTENCY Submission Inconsistent terminology and definition has been used through the documents. This creates uncertainty, miscommunication opportunities and outright confusion. There are instances of "Asset Groups", "Asset Categories", "Asset Classes", "Asset Types" cited, sometimes capitalised, sometimes not. What is the definition of each and how do they relate to each other. At times Asset Groups are referred to implicitly in a paragraph that is defining/discussing Asset Classes. Asset Class seems to be the same thing as Asset Category, although this is not clear. For example in Section 1.7 - Hierarchy, there is an "Asset Class" defined in 1.7, is this the same as "Asset Category" in 1.8? There is poor (unexplained?) asset management logic to some of the asset classes cited when compared to others. | NA | Asset categories are defined in Volume 1, changes can be transferred to Vol 2 as required. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | The classification has been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | 1 | [9 empty] | 1 |  |  | is this meant to say defined in the standard? | Yes , and changed |  |  | done | done | done | done | [5 empty] | Change made document updated |  | N/A
34 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission Asset Categories need better definition. All Code lists need to be published for comment at the same time as the rest of the standard. We have many questions, queries and uncertainties about asset classes/types which could very well be answered with a set of Code lists, so it is disappointing that they have been left out of the first draft. We have included some of the sorts of uncertainties we have in a separate section of this submission headed "DATA". | NA | Asset categories are defined in Volume 1, changes can be transferred to Vol 2 as required. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | The classification has been defined in the Standards Code Lists included | General | 1 | [9 empty] | 1 |  |  | is this meant to say defined in the standard? |  |  |  | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action |  | N/A
35 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission The standard should include further description of asset groups, classes and types to explain what they do and what they do/do not include, and what level of disaggregation or componentisation is required based on level of asset management maturity using the International Infrastructure Management Manual as a guide. Many asset managers group assets in different ways and include or exclude "components" based on personal preference, asset database capabilities, asset management maturity/objectives, data management cost/benefit, financial valuation constraints or a whole range of other factors. In our opinion the key to the asset data standards is to provide asset managers access to a recognised and accepted source of guidance to design asset registers safe in the knowledge that industry data aggregation and comparison with other 3 waters asset owners can be made on a like for like basis. | NA | Asset group, class not mentioned in Vol 2. Asset class only mentioned in Chapter 1. Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | The classification has been defined in the Standards | General | 1 | [9 empty] | 1 |  |  | is this meant to say defined in the standard? | [12 empty] | No action |  | N/A
36 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission It is suggested that groups and classes should be named as such to avoid confusion e.g. "Instrumentation Group", "Instrument Class", "Electrical Asset Group", "Electrical Equipment Class". (As a matter of interest, both "Electrical Asset" and "Mechanical Asset" have an "Equipment" class. How does this work to close out ambiguity and further questions i.e. which "Equipment" is grouped to "Electrical" vs "Mechanical" for consistent aggregation at industry/national level?) An example 3 Waters Schema for practical implementation of the standards at various levels of ;;::;set management :;sophistication (advanced, intermediate, basic} would be a useful reference. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards Code Lists included | General | 1 | [9 empty] | 1 |  |  | ok |  |  |  | naming resolved & codelists added | naming resolved & codelists added | naming resolved & codelists added | naming resolved & codelists added | [5 empty] | No action |  | N/A
37 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission Network Type does not include a "Communications" network that may encompass and service all the network types suggested. For example the water and wastewater and stormwater networks may all be serviced by a Wide Area Network (WAN) communications network, yet the way the standard is currently structured, these assets will need to be grouped to one of the 3 waters networks. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | Noted: no action required | Noted: no action required | In the context of these standards Network applies to one of the potable, waste or stormwater networks. The purpose of this documentation is to identify the various assets and their data requirements. Each and every organisation can apply their specific classifications after the data is received. | General for Hierarchy |  |  |  | 1 | [6 empty] | 1 |  |  | ok |  |  |  | no action | no action | no action | no action | [5 empty] | No action
38 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | HIERARCHY Submission The standard is very spatially focussed - particularly GIS 2D. In reality for many assets (e.g. much/elec/instr) spatial representation offers little value to the management of the asset vs the data capture I maintenance cost. Furthermore, the standard is specifying significant additional spatial information to be collected/populated e.g. polygons to represent asset extents rather than (or in addition to) just lines or points. While nice to have, it is unclear what the value of this additional work load will bring. | Spatial | Action on volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The adoption of extents of fields is determined by each organisation | General for Hierarchy |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
39 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Data Uncertainty - there are no attribute fields relating to data uncertainty. For example in some cases a construction date may be assumed based on a certain piece of evidence with known uncertainty (say a "for construction" drawing dated 1965 leads to an assumption of a 1965 install date - when in reality this could be sometime after 1965). Data uncertainty attributes should use International Infrastructure Management Manual for guidance. | Data | Agreed. Action: Include confidence level in each schema. | Vol 1 - Vol 2 |  | Data quality is an analytical output - see for example the Harmonic data maturity scale |  |  |  | Excluded | Excluded | Data quality is an analytical output - see for example the Harmonic data maturity scale | No Specific Reference |  | 1 | [6 empty] | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
40 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Data completeness - it would be useful to have guidance on how to calculate asset register data completeness for various levels of asset management maturity, in accordance with the standard for industry/national aggregation. | Mandatory Fields | Statement noted. Out of scope. For asset owners to determine the amount of data they collate. | Vol 1 - Vol 2 |  | Data quality is an analytical output - see for example the Harmonic data maturity scale |  |  |  | Noted: no action required | Noted: no action required | Data quality is an analytical output - Will dicsuss options for determining data quality e.g. Harmonic data maturity scale | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | research by GISSA for our info only |  | no action | no action | no action | no action | [5 empty] | No action |  |  |  |  | 1 | 1
41 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Valuation information - the following valuation information needs to be captured (Vol 2 of the various standards) - Replacement value, Book Value and Annual Depreciation. Values for Insurance also required separately namely Insurance Replacement Value, Indemnity Value and Residual Value | Financial Performance | ODRC, ORC and RC is already present in the table in 10.33. use of this attribute to be clarified in measurement of financial performance (Ch 5.3.4). | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | ODRC, ORC and RC is included | Code List 47: Financial Performance Metrics |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  | no action | no action | no action | no action | [5 empty] | No action |  |  |  |  | 1 | 1
42 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Datum - NZ Vertical Datum 2009 has been used in the draft standard. Many water suppliers will use different datums to this (including ourselves). Furthermore many Councils use a different datum for their other assets (e.g. Parks), so such a change will have major change management implications and risks for many organisations. We do not believe specification of a specific datum is required at a national level for the 3 Waters data set, and that it is more appropriately addressed at the regional or sub-regional level. The asset data standard should however define that a Datum is required. | Spatial | Action for Volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | Noted: no action required | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. | 2.1.2 Projections and Datums |  |  |  | 1 | [6 empty] | 1 |  |  | ok |  |  |  | no action | no action | no action | no action | [5 empty] | No action
44 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Default date 01/04/1800 - this is not a valid MSExcel date (i.e. will not work in MSExcel). A lot of data analytics is done in MSExcel, this is just a matter of fact, and is unlikely to change in the short term. It is suggested that 31/12/9999 (or similar) is used as the default date. | Data | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Suggestion to be adopted in all documents in all tables. 26/3/2017 | Included | Included | Adjustment will be made to standards | General | 1 | [9 empty] | 1 |  |  | ok |  | change needed in docs |  | done | done | done | done | [5 empty] | Change made document updated |  | N/A
45 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission 10 characters is restrictive for field values (Code list Reference). Fields should hold the actual values, not just codes that represent those values. For example - Proj_Type (Project Type) max length is 10 characters, but example "Capital Works" is 13 characters. 10 characters for a Project Type is very short. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. |  |  |  | Noted: no action required | Noted: no action required | The challenge to be systems agnostic is some systems to not allow greater than 10 characters. This accommodates all known systems. | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
46 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Unique_ID (Unique Identifier) is quite short at 20 characters and there is potential benefit for longer IDs, particularly when using 'smart' Asset IDs for things like mechanical assets where the IDs refer to site, location, asset type, etc. It is also noted that if the standard is written "for consultants", in most cases, the unique ID will not be provided by the consultant, but more likely by the asset owner. The consultant/builder will however have to uniquely identify the asset for communication purposes (even if it is a temporary and I or transitional ID). | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | In this context the unique id is created by the consultant as an audit trail before and after incorporation into asset owners systems | no action | no action | no action | no action | [5 empty] | No action
47 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Photo_Ref (Photographic reference) shouldn't be "Mandatory" for all asset types, e.g. for buried pipeline assets is the expectation that each metre, each length, each joint, each fitting is photographed? Maybe "Optional" is more appropriate for some assets. | Mandatory Fields | Agreed. Action required in both volumes. | Vol 1 - Vol 2 |  | George |  | Under Review | To be discussed with the TWG 25/03/2017 | Included | Included | Photographic Evidence is an optional attribute | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  |  |  | noted | noted | noted | noted | [5 empty] | change made document updated |  | N/A
48 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Hlth_Sfty (Health And Safety Issues) should be a "Mandatory" value on all assets, even if the default is "No specific requirements", as this means it will be thought about for all assets and not just skipped over. | Mandatory Fields | Agreed. Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | 2017-03-25 | Noted: no action required | Noted: no action required | No specific requirements attribution will be replaced with 'Standard H&S Requirements Code List proposed | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | what are you saying? | This a code list of its own e.g confined space certification, working at heights etc. | make mention of change request create codelist and change field to point to code list | create sample c odelist | [8 empty] | request documented | New Code List proposed | Health & Safety Type
49 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Length_m (Length) and Width_m (Width Metres) are both required, however "if the asset is circular please populate [width_m] with the diameter" - what should then be entered into Length_m? - This ambiguity is a simple example of the uncertainty these standards should eliminate by providing the complete guidance and commentary. | Mandatory Fields | Agreed. Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Clarification to be provided for all fields that have this requirement in all documents. 26/3/2017 | Included | Included | Adjustment will be made to standards | General | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | done | done | done | n/a | [5 empty] | Change made document updated |  | N/A
50 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Area of Work" is just a spatial area to link to through attribution, not an asset. It is starting to delve into asset management, capital works and business planning processes, should this be part of an Asset Data Standard? This extension of the Asset Metadata Standard is more applicable to a development code type specification. | Spatial | Action for Volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | The area of work boundary is submitted at practical completion. It is only intended to record the area where works have been completed and will hold the common information about the project the project | Included | Included | Area of work is required for Vol 2 Adjustment will be made to standards - For analytical purposes | General | 1 | [7 empty] | 1 |  |  |  |  | why added to Vol 2 ? | For analytical purposes Have added 'geographical units' code list | [11 empty] | No action |  | ?
51 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Location - none of the standards record whether the asset is located in the carriageway, berm, private property (unless this is included in Code lists?). | Spatial | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | GIS queries should be able to identify this in 3 waters. Location is identified in buildings. | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
52 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Retaining Structure Asset Class - what is this? It is not the actual structure in many cases (e.g. a stormwater pond will have an "Embankment" asset). The name of the Retaining Structure Asset Class is open to misinterpretation and consideration should be given to a more appropriate name I description. For example the asset type in this class could include stormwater soakage pits, treatment devices such as rain garden, tree pit, silt trap, gross pollutant trap (or are these just grouped as treatment devices?). Many questions that the Code lists may help eliminate. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under review | Have the code lists been distributed? 26/3/2017 | Included | Included | Code lists included in standards | 2.3.3 Retaining Structure | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | NOTED codelist added | n/a | NOTED codelist added | n/a |  |  |  |  | gauge input from next review | No action |  | N/A
53 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Pump" asset - the attributes are a mix of location and asset attributes e.g. impeller details and then asset connections, even going into tanks capacities and compressor details (aren't these last two separate asset classes?, they certainly would be in businesses aspiring to advanced asset management). Is there any benefit/value in recording the asset connections as attributes? Design life can also be run hours rather than years. This takes some analytics to convert to Remaining Useful Life based on current demand etc. but this is where Tauranga City Council is heading with our "Pump" asset class management. | Condition | 1. Data scientist feedback 2. agree, yes. Action on volume 1. 3. agree, we can have design life unit as a new field. Action on volume 1 and 2. | Vol 1 - Vol 2 |  | To discuss |  |  |  | Sector Discussion | Included | Attributes for analytics on duty etc. included - to be discussed Code lists developed for variable durations - to be discussed | General for Pump | 1 | [7 empty] | 1 | [7 empty] | please review yur response | [9 empty] | No action |  | ? | y | completed
54 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Valves" - this ls a separate asset class yet ls also described under the "Mechanical Equipment" asset class. I.e. lack of consistency and ambiguity creeping in. Size attribute - mixes ID (Internal diameter) and DN (Nominal diameter). Have all valves across all time had the same ID and DN? You cannot have some fields recording ID and some DN - what is it? There needs to be an additional attribute for Function or Purpose - e.g. a RSV can be an Isolation Valve or a Scour Valve - asset managers need to be able to sort the different functions. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under review | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | Sector Discussion | Sector Discussion | There are a number of elements in this discussion. Firstly assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. Discussion to be held regarding appropriate size attributes for the specific asset types ? Attribute field included for function/purpose called "Purpose" | General for Valves |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
55 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Cable Asset - why are we capturing the data at the level of mandatory detail suggested? At a treatment plant there are literally thousands of cables. The way the standard is written each one needs to be captured (spatially!). Drawings capture the cable details and will need to be referred to during field maintenance. There is little asset management benefit of capturing each exposed cable individually except in exceptionally advanced asset management systems (buried cables - particularly in public environment are a different story). Certainly higher priority asset classes than "Cable Asset" have been ignored. | Mandatory Fields | Action on volume 1. | Vol 1 - Vol 2 |  | These standards are not about Treatment Plants |  |  |  | Noted: no action required | Noted: no action required | These standards are not about Treatment Plants | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | no action | no action | no action | no action | [5 empty] | No action
56 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Why is a "Fan" grouped with "Electrical Equipment" yet a pump with a motor grouped with "Mechanical Equipment"? We need to see the Code lists to understand the full extent of the Asset Type I Class groupings. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Have the code lists been distributed? Can be assigned as sector discussion This detail was identified at the previous workshops and determined to be appropriate . 26/3/2017 | Included | Included | Code lists included in standards | General Equipment | 1 | [7 empty] | 1 |  |  |  |  | previoulsy missed | Code lists included | change needed in docs |  | NOTED codelist added | NOTED codelist added | NOTED codelist added | NOTED codelist added |  |  |  |  | gauge input from next review | Gauge input from next review |  | N/A
57 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Electrical Assets", "Mechanical Assets", "Instrumentation". For these asset class groupings the generic commentary within the standard are poor with regard choices, pros and cons and asset management maturity. Tauranga City Council would apply the following additional attributes: IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | To be reviewed by the TWG for consideration of inclusion. 26/03/2017 | Sector Discussion | Sector Discussion | Review with the sector | General for Electrical, Mechanical, Instruments |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | New attribute IP rating ingress protection Insulation class Efficiency rating Frame size Motor wiring RPM Rated Power (kW) Weight (kg) H&S aligning correct lifting gear for maint, hiab/cranes Rated Current -to set overloads, denotes wear Motor Position -vertical, horizontal - bearing logic Impeller curve code Impeller material Operational/redundancy strategy i.e. run to fail. | N/A
58 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Instruments" - We have concerns with including domestic water meters within the instrument asset class. We believe that domestic water meters are such an important asset for metered water suppliers that they should have their own asset class. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | Noted: no action required | Noted: no action required | Assets that have the same attribute requirements were grouped to enable a reationalisation of tables. This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as a discrete asset class in their systems once the asset data is provided. | 2.7.1 Instruments |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
59 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission "Pipe", "Fittings" - No information on the degree of "fittings" to be recorded. Is it mandatory to record all fittings, what about repairs? Similar for "Pipes", does the standard envisage pipe repair lengths during reactive maintenance to be recorded? - No guidance or commentary on data requirements. Although preferable to maintain single segments access point to access point, there are occasions where pipe is 2 separate assets between access points. Note when subdivisions may be connected up. The pipes may be installed years apart, of the same material but we record as 2 assets. The material may or may not be the same and even if the same manufacturing standards may change year to year. Manholes may also be removed. Can occur on older sections of pipe | Granularity | Agreed. Repair lengths to be recorded. A quantification of repair required. This feedback was requested from TWG but was not returned. Granularity question. Access point issues action on volume 1 | Vol 1 - Vol 2 |  | George |  | Under Review | Have the code lists been distributed? Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. 26/3/2017 | Included | Included | Code lists included in standards Otherwise other comments noted Record Repair lengths - yes - does not mean that a new segment needs to be created This will be determined by each asset owner. | General for Pipes | 1 | [7 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | NOTED codelist added | NOTED codelist added | NOTED codelist added | n/a |  |  |  |  | gauge input from next review | Gauge input from next review |  | N/A
60 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Cost information - is it really necessary to record to 2 decimal places? | Financial Performance | No action required. Put .00 if no decimal is required. | Vol 1 - Vol 2 |  | Unit rates are given as such by Valuation Reporting standards |  |  |  | Noted: no action required | Noted: no action required | Unit rates are given as such by Valuation Reporting standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
61 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Potable Water Vol 2 - P 69, Ref 7.08. - should read "Environmental" and not "Consequence Rating Overall" | QA | Agreed. Action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Reviewed and Noted for Inclusion | Code List 53: Environmental Outcomes Rating | 1 | [7 empty] | 1 | [7 empty] | check if done | [9 empty] | No action |  | ? | y | completed | 1 | 1
62 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Potable Water Vol 2 - Table 4 pp 13 - % not included as a data type in this table | QA | Agreed. Action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Reviewed and Noted for Inclusion | Data Table 4: Demand Attributes & Code List 33: Demand – Measure | 1 | [7 empty] | 1 |  |  |  |  | previously missed | Code lists included |  | check if done | [9 empty] | No action |  | ? | y | This is tables you provided in the 'introduction'. | 1 | 1
63 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Potable Water Vol 1 - P14 - Common Attribute Set, Tauranga City Council also captures Catchment Area /Demand Management Area (OMA). | Demand | Statement noted. This is captured in "Demand" schema, Vol 2. Catchment area is more design information and not necessarily required. | Vol 1 - Vol 2 |  | to discuss - catchment name reference name? |  |  |  | Sector Discussion | Sector Discussion | Reviewed and Noted for Inclusion | General for Common Attributes |  |  | 1 | [5 empty] | 1 |  |  |  |  | will the contrator know this at time of capture? Possibly for capital projects but not likley for subdivision developments Council can add post supply of data | For analytical purposes Have added 'geographical units' code list updated comment not answered | change needed |  | n/a | n/a | n/a | n/a | [5 empty] | New attribute proposed | New attribute Catchment Area /Demand Management Area (OMA) | codelilsts added
64 | Bryan Everitt | Tauranga City Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | DATA Submission Stormwater Vol 1- pages 95-96 - Mechanical Equipment Attribute Table, there is a problem with the data entry in this table which appears scrambled. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | noted | Resolved in new version. 26/3/2017 | Noted: no action required | Noted: no action required | resolved in updated version | 2.5.1 Equipment |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok |  | change needed in docs |  | done | done | done | n/a | [5 empty] | Change made document updated
65 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 2 | Global Asset Metadata Schemata |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. |  |  | Vol 1 | Add Rigid and Flexible to code list |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Rigid and Flexible to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | document request | Response changed to Sector Discussion | [8 empty] | document request | New attribute proposed | Rigid or Flexible as option
66 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 3 | Risk |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 | [13 empty] | More information required for a decision
67 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 3 | Design Performance |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Deflection testing to code list testing type - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | More information required for a decision
68 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 4 | Volume 3 - 1 |  |  |  | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... |  |  | Vol 1 | AddCCTV & Laser Profiling testing to code list testing type |  |  | Haydn | 2017-03-14 | Included | Included | AddCCTV & Laser Profiling testing to code list testing type | General | 1 | [7 empty] | 1 | [17 empty] | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling
69 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | Sector Discussion | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.7.1 Instruments | 1 | [7 empty] | 1 | [6 empty] | document request | Response changed to Sector Discussion | make mention of change request | make mention of change request | make mention of change request | [6 empty] | New attribute proposed | Installer of Asset
70 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 |  |  |  | INCLUDED - Addressed from previous comments | 2017-03-14 | Sector Discussion | Included | Reviewed and Noted for Inclusion | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | Vol2 ? | Haydn please review | [9 empty] | More information required for a decision |  |  | y | Updated comment
71 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. |  |  | Vol 1 | Add Table |  |  | Haydn | 2017-03-14 | Included | Included | Add Table | General | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | GISSA to ADD table | add table | add table | add table | ?? | [5 empty] | New Code List entry for Condition Assessment Type proposed | Deflection Test
72 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation Format Instructions |  |  |  | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. |  |  | Vol 1 | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) |  |  | Haydn | 2017-03-14 | Noted: no action required | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
73 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Con_Ass_T |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | 1 | [7 empty] | 1 | [16 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
74 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Photo_Ref |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Add Compaction and Deflection testing to code list testing type | 2.1.10 Common Attributes | 1 | [7 empty] | 1 | [16 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation
75 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.1 | 53 | Access Chamber Attribute & Validation File Format Instructions Photo_Ref |  |  |  | Deflection Test result |  |  | Vol 1 | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | 2017-03-14 | Included | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.1 Access Chamber | 1 | [7 empty] | 1 | [17 empty] | New Code List entry for Condition Assessment Type proposed | Compaction Test
76 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.1 | 55 | Access Chamber Attribute & Validation File Format Instructions Cov_Type |  |  |  | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not) |  |  | Vol 1 |  |  |  | George/Haydn | If we agree on these then recommend ratification after documents are distributed. 14/03/2017 | Sector Discussion | Sector Discussion | Sector Discussion - intent to include in standards | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 |  |  |  |  | do we need more information before including in standards? | Changed final comment | make mention of change request | [9 empty] | request documented | New attribute proposed | Frame and Cover Class Standard of Manufacture NZS Joint Seal Type Safety Access limit (or not)
77 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.1 | 56 | Access Chamber Attribute & Validation File Format Instructions Cov_RL |  |  |  | Seal Access Safety |  |  | Vol 1 |  |  |  | George/Haydn | If we agree on these then recommend ratification after documents are distributed 14/03/2017 | Sector Discussion | Included | This a code list of its own e.g confined space certification, working at heights etc. | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 |  |  |  |  | do we need more information before including in standards? | cant this be part of the H&S coment? | make mention of change request | [9 empty] | request documented | New Code List & entries proposed | Health & Safety Type
78 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.3 | 69 | Fittings Attribute & Validation File Format Instructions Material |  |  |  | Manufacturer Manufacturing Standard Third Party QA Accreditation |  |  | Vol 1 | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Manufacturer included Consider Manufacturing Standard Third Party QA Accreditation | 2.4.3 Fitting | 1 | [7 empty] | 1 | [17 empty] | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
79 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 72 | Pipe Attribute & Validation File Format Instructions Des_Life |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for stormwater applications. |  |  | Vol 1 | Add Rigid and Flexible to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | Add Rigid and Flexible to code list | 2.4.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Haydn please explain how these will be included changed to Sector Discussion | [8 empty] | request documented | New attribute proposed | Rigid or Flexible as option |  | y | These are a code we need to add in the 'materials section'
80 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 73 | Pipe Attribute & Validation File Format Instructions Photo_Ref |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing / Laser Profiling / Compaction results to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
81 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 75 | Pipe Attribute & Validation File Format Instructions Pshape |  |  |  | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test |  |  | Vol 1 | Add Deflection Testing / Laser Profiling / Compaction results to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | Additional entries included in Code list Condition Assessment Type |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
82 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 75 | Pipe Attribute & Validation File Format Instructions Pshape |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing / Laser Profiling / Compaction results to code list |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection test Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
83 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 77 | Pipe Attribute & Validation File Format Instructions Instl_Mthd |  |  |  | Rigid material standard and QA Separate Flexible material standard and it's QA |  |  | Vol 1 | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | Add Rigid Material Std and its QA and Flexible Material Std and its QAas an attribute | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Haydn please explain how these will be included changed to Sector Discussion | [8 empty] | request documented | New attribute proposed | Rigid material standard and its QA Flexible material standard and it's QA |  | y | Code list to materials type
84 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 78 | Pipe Attribute & Validation File Format Instructions Haunching |  |  |  | Foundation strength pre-install Compaction strength per NZS4566.2 |  |  | Vol 1 | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Included | Included | Add Compaction Testing result to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.4.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
85 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 78 | Pipe Attribute & Validation File Format Instructions Backfill |  |  |  | Compaction strength per NZS4566.2 |  |  | Vol 1 | More information required for a way forward |  |  | Haydn | Is this to be provided by engineers? 14/03/2017 | Sector Discussion | Included | More information required for a way forward | 2.4.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | More information required for a decision |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
86 | Adrian Hynds | Hynds Group of Companies | Stormwater | Vol 1 | 2.4.4 | 78 | Pipe Attribute & Validation File Format Instructions Manu |  |  |  | Third Party QA for pipe material manufacturer |  |  | Vol 1 | Third Party QA Accreditation to code lists |  |  | Haydn | 2017-03-14 | Sector Discussion | Included | Third Party QA Accreditation to code lists | 2.4.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | New attribute & associated Code List proposed | Third Party QA Accreditation Third Party QA Accreditation pick list |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
87 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 2 | Global Asset Metadata Schemata |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. |  |  | Vol 1 |  |  |  | George/Haydn | I get what is being said and see this as a conversation for appropriate design and construction practice to mitigate risk. I also see this as education for the industry that could be provided by companies like Hynds. What if this was the start of an educational series of seminars/webinars etc ? 10/3/2017 | Included | Included | Standards includes the ability to record the rigid and frlexible pipe options - education will follow in due course | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  |  | do you want us to include new attributes? Wouldn’t this be defined by the pipe material and then added as a code? | Yes no change to comment Pipe Material not defining attribute | same as 66 | same as 67 | same as 67 | same as 67 | same as 67 |  | n/a | n/a | n/a | n/a | Make sure request documented | New attribute proposed | Rigid or Flexible as option
88 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 3 | Risk |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection Testing to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
89 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 3 | Design Performance |  |  |  | Deflection testing of flexible pipelines are not occurring according to Part 2 of NZS New Zealand Standard 4566. |  |  | Vol 1 | Add Deflection Testing to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
90 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 4 | Volume 3 - 1 |  |  |  | ....CCTV camera assessments or laser profiling deflection testing (of all forms of flexible pipelines).... |  |  | Vol 1 | Add CCTV & Laser Profiling testing to code list testing type |  |  | Haydn | 2017-03-10 | Included | Included | Add CCTV & Laser Profiling testing to code list testing type | 2.3.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | CCTV Laser Profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
91 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table for "Instruments Attribute & Validation File Format Instructions" A record is needed to also include: Designer of Asset Manufacturer of Asset Installer of Asset Currently the table only includes the "Manufacturer of the Asset" |  |  | Vol 1 |  |  |  | George/Haydn | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | Included | Included | Reviewed and Noted for Inclusion Designer of Asset covered in Project Attributes table in the "Design_Co" field | 2.6.1 Instruments |  |  | 1 | [5 empty] | 1 |  |  |  |  | is there any action on our part? | Yes build a code list | make mention of change request manufacr=turer exists designer ? Installer ? Installer warranty ? | [9 empty] | request documented | New attribute proposed | Installer of Asset
92 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.6 | 5 | Volume 5 |  |  |  | Table also states "Photographic Reference" Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing/Laser Profiling result to code list |  |  | Haydn | isnt this part of the construction phase and recorded? 10/3/2017 | Included | Included | Add Deflection Testing/Laser Profiling result to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 | [7 empty] | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
93 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 1.7 | 1 | 1 |  |  |  | Missing table: Attribute & Validation File Format Instructions: Condition Assessment Type. Needs a reference to Deflection Test result from as-built on site. |  |  | Vol 1 | Add Table |  |  | Haydn | 2017-03-10 | Included | Included | Add Table | 1.7 Heirarchy | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | [9 empty] | Create tabel and add to codelist and pivot table | Create entries Desktop Visual cctv laser etc
94 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation Format Instructions Des_Life |  |  |  | There is not a link between the intention to achieve a design life and the choice of pipeline materials and the adoption of the installation and inspection standards. Pipeline materials have varying design life parameters. Non use of installation QA requirements then reduces the ability to achieve the design life. We need to note the QA Deflection Test result after installation for flexible pipelines per requirements of NZS4566.2. Design is to be performed to NZS4566.1, including the link with pipe yield, material type, stiffness. Needs link to installation compaction tests, installation layer compaction tests, post installation deflection tests, and optional 1-year post deflection tests. |  |  | Vol 1 | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) |  |  | Haydn | 2017-03-10 | Noted: no action required | Noted: no action required | This is not within the remit of Vol 1 & 2 (but we agree with the sentiments) | 2.1.10 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
95 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Comments |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-10 | Included | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
96 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation Format Instructions Photo_Ref |  |  |  | Flexible Pipe: Compaction Tests Deflection Test post installation |  |  | Vol 1 | Add Compaction and Deflection testing to code list testing type |  |  | Haydn | 2017-03-10 | Included | Included | Add Compaction and Deflection testing to code list testing type | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Compaction Test Deflection Test post installation |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
97 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 44 | Pipe Attribute & Validation File Format Instructions Des_life |  |  |  | Design Life - Pipeline types need to be defined separately as Rigid and Flexible. Currently the industry does not understand the differences. The separate standards for each material have a corresponding different installation standard. There are different inspection and QA requirements for each. The designers, installers, auditors/inspectors do not understand the difference. They are being buried the same way and risk on structural failure exists now that diameters of new pipeline materials are being allowed for wastewater applications. |  |  | Vol 1 | Add Rigid and Flexible to code list |  |  | Haydn | 2017-03-10 | Sector Discussion | Included | Add Rigid and Flexible to code list | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | make mention of change request | changed to sector discussion | [8 empty] | request documented | New attribute proposed | Rigid or Flexible as option
98 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 44 | Pipe Attribute & Validation File Format Instructions Photo_Ref |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing/Laser Profiling result to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type proposed | Deflection testing Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
99 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 48 | Pipe Attribute & Validation File Format Instructions PShape |  |  |  | Need to include: Installation QA of soil strength and compaction per NZS4566.2. Foundation Strength Compaction Strength in notified layers Deflection Test |  |  | Vol 1 | haydn |  |  | Haydn | 2017-03-10 | Sector Discussion | Included | More information is required to inform a way forward | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | More information required for a decision |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
100 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 48 | Pipe Attribute & Validation File Format Instructions PShape |  |  |  | Need to also include/record results from "Deflection Testing/Laser Profiling" during the as-built. Deflection Testing for Flexible Pipelines is a requirement of the installation standard. Flexible pipelines rely almost completely on the soil strength and interaction with the yield and buckling resistance of the flexing pipe wall. This is a requirement of NZS4566.2 but is not being registered - and a future asset failure risk is promoted if not checked per the request of the Standard. |  |  | Vol 1 | Add Deflection Testing/Laser Profiling result to code list |  |  | Haydn | 2017-03-10 | Included | Included | Add Deflection Testing / Laser Profiling / Compaction results to code list - Calculation of results into ratings (e.g. Condition) are a Vol 3 requirement | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Is this to be added to Condition Assessment Type code list | [8 empty] | request documented | New Code List entry for Condition Assessment Type | Deflection testing Laser profiling |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
101 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 52 | Pipe Attribute & Validation File Format Instructions Haunching |  |  |  | Foundation strength pre-install Compaction strength per NZS4566.2 |  |  | Vol 1 | Add Foundation strength pre-install and compaction strength per NZ4566.2 |  |  | Haydn | 2017-03-10 | Included | Included | Add Foundation strength pre-install and compaction strength per NZ4566.2 | 2.3.4 Pipe | 1 | [7 empty] | 1 |  |  |  | 1 |  |  | make mention of change request | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | New Code List entry for Condition Assessment Type | Compaction Test per NZ4566.2 Foundation strength pre-install |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
102 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 52 | Pipe Attribute & Validation File Format Instructions Backfill |  |  |  | Compaction strength per NZS4566.2 or NZS3725 |  |  | Vol 1 | More information required for a way forward |  |  | Haydn | 2017-03-10 | Sector Discussion | Included | More information required for a way forward | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | Haydn please explain how these will be included change to Sector Discussion ? | [8 empty] | request documented | More information required for a decision |  |  | y | These are code lists which record how condition was determined (like visualisations) - they are examples of types materials testing
103 | Adrian Hynds | Hynds Group of Companies | Wastewater | Vol 1 | 2.3.4 | 52 | Pipe Attribute & Validation File Format Instructions Manu |  |  |  | Third Party QA for pipe material manufacturer |  |  | Vol 1 | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists |  |  | Haydn | 2017-03-10 | Included | Included | Add Manufacturer Manufacturing Standard Third Party QA Accreditation to code lists | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | [9 empty] | request documented | New attribute proposed | Manufacturer Manufacturing Standard Third Party QA Accreditaion
104 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | General | [5 empty] | Treatment Devices (Retaining Structures) Asset Data Schema Morphum Environmental are currently preparing the Treatment Devices asset data schema for Hamilton City Council and have previously had input into the current Auckland Stormwater Asset Data Standard. We recommend that the attributes outlined in Appendix 1 are replaced with the attributes provided in the PDF attached which closely mirrors the Auckland Council draft Stormwater Assets Metadata Standard and has been prepared for Hamilton City Council. In summary, we believe that the proposed scheme presented in Appendix 1 will not provide enough resolution to manage these complex assets and should be significantly modified. The provided schema represents more than 600 ponds and wetlands in the New Zealand urban landscape worth more than 1 Billion dollars. |  |  | Vol 1 | Me either |  |  | Haydn | Have not seen this pdf with the attributes proposed 14/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.3.3 Retaining Structure |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
105 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 1.8 | 1 | Channel |  |  |  | Spillway should be its own Asset Class |  |  | Vol 1 |  |  |  | Under review | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. 14/03/2017 | Sector Discussion | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.8 Theme Structure |  |  | 1 | [5 empty] | 1 | [7 empty] | Request for details to be captured currently spillway covered as an asset type within Channels Class | [9 empty] | More information required for a decision
106 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 1.9 | 4 | Stormwater Asset Class |  |  |  | Other Asset Classes we believe are missing: -Watercourse (Line or Polygon) -Forebay (Polygon) -Bridge (Polygon) -Maintenance Track (Polygon) -Fence (Line) -Viewing Platform (Polygon) -Erosion protection (gabion baskets etc.) (Polygon) |  |  | Vol 1 |  |  |  | Under review | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. 14/03/2017 | Sector Discussion | Sector Discussion | Further information required about what data is required to be able to manage these assets. The principal applied is that all assets that have the same characteristics are grouped. If they do not then a new asset class is created and offered for review and adoption or not by the community. | 1.9 Data Principles |  |  | 1 | [5 empty] | 1 | [7 empty] | what kind of watercourse? Forebay = retention Bridge - roading Maintemnance track - roading Fence - roading Viewing platform - not in scope erososion protection - more information neeeded | [9 empty] | More information required for a decision
107 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.1.8 | 14 | Common Attribute & Validation File Format Instructions |  |  |  | Source for what? This should have more detail. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Clarified the purpose of this field | Included | Included | Clarified the purpose of this field | 2.1.10 Common Attributes | 1 | [7 empty] | 1 | [6 empty] | change needed doc | change in pivot table | done | done | done | done | [5 empty] | Change made document updated
108 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.3.2 | 27 | 2 |  |  |  | Does this include forebay bunds and pond banks associated with ponds? |  |  | Vol 1 |  |  |  | Under review | Incorporate forebay bunds and pond banks as code list types 14/03/2017 | Sector Discussion | Sector Discussion | Incorporate forebay bunds and pond banks as code list types | 2.3.2 Embankment |  |  | 1 | [5 empty] | 1 | [6 empty] | changed mind these are embankment types | changed to Included | [9 empty] | New Code List Entry for Embankment Type proposed | Forebay bunds Pond banks
109 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.3.3 | 37 | Figure 17 |  |  |  | How would you like ponds and wetlands captured? Do you captured the permanent water level or the perimeter of the pond from aerials? |  |  | Vol 1 |  |  |  | Under review | Review the requirements for capture 14/03/2017 | Sector Discussion | Sector Discussion | Review the requirements for capture | 2.3.3 Retaining Structure |  |  | 1 | [5 empty] | 1 | [6 empty] | change needed | make mention of change request OFFER SUGGESTION | [9 empty] | More information required for a decision
110 | Alice Rieger | Morphum Environmental Ltd | Stormwater | Vol 1 | 2.3.3 | 43 | Retaining Structure Attribute & Validation File Format Instructions Link_ID |  |  |  | Bathymetry Attribute? |  |  | Vol 1 |  |  |  | George/Haydn | please say more about this. In what context would this attribute be used? | Included | Included | Bathymetrics are the equivalence of Topographics and used in water bodies as an attribute to descibe water body type | 2.3.3 Retaining Structure | 1 | [8 empty] | 1 |  |  |  | ok |  |  | suggest change to EXCLUDED as out of scope | [9 empty] | Haydn suggest this is excluded as I think it can be sourced from LINZ |  |  | y | we manage water bodies as part of stormwater and water asstes - we should add this
111 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | General | [5 empty] | Preamble: Housing New Zealand’s Asset Management strategy is supported by a set of internal standards, guidelines and manuals that describes and in some cases prescribes the design elements, components, materials and other aspects for our new builds and the maintenance and upgrade of existing Housing New Zealand homes. Those standards/guidelines and manuals have been developed over time based on industry practice and new technology/materials along with practical experience and reference existing legislation, regulatory standards and codes along with references to other similar jurisdictions social housing practices e.g. UK’s Decent Homes Standards. Housing New Zealand already collects a range of data for it’s portfolio to support both adherence to these standards e.g. type and condition of insulation in ceilings and also to inform internal and external reporting, strategic and operational planning; financial and investment decisions, rent setting and financial modelling. As a result some of the proposed Metadata Standards, some details are captured and currently used by Housing New Zealand; some data is on Housing New Zealand’s plan to be captured in the foreseeable future while there are other data sets proposed (refer specific content feedback) that Housing New Zealand would not necessarily see adding value to Housing New Zealand’s asset management approach at this point. Key: ✕ = Not needed / too hard to obtain ? = What does this mean? / doesn’t make sense ✓ = Achievable |  |  | Vol 1 |  |  |  | Noted | GISSA reference for review - Z:\Clients Projects\LINZ Meta-Data Standard Project\Buildings\Building Draft Standards\Distributed\Buildings New Format - V1 1 DRAFT - gissa v12 20160619 - Distributed Uncontrolled Copy 20/03/2017 | Noted: no action required | Noted: no action required | GISSA reference for review - Z:\Clients Projects\LINZ Meta-Data Standard Project\Buildings\Building Draft Standards\Distributed\Buildings New Format - V1 1 DRAFT - gissa v12 20160619 - Distributed Uncontrolled Copy | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
112 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 1.3 | 1 |  |  |  |  | The Hierarchy table works well |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 1.7 Heirarchy |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
113 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Global Asset Metadata Schemata | 2 |  |  |  |  | The schemata capture high level property data and component level data. The amount of data required is enormous based on the attributes of each asset, pp. 11 – 244. If the purpose of providing these data is for evidence-based investment decision making, in practice do we require having them all to come up with a perfect decision? Is there an optimal set of data attribute that could address this concern? We need to balance the effort required and the costs to provide the data with the benefits that could come out of a good investment decision. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Noted: no action required | Reviewed and Noted only for discussion | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | possible sector discussion this is the mandatory vs optional conversation | n/a | n/a | n/a | possible sector discussion this is the mandatory vs optional conversation | [5 empty] | No action |  |  | y | Updated comment
114 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 1.5 Data Principles | 3 |  |  |  |  | Complex requirement for such a large property portfolio |  |  | Vol 1 |  |  |  | Haydn | Noted 20/03/2017 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
115 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 1.6 Graphical Data Construction Principles | 4 |  |  |  |  | CAD requirement utilisation means HNZ would require all CAD documentation in an acceptable format for all properties. This would be a huge project should existing stock need to be included in this requirement. Huge cost, risk of accurate outcome for existing buildings. What advantage is there in this work? |  |  | Vol 1 |  |  |  | Noted | Reference to "please use sound CAD practices.." refers to the construction of linework 20/03/2017 | Noted: no action required | Noted: no action required | Not within the scope of these standards | 1.10 Geographical Data Construction Principles |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
116 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.1 Accuracy Requirement for Locating Asset | 5 |  |  |  |  | This is a huge task for as constructed / as built for a large portfolio |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
117 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Asset Management Frameworks | 5 |  |  |  |  | Blank. If the text will be the same as in Volume 2 then the examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | n/a | n/a | n/a | NOTED | [5 empty] | No action
118 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Asset Management Frameworks | 5 |  |  |  |  | There is a significant amount of information required from this survey – much of which will be difficult to define. This is problematic where a field can not be left empty. Can it be assumed that an unknown or N/A can be utilised where appropriate? I.e. see below |  |  | Vol 1 |  |  |  | Noted | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. 20/03/2017 | Noted: no action required | Noted: no action required | Yes - there will be an appropriate entry for fields that are not required or cannot be populated. | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | review and see where N/A and unknown is appropriate | [9 empty] | No action
119 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 Common Attributes Across all Asset Classes | 11 |  |  |  |  | QA Validation column has a Default = N/A. Note this used in some boxes and is not given as an option in other boxes - so is this item selected as opposed to a blanket option? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | This is selected versus a blanket option | Included | Included | This is selected versus a blanket option | 2.1.8 Common Attributes | 1 | [8 empty] | 1 |  |  |  | ok |  |  |  | COMMUNICATION | COMMUNICATION | COMMUNICATION | COMMUNICATION | [5 empty] | No action
120 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 Common Attributes Across all Asset Classes | 11 - 244 |  |  |  |  | The risk attributes required in Volume 1 are mainly on describing the risk and Volume 2 presents the risk schema. While risk information is useful for decision making it has to consider the process per AS/NZS ISO 31000:2009. This process in not quite well articulated in these two documents. Risk attribute required in this standard is static. For it to be useful however, it has to consider over time how other aspects of the risks such as mitigations applied (repairs and maintenance) lower the risk rating, changes to material/component properties due perhaps to natural deterioration, and the impact of significant events (earthquake, gales, flooding) modifies the risk profile of a property or portfolio. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Reviewed and Noted for Inclusion Risk is defined in standards and has a chronological attribution to measure change over time. | 2.1.8 Common Attributes |  |  | 1 | [5 empty] | 1 |  |  |  |  | what is to be included? |  |  | updated comment suggest remove that it is to be included | n/a | n/a | n/a | NOTED | [5 empty] | More information required for a decision |  |  | y | no change
121 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 11-251 |  |  |  |  | HNZ currently holds/uses very little of the proposed metadata in its systems. The as-constructed/as-built asset data we hold in our system includes: • Location – Address/Geo location/Census Area Unit/Meshblock/Territorial Local Authority • Asset Type • Ownership • Asset Status/Future Use • Build year/acquisition date and type • Hazards/Risks/Fire Compliance • Basic dimensions e.g. land/floor area; number of bedrooms/toilets; number of stories; site type; etc. • Title Information • Data for each Space in the property (e.g. Bedroom; Bathroom; Kitchen; Building Envelope; etc.) including: o Configuration description e.g. living/dining/kitchen/ o Wall/ceiling/floor finish o Key components and type e.g. bath; shower; Panel Heater – Electric; Cladding - Fibre Cement Weatherboard; Roof Type - Concrete Tile; o Installation date for some key components • Work order data for planned, responsive and routine work based on schedule of rates • Fixed asset cost and annual revaluation  We don’t capture detailed component information (e.g. types of doors, windows, lights etc.) or construction type (e.g. jib board, plywood, wooden frame, steal frame, etc.) |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Noted 20/03/2017 | Noted: no action required | Included | Reviewed and no changes made Noted - Organisations can collect what they see fit in Volume 2 for asset management purposes | General |  |  | 1 | [6 empty] | 1 |  |  |  | not saying its to be included However comparison needed to ensure these areas covered or not Will do after release of documents suggest change this to sector discussion |  | review against standard |  | n/a | n/a | n/a | NOTED | n/a | n/a | n/a |  |  | No action
122 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 12 |  |  |  |  | H_Prec  is it to be assumed this is national cadastral relative data? QA Validation column requires input not always available |  |  | Vol 1 |  |  |  | Noted | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. 20/03/2017 | Noted: no action required | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
123 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 13 |  |  |  |  | V_Proc  what is this and what is it to relate to? |  |  | Vol 1 |  |  |  | Noted | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. 20/03/2017 | Noted: no action required | Noted: no action required | No - this refers to the level of accuracy and precision that is used to capture the geographic location of the asset. | 2.1.8 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
124 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 13 |  |  |  |  | There are many ‘Link field to Volume 2’. Where / how is this linked? Is there to be a reference or word link? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Haydn please provide wording for how this will be applied/linked 20/03/2017 | Included | Included | Tables will be referenced in Final Versions | General | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | n/a | [5 empty] | No action
125 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.1.6 – 2.8 | 17 |  |  |  |  | Integer, compliance with relevant Building Code Energy rating  Define what is required? Difficult to provide this given the changed BC requirements. It this to capture when built / or at current time of survey. This is a moving target given the increased levels of R-value. |  |  | Vol 1 |  |  |  | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. 20/03/2017 | Sector Discussion | Sector Discussion | These standard data specifications are to enable data capture at time of completion of works and this value is to be captured when built and combined with the date will provide an audit trail for context. | 2.1.6-2.1.8 |  |  | 1 | [5 empty] | 1 | [11 empty] | NOTED | [5 empty] | More information required for a decision
126 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Reference unknown- cut off page | [5 empty] | Wind-loading  this info is on TA PIM /LIM as a site specific, which can vary from NZBC wind zones. What is required, why and how relevant is this information? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Sector Discussion | Sector Discussion | A wind loading table code list per the NZ Building Code is to be included and linked to the wind load rating - For analytical purposes To be discussed with the working group | 2.2.1 Building Footprint & 2.4.4 Roof |  |  | 1 | [6 empty] | 1 |  |  |  | your suggested response does not answer the question of why was it included. A wind loading table is not required as this is a calculated value | For analytical purposes updated comment Not answered | [5 empty] | THIS IS NOT WIND ZONES THIS IS A VALUE CALCULATED FIOR EACH BUILDING | [5 empty] | More information required for a decision
127 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Reference unknown- cut off page | [5 empty] | Fixed Load rating (Dead load?)  what is required, and at what time. If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
128 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Reference unknown- cut off page | [5 empty] | Live Load rating  can be a variable so what is required, and at what time in use? If unknown, how is this filled in a mandatory QA Validation box? What purpose is this for? It would never be used by the owner |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint & 2.4.2 Floor |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
129 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Seismic – what is required here and how is this obtained from existing properties. May be useful for multi-storey development, but is it for standalone |  |  | Vol 1 |  |  |  | Haydn | I think this detail is to be provided at the time it was built not at time of capture? - thoughts?? This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? 20/03/2017 | Noted: no action required | Noted: no action required | I think this detail is to be provided at the time it was built not at time of capture? - thoughts?? This detail was identified at the previous workshops and determined to be a required field. Please provide a specific reference to the table this comment is related to for further review. Is this related to the Building Footprint table? | 2.2.1 Building Footprint |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
130 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Fungi treatment is probably applicable to builds impacted upon by weather tightness issues, but empty field for other projects needs to have a N/A application available |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
131 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Ground type how is this to be defined without geotechnical engineering input and related expense. For what purpose |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Sector Discussion | Sector Discussion | A geotechnical table code list (%NBS) per the NZ Building Code is to be included - For analytical purposes | 2.2.1 Building Footprint |  |  | 1 | [6 empty] | 1 |  |  |  | your suggested response does not answer the question of why was it included. | For analytical purposes Have added 'geographical units' code list updated comment Not answered |  |  | n/a | n/a | n/a | codelists added | [5 empty] | Change made document updated
132 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Graffiti  irrelevant |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
133 | Andy Walmsley | Housing NZ | Buildings | Vol 1 |  | 18 |  |  |  |  | Flood  applicable only in related areas, and this information is on local council records |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
134 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 18, 20-250 |  |  |  |  | A number of building footprint attributes (seismic performance status, asbestos, fungi) and even in the component attributes (ground type, utilisation, fire barrier type, fire rating) are by itself or in combination with other attributes could become a risk for a property. The standard is silent on how these attributes interact or linked to help inform on and assess the risk/s of a property? |  |  | Vol 1 |  |  |  | Haydn | Please refer to Volume 2. 20/03/2017 | Noted: no action required | Noted: no action required | Please refer to Volume 2. | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
135 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 20 |  |  |  |  | Ground type  how is this to be defined without geotechnical engineering input and related expense. For what purpose |  |  | Vol 1 |  |  |  | Noted | Addressed from previous comments see ID 131. 20/03/2017 | Noted: no action required | Noted: no action required | Addressed from previous comments see ID 131. | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 |  |  |  |  | SEARCH ON GEOTECHNICAL QUESTION |  |  |  |  | PREVIOUSLY COVERED | [5 empty] | No action
136 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 20 |  |  |  |  | Design life how is this applied to existing property |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.2.1 Building Footprint |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
137 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 23 |  |  |  |  | Most of this requirement seems more appropriate to multi-storey complexes, but not relevant to standalone housing. The exclusion is the structure type and materials |  |  | Vol 1 |  |  |  | Noted | This standard will be applicable to both residential and light commercial buildings. 20/03/2017 | Noted: no action required | Noted: no action required | This standard will be applicable to both residential and light commercial buildings. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
138 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 24-25 |  |  |  |  |  As above, in addition the Condition Assessment, condition and repairs may be of use. The rest is superfluous to requirement (more and asset decision than standards) |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
139 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 25-28 |  |  |  |  | Bracing  difficult to obtain this information in existing properties and for what use. Age can establish levels of possible bracing, and anything prior to 2011 will be inadequate to current building code requirement. Many of the items asked for are too complex – most of page 26, 27 and 28. What relevance? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field and would be collected as part of the project requirements. If Housing NZ do not collect this data now would they consider collecting it in the future? | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
140 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 28 |  |  |  |  | Finish  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
141 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 29 |  |  |  |  | Finish condition assessment, condition and repairs  ✓ The rest is superfluous |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
142 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 30 -34 |  |  |  |  | Insulation type, material installer warrantee, acoustic design life, con ass and condition, repairs (maybe)  all ok. The rest is irrelevant. How is cu metre to be found and why? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satify both facilities management and asset management. With respect to cu metre please provide more information. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be required field. It is acknowledged that the level of detail is to satify both facilities management and asset management. With respect to cu metre please provide more information. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
143 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 34 |  |  |  |  | Services, fire barrier and type, installer, warranty FRR  yes. Design life Covered with building consent durability. If existing difficult to establish. |  |  | Vol 1 |  |  |  | Noted | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | It is acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
144 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 35 |  |  |  |  | Fire Rating  ✓ Fire Resistance standard  Difficult to define, because accepted = adequately |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
145 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 35 |  |  |  |  | Design life  If new = Ok |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Excluded | Reviewed and Noted only | 2.4.1 Ceiling |  | 1 | [8 empty] | 1 | [6 empty] | no action | no action | no action | NOTED | [5 empty] | No action
146 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 35 |  |  |  |  | Cost  Not needed? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Included | Reviewed and Noted only | 2.4.1 Ceiling | 1 | [9 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
147 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 36 |  |  |  |  | Condition Assessment Type  ✓ Condition  ✓ Repairs and Maintenance, Utilisation, and Demand Contents  Too detailed for stand alone housing |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Included | Reviewed and Noted only | 2.4.1 Ceiling | 1 | [9 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
148 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 37 |  |  |  |  | Too much detail required for ceilings. Condition, material, surface finish = Yes |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
149 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 37 |  |  |  |  | Risk, Resilience, and Financial performance  Too much detail |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Included | Reviewed and Noted only | 2.4.1 Ceiling | 1 | [9 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
150 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 37 |  |  |  |  | Acoustic barrier, QA validation, Field cannot be empty  Problem. Has an acoustic barrier been installed?  Where? Application? Not sure how this applies residentially. Acoustic may be relevant in multi-storey, but should be deleted for standalone housing. Too much info even for resident multi-level. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
151 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 40 |  |  |  |  | Links to Volume 2  how does this work? Difficult to define and what relevance does it have in existing housing? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Links will be Reviewed and Noted for Inclusion | 2.4.1 Ceiling |  |  | 1 | [7 empty] | 1 |  |  | review your response as not consistent with question | updated comment | [5 empty] | COMMUNICATION | [5 empty] | More information required for a decision
152 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 40 |  |  |  |  | Smoke_Barr  Smoke relevant to multiunit development only. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
153 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 41 |  |  |  |  | First 5 rows – achievable in new build buy why would this be required or used? Stand alone not needed |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | For analytical purposes for Vol 2 | 2.4.1 Ceiling |  |  | 1 | [7 empty] | 1 |  |  | review your response as not consistent with question | updated comment not answered | [5 empty] | NOTED | [5 empty] | Change made document updated
154 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 41 |  |  |  |  | Des_Life - ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
155 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 41 |  |  |  |  | Cost ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
156 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 42 |  |  |  |  | Condition Assessment Type  ✓ Condition  ✓ Last 4 rows  ?\ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
157 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 43 |  |  |  |  | Whole page  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Ceiling |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
158 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 47 |  |  |  |  | Build_ID Floor_ID, Purpose, Disable_Ac, Struc-Type, Struct_Ma  ✓, Floor elevation  How can this be defined in existing housing and for what reason? Is this related to the national datum? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. Floor Elevation - Yes this is related to the national datum and will be used for modelling against events such as flooding. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
159 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 47 |  |  |  |  | Dead load rating à What use? This must be because compliant for new and unknown for existing properties. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
160 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Live load rating of floor à too difficult to define |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
161 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Des-Life, Con-Ass_T, Condition à ✓ Cost row à ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
162 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Repairs and Maintenance à what’s the need for this? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Noted, for analytical purposes, e.g. investment decision | 2.3 Repairs, Maintenance and Operations Schema |  |  | 1 | [7 empty] | 1 |  |  | what is to be included? | updated comment | [5 empty] | NOTED | [5 empty] | No action
163 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 48 |  |  |  |  | Utilisation, Demand, and Critically à Fully needed and used. Floors = Always critical. So this would be a constant and why needed? ** |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Sector Discussion | Sector Discussion | Noted, for analytical purposes, e.g. economic yield | No Specific Reference |  |  | 1 | [7 empty] | 1 |  |  | what is to be included? | updated comment | [5 empty] | NOTED | [5 empty] | No action |  |  |  |  | 1
164 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 49 |  |  |  |  | First 5 rows à Very detailed for residential use. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
165 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 50 |  |  |  |  | Bracing is as per ceiling notes |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
166 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 52 |  |  |  |  | Floor_Mat, Floor_Cond à ✓ Pen_seal, Last row à Why would this be needed, or used? |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor |  |  | 1 | [7 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | More information required for a decision
167 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 53 |  |  |  |  | First row  as above Des_Life  ✓ Cost row ✕ Con_Ass_T  ✓ |  |  | Vol 1 |  |  |  | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops 20/03/2017 | Sector Discussion | Sector Discussion | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. Will finalise following final workshops | 2.4.2 Floor |  |  | 1 | [7 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | More information required for a decision
168 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 54 |  |  |  |  | Condition  ✓ Repairs  ✓ Second row  Not sure repairs need noted. Replacements yes. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
169 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 54 |  |  |  |  | Third row à Maybe |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
170 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 54 |  |  |  |  | 3rd, 4th and 5th row à Some of these items called for are obviously needed and are critical, so why the need for such intense breakdown. Too detailed – throughout. |  |  | Vol 1 |  |  |  | Noted | The breakdown is provided to be clear and specific about the requirements. 20/03/2017 | Noted: no action required | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | COMMUNICATION | [5 empty] | No action
171 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 55 |  |  |  |  | Whole page  ✕, too much detail. However, material, age (?), condition, date installed, maybe slip resistance Is all required. |  |  | Vol 1 |  |  |  | Noted | The breakdown is provided to be clear and specific about the requirements. 20/03/2017 | Noted: no action required | Noted: no action required | The breakdown is provided to be clear and specific about the requirements. | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
172 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 56 |  |  |  |  | Design Life – Surface  ✓ Last 7 rows in grey  Multi storey application only. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
173 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 57 |  |  |  |  | Multi storey application only. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
174 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 58 |  |  |  |  | - Multi storey application only. Too much detail required. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
175 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 59 |  |  |  |  | Last 5 yellow rows à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 | [6 empty] | 1 | [9 empty] | NOTED | [5 empty] | No action
176 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 60 |  |  |  |  | - 2nd row à ? Building Code complaint for new works. Unknown for much existing |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
177 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 60 |  |  |  |  | Inst_W, Fire Rating, Con_Ass_T  ✓ 3rd row  ? 4th row  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
178 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 62 |  |  |  |  | Thermal barrier à ? Floor insulation is all that is relevant in residential. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
179 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 63 - 65 |  |  |  |  | All pages à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
180 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 66 |  |  |  |  | Whole page à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
181 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 67 |  |  |  |  | Acoustic row, content  maybe Cost  X Rest of page  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
182 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Building Footprint Attribute | 68 |  |  |  |  | Util, Crit, Risk, resil,Structure  ✓ Demand  ? Design  ? Finance performance  ? tenant cost savings? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.2 Floor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
183 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 70 |  |  |  |  | This section is underground and undefinable in existing housing stock. Therefor, all tables are unable to be filled, except for new build works (What need to data collect over and above because of documents?) |  |  | Vol 1 |  |  |  | Noted | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. 20/03/2017 | Noted: no action required | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
184 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 71 |  |  |  |  | Whole page  undefinable in existing housing. |  |  | Vol 1 |  |  |  | Noted | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. 20/03/2017 | Noted: no action required | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
185 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 72 |  |  |  |  | Vents  ✓ Membrane rows  Define what membrane? |  |  | Vol 1 |  |  |  | Noted | The membrane refers to the membrane between the foundation and the floor. 20/03/2017 | Noted: no action required | Noted: no action required | The membrane refers to the membrane between the foundation and the floor. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
186 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 72 |  |  |  |  | Foundation area, content à ? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field as the foundation area is larger than the footprint of the building and will be important in determining the extents in the event of works nearby. | 2.4.3 Foundation |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
187 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 73 |  |  |  |  | à See previous foundation notes |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | As the page numbers do not correspond with the document please provide additional comments for context. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
188 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.3 Foundation | 74-77 |  |  |  |  | All pages à ✕ |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | As the page numbers do not correspond with the document please provide additional comments for context. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.4.3 Foundation |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
189 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Roof_Sturc, Frame_Mat, Des-Life, Con_Ass_T  ✓ Area row  need for? |  |  | Vol 1 |  |  |  | Noted | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified"This detail was identified at the previous workshops and determined to be a required field if there is more than one roof system. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
190 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Load wind/fix  Not known in existing stock |  |  | Vol 1 |  |  |  | Noted | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. 20/03/2017 | Noted: no action required | Noted: no action required | The intent is to create a common structure for data to be collected. It is acknowledged that some data will not be available for existing assets. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
191 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Frame_Tr  not always identifiable Frame_ Sp  why? |  |  | Vol 1 |  |  |  | Noted | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | These two fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
192 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 79 |  |  |  |  | Cost row à ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
193 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 80 |  |  |  |  | Con, Repairs, Util, Crit  ✓ Demand row  ? Risk row  ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
194 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 80 |  |  |  |  | Last 3 rows  Is this needed and how is it defined? |  |  | Vol 1 |  |  |  | Sector Discussion | Please specify the rows. 20/03/2017 | Sector Discussion | Sector Discussion | Please specify the rows. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
195 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 81 |  |  |  |  | Cladding  ✓ Finish on the Cladding  ✓ ? Manufacture, installation etc.  only able to be filled in new builds and replacement works. |  |  | Vol 1 |  |  |  | Noted | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | These fields were identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or replacement works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
196 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 81 |  |  |  |  | First row, QA Validation  N/A needs to be applied here |  |  | Vol 1 |  |  |  | Noted | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. 20/03/2017 | Noted: no action required | Noted: no action required | If this refers to the Unique Identifer field this is to be created by the data supplier as a reference point. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
197 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 82 |  |  |  |  | Condition  ✓ Repair row  How do we accurately collect and record this information, and why? Unrealistic. |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
198 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 82 |  |  |  |  | Last 5 rows  as per previous notes |  |  | Vol 1 |  |  |  | Sector Discussion | Please specify the rows. 20/03/2017 | Sector Discussion | Sector Discussion | Please specify the rows. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
199 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 83 |  |  |  |  | Spout type, Material  ✓ Spouting product detail  ? Spouting length  ✕ |  |  | Vol 1 |  |  |  | Noted | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | These fields were identified at the previous workshops and determined to be required. Spouting product detail - refers to the fact sheet available for the product to be provided. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
200 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 84 |  |  |  |  | Whole page  ✓ apart from: Cost row  ? |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
201 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 85 |  |  |  |  | First 3 rows  ? |  |  | Vol 1 |  |  |  | Sector Discussion | Please specify the rows. 20/03/2017 | Sector Discussion | Sector Discussion | Please specify the rows. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
202 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 85 |  |  |  |  | Last row, QA validation à Critical |  |  | Vol 1 |  |  |  | Sector Discussion | Please provide more information on the requirement. 20/03/2017 | Sector Discussion | Sector Discussion | Please provide more information on the requirement. | 2.4.4 Roof |  |  | 1 | [5 empty] | 1 | [11 empty] | COMMUNICATION | [5 empty] | More information required for a decision
203 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 86 |  |  |  |  | Risk  ✓ Resil, Des_Perf  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
204 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 87 |  |  |  |  | First 2 rows  ✕ Downpipes product detail ✕ Downpipes length  ✕ Downpipe capacity  ? D_Manu, D_Man-W  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
205 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 88 |  |  |  |  | Whole page à ✓ Apart from Cost row à ? |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
206 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 89 |  |  |  |  | First 3 rows à? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
207 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 89 |  |  |  |  | critically, QA Validation à Critical |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
208 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 90 |  |  |  |  | All 3 rows  ? Row 3  Too much detail |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
209 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 91 |  |  |  |  | 1st row  ✕ 2nd row  ? Fascia_Type, Fascia_Mat  ✓ Last 3 rows  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
210 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 92 |  |  |  |  | Condition  ✓ Cost row  ✕ Last 2 rows  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
211 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 93 |  |  |  |  | All 4 rows  ✕, ?, ?, ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
212 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 94 |  |  |  |  | 1st 3 rows  ✕ Sof_Type, Sof_Mat  ✓ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
213 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 94 |  |  |  |  | Enclosure soffit length and area  ✕. Too detailed, why the need? Enclosure soffit width  ? Can identify risk – needed? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Not certain how to answer this one. 20/03/2017 | Included | Included | Width and length = sqm (e.g. paint) | 2.4.4 Roof | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | No action
214 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 95 |  |  |  |  | Condition  ✓ Top 2 rows  ✕ Repairs  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
215 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 96 |  |  |  |  | Whole page à✕. Risk – could relate to a water risks |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
216 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 97 |  |  |  |  | Whole page à ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
217 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 98-101 |  |  |  |  | Classifications, Masterpec, Enclosure à not sure what this is representing? |  |  | Vol 1 |  |  |  | Noted | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz 20/03/2017 | Noted: no action required | Noted: no action required | Masterpsec is a classification systen created in NZ. www.masterspec.co.nz | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | COMMUNICATION | [5 empty] | No action
218 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 101 |  |  |  |  | Ins-Type, R_Value à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
219 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 102 |  |  |  |  | Whole page  ✓ Insulation installer and warranty  maybe |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
220 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 103 |  |  |  |  | Des_Life, Con_ass_T, Condition  ✓ Cost row  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
221 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.4 Roof | 104-106 |  |  |  |  | Whole pink pages/part  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Roof |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
222 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 109 |  |  |  |  | Unique_ID, Build_ID, Floor_ID  ✓ Planted wall, Planted wall standard and Wall identifier  Not applicable |  |  | Vol 1 |  |  |  | Noted | Not required for residential housing at Housing NZ | Noted: no action required | Noted: no action required | Not required for residential housing at Housing NZ | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
223 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 109 |  |  |  |  | Last row, Shear Wall  Structural engineering determined. Hard to establish in existing houses and why needed? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
224 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 110 |  |  |  |  | First four rows  too much information that would not be needed for housing. Difficult to define in existing housing. Superfluous. Wal-Type, Wall_Mat, Drainage  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
225 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 110 |  |  |  |  | Grout and Wall Structure Joint  ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
226 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 111 |  |  |  |  | Drain type  ✕ Manufacturer  ? Cost  ✕ D_Manu, Des_life, Con_ass_T  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
227 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 112 |  |  |  |  | Condition  ✓ Repairs  ? |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
228 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 113 - 115 |  |  |  |  | Structure, Bracing à As per floor and roof bracing |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
229 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 116 |  |  |  |  | Enclosure, yellow contents, Plasterboard à standard grade & water-resistant – this would not be determinable in existing properties |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
230 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 118 |  |  |  |  | Wall, Design Life à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
231 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 119 |  |  |  |  | Condition  ✓ Cost row  ✕ Repairs  ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
232 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 121 |  |  |  |  | Fire barrier à Multiunit. May not be known on existing stock |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
233 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 124-125 |  |  |  |  | Orange à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Walls |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
234 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.4.5 Walls | 126 |  |  |  |  | Insulation Installer Warranty, QA validation, Field cannot be empty à What if not applicable as is the case in most housing? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available or applicable for existing assets and therefore a nominated default value would be utilised. | 2.4.5 Walls |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
235 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 132 |  |  |  |  |  Why would door info be needed? Maybe unidentifiable in existing stock* Function of the door, Control system on the asset, and Asset grill  Applicable to multi-unit complexes. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new or rehabilitated works this will be available. | 2.5 Structure - Minor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
236 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 133 |  |  |  |  | Whole page à why would we use this information? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5 Structure - Minor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
237 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 134 |  |  |  |  | Acoustic and Thermal rating à Not used. Where applicable? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | 2017-03-20 | Noted: no action required | Reviewed and Noted only | Reviewed and Noted only | 2.5 Structure - Minor | 1 | [8 empty] | 1 |  |  |  | what is to be included? These fields already exist. | updated comment | [5 empty] | NOTED | [5 empty] | No action
238 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5 Structure – Minor | 137-138 |  |  |  |  | Green Ironmongery section à difficult to identify in existing stock and why would we need this info? Maybe just notes in type; lever, knob, lockable, key, push button? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5 Structure - Minor |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
239 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 141 |  |  |  |  | à Why / how would we use this? Too much information required. |  |  | Vol 1 |  |  |  | Noted | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. 20/03/2017 | Noted: no action required | Noted: no action required | The diagram is indicative of the components of a staircase. This level of detail is not completely required. Please refer to the table. | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
240 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 142 |  |  |  |  | Type, Content  ✓ Material  Not able to be found if covered in carpet Manufacturer Warranty, Installation date, Installer, Installer warranty  ✕ |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
241 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 143 |  |  |  |  | Rail type and rail material  maybe landings  ✕ Ramp gradient  hard to determine in reality Non slip  how to determine Emergency  0 Applicable to multi-unit, but covered in building WOF |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
242 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.2 Stairs | 144 - 146 |  |  |  |  | Pages  ✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.2 Stairs |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
243 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 151 |  |  |  |  | Type, Finish, Sash_Mat, Sash_Fnsh  ✓ Location  Only record external in housing - suggested |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | not certain what is being suggested. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
244 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 151 |  |  |  |  | Framed and Frame material à not defined in window anatomy page 149 |  |  | Vol 1 |  |  |  | Sector Discussion | Update diagram on p149 | Sector Discussion | Sector Discussion | Update diagram on p149 | 2.5.3 Windows |  |  | 1 | [5 empty] | 1 | [6 empty] | change needed | update diagrams for buildings GISSA TO FIND DIAGRAMS | n/a | n/a | n/a | REVIEW DIAGRAM | [5 empty] | Modify Diagram
245 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 151 |  |  |  |  | Height of windows in mm à what value? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | am open to suggestions. 20/03/2017 | Noted: no action required | Reviewed and Noted only | External for H&S. This is included for access and maintenance purposes | 2.5.3 Windows | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | NOTED | [5 empty] | No action
246 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Condition  ✓ Width  why needed? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | am open to suggestions. 20/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.5.3 Windows |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [6 empty] | COMMUNICATION | [5 empty] | More information required for a decision
247 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Manufacturer, warranty, installation date, installer àUnknown on existing |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
248 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Design life à How to define? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
249 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 152 |  |  |  |  | Repairs à ? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | NOTED | [5 empty] | No action
250 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 153 |  |  |  |  | Page à✕ |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
251 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 154-156 |  |  |  |  | Yellow Glazing section àUnrealistic. Unidentifiable on existing. Safety glass identified? Double or single glazed is appropriate. |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
252 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 156 |  |  |  |  | Hardware à Locks, Yes. Lever/knobs maybe. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
253 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 157 |  |  |  |  | Whole Column Name – Full is circled à Not always known on existing. Why needed? |  |  | Vol 1 |  |  |  | Noted | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. 20/03/2017 | Noted: no action required | Noted: no action required | This structure has been developed to provide a common structure for data hat will be collected. It is acknowledged that this may not be available and will provide a Gap when a comparison is undertaken with your organisations data currently held. | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action
254 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.5.3 Windows | 157-159 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.3 Windows |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
255 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6 Utilities | 163 |  |  |  |  | Whole page à too detailed for residential application. Not even sure all these is useful on multi-storey? |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | 2017-03-20 | Included | Included | Organsiations will decide on the levcel of detail - some require this level | 2.6 Utilities | 1 | [8 empty] | 1 |  |  |  | your suggested response does not answer the question of why was it included. | updated comment | [5 empty] | NOTED | [5 empty] | No action
256 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6 Utilities | 164 |  |  |  |  | à Maybe cover meter / switch board + light fittings? LED/incandescent/fluro |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6 Utilities |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
257 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6 Utilities | 164 |  |  |  |  | Services, pink section àmore commercial application. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6 Utilities |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
258 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.2 Electrical Components (Polyline) | 168-170 |  |  |  |  | à No! How is this captured realistically and why? |  |  | Vol 1 |  |  |  | Haydn | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. | 2.6.2 Electrical Components |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
259 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.3 HVAC-General (Point) | 172-175 |  |  |  |  | Not applicable to Residential |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
260 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.4 | [5 empty] | Not applicable to Residential |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
261 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.5 | [5 empty] | Not applicable to Residential |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.3 - 2.6.6 HVAC |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
262 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Plumbing – Fittings (point) | 187 |  |  |  |  | à Would we use this at a per item attribute? |  |  | Vol 1 |  |  |  | Haydn | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
263 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | Plumbing – Fittings (point) | 188 |  |  |  |  | Type à ✓ Last row, content à NA |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.7 Plumbing - Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
264 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.7 Plumbing – Pipework (Polyline) | 192 |  |  |  |  | à Problematic to get this info, other than gulley traps (or a number of water info – buy why need this?) |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
265 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.6.7 Plumbing – Pipework (Polyline) | 194 |  |  |  |  | àToo difficult and unnecessary info |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.6.8 Plumbing - Pipework |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
266 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7 Services | 197 |  |  |  |  | à Stove have heater fans |  |  | Vol 1 |  |  |  | Noted | Included as part of the product fact sheet provided with the appliance. 20/03/2017 | Noted: no action required | Noted: no action required | Included as part of the product fact sheet provided with the appliance. | 2.7.1 Appliances and Equipment |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action
267 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7 Services | 198 |  |  |  |  | Pink section: Type, Manufacturer, Location, and Utility supply  useful information Manufacturer warranty  ✕ Installation date  ? |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.1 Appliances and Equipment |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
268 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7 Services | 199 |  |  |  |  | Type, Manu, Location, Supply  ✓ PAT, QA Validation – N/A Compliance Contents  ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.1 Appliances and Equipment |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
269 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.72 Data & Communication (Point) | 202 |  |  |  |  | Blue section  ✓ Condition Assessment Type  ✓ Condition  ✓  Not a lot of info required. If there, what, condition |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.2 Data & Communication (Point) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
270 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.72 Data & Communication (Point) | 203 |  |  |  |  | Pink section  Not sure how much of this is required/useful |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.2 Data & Communication (Point) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
271 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 211 |  |  |  |  | Blue section - ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.4 Fixtures & Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
272 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 211 |  |  |  |  | Asset type à ✓ Kitchen Vanities in contents |  |  | Vol 1 |  |  |  | Included | Add to codelist | Included | Included | Add to codelist | 2.7.4 Fixtures & Fittings | 1 | [8 empty] | 1 | [10 empty] | DONE NEW CODE LIST ENTRY | [5 empty] | New Code List entry for Fittings Type proposed | Kitchen Vanities
273 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 211 |  |  |  |  | Length, Height, Width à Why? |  |  | Vol 1 |  |  |  | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. 20/03/2017 | Sector Discussion | Sector Discussion | To be reviewed by the TWG for consideration to be excluded. | 2.7.4 Fixtures & Fittings |  |  | 1 | [6 empty] | 1 | [5 empty] | make mention of change request |  | n/a | n/a | n/a | NOTED | n/a | n/a | n/a | n/a | request documented | More information required for a decision
274 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.4 Fixtures & Fittings (Point) | 212 |  |  |  |  | Whole page à Doubt this would be known |  |  | Vol 1 |  |  |  | Noted | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. 20/03/2017 | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be a required field. It is anticipated that when capturing data for new works this will be available. It is also acknowledged that this may not be available for existing assets and therefore a nominated default value would be utilised. | 2.7.4 Fixtures & Fittings |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
275 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.5 Fire Protection Components (Point) | 217 |  |  |  |  | à Applicable to multiunit complexes. *Expert input required = consultant needed = $$ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.5 Fire Protection Components (Point) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
276 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.6 Fire Protection Components | 221 |  |  |  |  | à Covered in Building WOF. *Specialist area = consultant needed = $$ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.6 Fire Protection Components |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
277 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.7 Lifts (Polygon) | 226 |  |  |  |  | àSpecialists information and only applicable to multi-unit/storey complexes. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.7 Lifts |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
278 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.9 Security (Point) | 237 |  |  |  |  | à CCTV: only applicable in multi-units. Is it needed? Application? Maybe as a record but this is too detailed. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.9 Security |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
279 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.7.10 Signage | 242 |  |  |  |  | à Not so useful in residential and difficult to maintain/update. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.7.10 Signage |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
280 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.8.1 Space (Polygon) | 248 |  |  |  |  | à Not really applicable to existing housing. Maybe some use in multi-unit development. |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.8.1 Space |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
281 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 252 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
282 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 254 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | GEORGE & HAYDN | Will have a particular application for connection to civil works. | Included | Included | Will have a particular application for connection to civil works. | 2.9 Supplementary data | 1 | [8 empty] | 1 |  |  |  | ok | [6 empty] | NOTED | [5 empty] | No action
283 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 255 |  |  |  |  | à ✕ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
284 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 256 |  |  |  |  | Material à ✓ |  |  | Vol 1 |  |  |  | Noted | 2017-03-20 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
285 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 257 |  |  |  |  | Pipe type à ✕ |  |  | Vol 1 |  |  |  | Noted | Required for assets recorded in a building 20/03/2017 | Noted: no action required | Noted: no action required | Required for assets recorded in a building | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
286 | Andy Walmsley | Housing NZ | Buildings | Vol 1 | 2.9 Supplementary data | 257 |  |  |  |  | Water type à ? |  |  | Vol 1 |  |  |  | Noted | To address if this is potable, recycled, raw etc. 20/03/2017 | Noted: no action required | Noted: no action required | To address if this is potable, recycled, raw etc. | 2.9 Supplementary data |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action
287 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | General | [5 empty] | Preamble: Housing New Zealand’s Asset management performance approach has recently been reviewed and in light of this a number of initiatives are in place to improve the maturity of this approach. The focus on this approach is to ensure that we are designing tools and performance measures that are “fit for purpose” for a large scale social housing business owned by the Crown to ensure Housing New Zealand is the social housing provider of choice. As such we have recently embarked on a new approach to assessing property condition; refreshed a range of financial and investment methodologies; improved Housing New Zealand’s market rent setting policy and methodology and are continuing to invest in maturing our approach to asset management. We currently have tools and systems that reflect both the customer (tenant) and asset (rental property) which link both upstream to the purchaser (MSD); across to banking systems; and downstream to large and medium scale performance based maintenance contractors and national suppliers. Housing New Zealand is supportive of evolving and improving on the way we report and understand performance of our assets (and how they meet the needs of our customer base) however any potential large scale changes to measuring and monitoring performance is likely to have significantly implications both up and down stream; and we caution the need to confirm with each agency the level of unintended impact (especially to current performance/service levels) before final standards are agreed. | General | Statement noted. To be considered in business case. No changes required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | To be considered in business case. No changes required. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
288 | Andy Walmsley | Housing NZ | Buildings | Vol 2 |  | iv |  |  |  |  | ‘While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are correct and relevant.’ What does this mean? | Front End | Rewrite "In Summary", to reflect public asset ownership. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Edited to make clearer | No Specific Reference | 1 | [8 empty] | 1 | [10 empty] | CHGNAGE DONE COMMUNICATION | [5 empty] | No action |  | Modified text |  |  | 2 | 2
289 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.1 Purpose of this Document | 8 |  |  |  |  | This document excludes industrial buildings and Ancillary building’s  provide examples | Front End | Remove Table 1. Table 1 and reference are no longer needed, as two standards are combined, refers to the building act. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 2 | 2
290 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.1 Purpose of this Document | 9 |  |  |  |  | Table 1 Building Act Classification  Where are other types of buildings – e.g. residential. houses used for community facilities (office spaces; meeting rooms) ‘Hall’ is an example – does this mean Community spaces? | Front End | Remove Table 1. Table 1 and reference are no longer needed, as two standards are combined, refers to the building act. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 2 | 2
291 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.1 Purpose of this Document | 10 |  |  |  |  | Added Laundry to Outbuildings, included in the Residential standard | Front End | Remove Table 1. Table 1 and reference are no longer needed, as two standards are combined, refers to the building act. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Table 1 updated per the Building Code (Residential and Light Commercial Buildings) | Table 1: Building Act Classification of Residential and Light Commercial Buildings | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  |  | y | Updated comment | 2 | 2
292 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.2 Structure of Standard | 10 |  |  |  |  | The bullet points à are they attributes or measures? | Front End | Changed this to schema's and align with cohorts. | Vol 2 |  |  | Included in draft |  |  | Included | Included | These are design elements - per Volume 2 | 1.2 Structure of Standard | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  |  | y | completed | 2 | 2
293 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.2 Structure of Standard | 12 |  |  |  |  | What is Boolean data type? | Front End | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Vol 2 |  |  | noted |  |  | Excluded | Excluded | No change required. Boolean is a data type with only two possible values i.e. Yes or No; true or false, as indicated in report. | Table 4: Data Type |  | 1 | [7 empty] | 1 | [7 empty] | no action | no action | no action | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
294 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.4 Context of Asset Data and Analytics | 16-17 |  |  |  |  | Vulnerability is circled in Figure 1 Global Asset Metadata Schemata. It is shown in Figure 1, but not included in the list of all the other decision elements. à Where is it? | Vulnerability | Vulnerability Schema has now been added -was missing from draft. No change required. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Vulnerability Schema has now been added -was missing from draft. No change required. | 4.2 Vulnerability Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | already done | y | no change | 2 | 2
295 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.4 Context of Asset Data and Analytics | 17 |  |  |  |  | Criticality: the significant of the removal of any individual component or asset… à Is this also failure? | Criticality | Agreed. Action: Wording will be changed to clarify: e.g. removal/failure | Vol 2 |  |  | Yes it is also failure, in a broad sense. More reflects removal of service of asset (for example, the asset could be turned off), as opposed to failure per se |  |  | Included | Included | Criticality and Failure are different. Criticality is a decision element of a network, failure is a consequence of an event incurred on a network | 4.3 Criticality & Code List 21: Repairs, Maintenance and Operations Failure Mode – Type | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | no action |  | ? | y | Updated comment | 2 | 2
296 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.4 Context of Asset Data and Analytics | 18 |  |  |  |  | The third and fourth suite of analytics à seems very granular? | Front End | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No change required. Intended to explain how more sophisticated techniques can be applied when more data is available. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2 | 2
297 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | Asset Management Frameworks (volume 5) | 19 |  |  |  |  | à The examples indicated are not providing a good view of all the requirements needed in asset management. Indicate a reference to the list of legislation, regulatory, and industry requirements. For example, HNZ’s compliance requirements cover over 60 legislations, regulations, and industry standards that we need to adhere or complied with. | Front End | No change required. Only intended as examples. A full list applicable to everyone HNZ through Corrections, MoE etc. would be enormous. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | References are being considerd | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
298 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 1.8 Theory and practice | 29 |  |  |  |  | Optimised replacement schematic – risk as an influence. à Is this the same as criticality? | Front End | Updated | Vol 2 |  |  | Included in draft |  |  | Included | Included | No, note Risk and Criticality Schemas | 4.3 Criticality Schema and 4.4 Risk Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  |  | y | no change | 2 | 2
299 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2 Condition Schema | 30 |  |  |  |  | à Should there be a requirement to define timing/cycle of when condition grade is assessed? | Condition | No change required. This is a metadata standard., not a condition manual. Each organisation needs to decide their own frequency. Condition is a snapshot at any given time which, together with age and working life can be used to assess when an asset may need attention ($). | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Age of an asset (or expected life or residual life) of an asset are all measured independently from one another of required - the attributes in the standards allow this where / when required | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action |  |  |  |  | 2 | 2
300 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2.3 Interfaces with Other Schema | 31 |  |  |  |  | Table 4. à unclear what this actually shows? | Condition | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Vol 2 |  |  | Noted |  |  | Noted: no action required | Noted: no action required | No change requires: The table below identifies the other Schema that the Condition Schema interfaces with. | Table 5: Condition – Interface with Other Schemas |  |  |  | 1 | [5 empty] | 1 | [10 empty] | COMMUNICATION | [5 empty] | No action |  |  |  |  | 2 | 2
301 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2.4 Assessing Asset Condition | 32 |  |  |  |  | Data Table 2 Condition Assessment Attributes - 2.06 Qualification of the Assessor.: Mandatory  believe this information is too detailed for recording - 2.07: Number of years’ experience the assessor has. Mandatory  believe this information is too detailed for recording. - 2.11: Supporting documents. Mandatory  Should be optional not mandatory. - 2.12: Image ID. Mandatory  Should not be optional. - 2.14 2.15: Remaining Useful Life  These will be estimates. | Condition | 2.06 & 2.07Atributes optional. 2.11 Attribute optional. 2.12 Attribute optional. 2.14 & 2.15 They are calculated but are estimates yes. No changes required. | Vol 2 |  |  | Adjusted in draft |  |  | Included | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | Code List 16: Condition Rating | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | modified mandatory fields | y | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | 2 | 2
302 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 2.5.1 Description of Condition Rating | 36 |  |  |  |  | Code List 5 Condition Rating – Internal Missing description comment for Very Good and Good. | Condition | Agreed. Action: to add. | Vol 2 |  |  | George | For action | Is this addressed in the work you did? 26/3/2017 | Included | Included | Updated in draft Standards | Code List 16: Condition Rating | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed in docs | check if done | n/a | n/a | n/a | [6 empty] | No action |  |  | y | completed | 2 | 2
303 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 3.4 Components | 42 |  |  |  |  | Operations definition à What does this mean? Is this routine/preventative maintenance? | Repairs, Maintenance & Operations | Maintenance attributes defined in Volume 2 | Vol 2 |  |  | George |  |  | Noted: no action required | Noted: no action required | Updated in draft Standards | Repairs, Maintenance and Operations Intervention – Workflow Response Type |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [6 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
304 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 3.4 Components | 43-45 |  |  |  |  | Data Table 3 - 3.02: Activity type. LN is 1  What does this mean? - 3.03/3.03/3.05:  Very onerous – can this be one & same - 3.08 Job Number ID:  Has as an optional field yet has Yes for Mandatory - 3.14 & 3.15:  Geared to different assets – needs hierarchy of building in which this information is mandatory. E.g. toilet* - 3.16 Quantity:  Has as an optional field yet has Yes for Mandatory - 3.19 has deferred:  How is this defined? - 3.20 is deferred:  Surely this isn’t work done then at this point? -3.22 & 3.32 reassurance cycle:  Interesting why this isn’t mandatory? - 3.24 cost: Yes to Mandatory scale of repairs ranges but much is high volume/minor cost e.g. change a tap washer - 3.26 & 3.27 Date cost incurred and date paid:  Why is this important? | Repairs, Maintenance & Operations | 3.02 is Planned, Reactive or operational. no action required. 3.03-3.05 Agreed. Action: Other then start date, all optional. 3.08 Agreed, action: should be optional. 3.14-3.15 Agreed. Action: should be optional as answer may be "zero" 3.16 Agreed, action: change to optional. 3.19 No action needed. Example "it broke because we didn't maintain it -e.g. didn't lubricate bearings". 3.20 No action needed. Attempts to capture future maintenance obligations. 3.22 & 3.23 No action needed. Not mandatory as it may be a reactive repair 3.24 No action needed. Not much point in recording any of this info if we don't capture cost 3.26 & 3.27 Agreed. Action: take out information. Not vital in this context. | Vol 2 |  |  | Adjusted in draft |  |  | Included | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  | modified mandatory fields | y | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | 2 | 2
305 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 3.4 Components | 43-45 |  |  |  |  | [Finance team] – 3.04 Start_time  Delete (not needed) – 3.06 End_time  Delete (not needed) – 3.08 JobLn_ID  Insert: Each Job number per 3.08 can have up to 300 lines, one for each task performed according to the schedule of rates. – 3.09 Image_ID  Change to be optional (there would be a need for in excess of 400 000 images per month if done in detail). - 3.19 & 3.20  Deferred or not, depending on definitions / policy and asset maturity of the respondent organisation this could be prone to great subjectivity and variance in interpretation so some practical application rules will need to support the taxonomy.  No attribute regarding capex or opex – should there be a Boolean Yes or No (or is all R&M assumed to be Opex – I may have missed this in my reading?) | Repairs, Maintenance & Operations | 3.04 -3.06 Agreed, it's optional. No action needed. 3.08 Action: needs to be an optional field. Your comment seems to refer to multiple items that might be done on one "Job" for an individual asset (Say a house). 3.09 Agreed. Action: change to optional field. 3.19 & 3.20 Agreed, Action: change to optional field. Capex is not covered by this schema. That's defined as replacing the asset at end of life. This is about repairing it during its life. No action required. | Vol 2 |  |  | George and Adjusted in draft |  |  | Included | Included | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  | modified mandatory fields | y | These tables have been completely revamped. The analytical intent of the attributes are reflective of what has been included | 2 | 2
306 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 4.4 Calculating Utilisation | 50-51 |  |  |  |  | Data Table 4  Given this is optional surely all these attributes are also optional? - 4.06 & 4.07 Name and Organisation of the assessor  These won’t need to be assessed by external party - 4.06 – 4.09  Assessor info. Questionable of Mandatory. | Utilisation | If you decide to fill it in, some attributes are required and other aren't. 4.06 & 4.07 No action needed. They may be contracted out not all orgs will do in-house 4.06 - 4.09 Optional. | Vol 2 |  |  | Included in draft |  |  | Sector Discussion | Included | Mandatory / Optimal and Optional will be discussed | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | modified mandatory fields | y | Updated comment | 2 | 2
307 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 4.5 Utilisation Code Lists | 52 |  |  |  |  | - Code A, beds occupiedà more relevant for HNZ than- Code H , occupants/m2 | Utilisation | Will vary for different building types | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Included in Draft Standards | Code List 25: Utilisation – Capacity Unit of Measure (Availability) |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
308 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 5.4 Calculating Demand | 55 |  |  |  |  | 5.4 Description of Calculating demand. à Unclear how this would apply in HNZ setting? | Demand | No action required. HNZ has X houses with Y beds, the demand for this housing is presumably different to X and Y we should be able to put one figure over the other to produce a percentage. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Volume 2 is complete in these draft standards | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2 | 2
309 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 6.2 Purpose of Schema | 59 |  |  |  |  | 1st bullet point à E.g. roof? Fire alarms? | Criticality | Can be as granular as needed. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Can be as granular as needed. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | n/a | [5 empty] | No action |  |  |  |  | 2 | 2
310 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 6.6 Calculating Critically | 61 |  |  |  |  | 1st bullet point… In Code list 17Error! Reference source not foundà Mistake that needs fixing. | Criticality | Change reference. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Updated in Draft Standards | No Specific Reference | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  | ? | y | Updated comment | 2 | 2
311 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.1 Definition of risk | 67 |  |  |  |  | à The definition of asset risk does not align with the referenced AS/NZS ISO 31000:2009 & SA/SNZ HB 436:2013 | Risk | Definition is based on the guidelines, not an exact copy. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Definition is based on the guidelines, not an exact copy. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
312 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.4 Components of Risk | 68 |  |  |  |  | The risk schema is focus only on the risk arising from the performance of assets. It fails to consider that risks can also emanate from the attributes of an asset and perhaps in most cases these performance risks are just knocked on risks from the inherent risks evident in an asset’s attributes. The process to link these main sources of risks and how the information are interfaced to inform on the risk/s is unclear in this standard, otherwise there could be an issue of double counting or reporting. | Risk | No change required. This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | This depends on at what level you assign or measure risk. Is the risk assigned at the building level or component. It will vary with each organisation depending on the granularity of their asset data structure. | 4.4 Risk Schema |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | An explanation of Data Science will be provided for at the Technical Working Groups |  |  |  |  | 2 | 2
313 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.4 Components of Risk | 69 |  |  |  |  | Top of page 69 emphasises "vulnerability" as part of Likelihood, but the term vulnerability then does not appear in following sections, e.g., Data Table 7. The reader has to then make their own interpretation as to whether the "product" as used at the top of page 69 is a mathematical product of two numbers, or just a general "combination" to be rolled into one field, e.g. Ref 8.04 in Data Table 7 | Risk | Phrases deleted in newer version. A new schema covering vulnerability has now been created and separated from Risk or Criticality. No action required. | Vol 2 |  |  | Included in draft |  |  | Included | Included | Vulnerability Schema has now been added into the Draft Standards | 4.2 Vulnerability Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | No action |  | N/A | y | completed | 2 | 2
314 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.4 Components of Risk | 69 |  |  |  |  | Section 7.5 "Calculating Risk" leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Risk | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
315 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.5 Calculating Risk | 69 |  |  |  |  |  This section leaves open the possibility of assigning a risk rating that is too high. For example, if there is a 70% chance of a level 1 financial loss (consequence), and 1% chance of a level 5 governance impact (consequence), we probably don't want to state implicitly that there is a 70% chance of a level 5 impact. But 7.5 suggests that could happen. | Risk | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Code List 21 would turn % into a 1-5 scale. The 70% chance would only be significant if it affected a large number of users. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2 | 2
316 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.5 Calculating Risk | 70 |  |  |  |  | Data Table 7  At what level does this need to be assessed, e.g. window? House? Houses in flood zones? | Risk | It's optional depending on the granularity of asset data collection. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | It's optional depending on the granularity of asset data collection. | Data Table 7: Risk Attributes |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
317 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 Risk Code lists | 72 |  |  |  |  | Code G, Malicious damage à Does this include tenant damage? | Risk | Yes | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Now Third Party Damage or Vanadalism | Code List 22: Repairs, Maintenance and Operations Failure Mode – Cause |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
318 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 Risk Code lists | 73 (code List 22) |  |  |  |  | à Reference to risk management guidelines SA/SNZ HB 436:2013 appear to be inaccurate for table C5. Also the guidelines are referred to as SA/SNA HEB 436:2013 so not sure if there is some mismatch in the actual document being referenced. | Risk | Tables are based on the guidelines, not an exact copy. No action required. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Tables are based on the guidelines, not an exact copy. No action required. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
319 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 Risk Code lists | [5 empty] |  This section reproduces tables from SA/SNZ HB 436:2013 and by reference AS/NZS ISO 31000:2009. The practise of reproducing parts of one Standard in another is strongly discouraged because of the potential transposition errors, the loss of context, version issues, and potential for misunderstandings. Good practice is to reference a document and only describe where there are changes from the referenced document in the new document. | Risk | The purpose of the table is to provide the needed information without having to consult another document. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | The purpose of the table is to provide the needed information without having to consult another document. | Code List 39: Risk Rating |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
320 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.7 Consequence Table | 73, 74-79 (code list 22 & 23) |  |  |  |  |  Sections 7.6 and 7.7 are quite specific for likelihood and consequence scales respectively. This has some advantages, however could easily stray into being too prescriptive. Can one scale for each actually serve the needs of organisations which have assets of very different sizes and types? | Risk | We require one standard for all organisation or we can't compare them. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | We require one standard for all organisation or we can't compare them. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
321 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.7 Consequence Table | 73, 74-79 (code list 22 & 23) |  |  |  |  |  The health and safety consequences jump from a 4 Localised Major impact. Individuals could potentially be exposed to circumstances that could cause fatalities to 5 Widespread major impacts. Multiple fatalities might occur. This appears to be a big jump in consequence and the subjective interpretation of localised vs. widespread and how this applies to large number of residential houses physically very close to each other would be difficult to determine. | Risk | Noted. Action: need rewrite, two paragraphs are too similar to reflect difference. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Changes in codelists have addresssed this submission | Code List 10: Minor Event Significance Rating & Code List 11: Major Event Significance Rating |  |  |  | 1 | [5 empty] | 1 | [6 empty] | check if done CHANGE STATUS TO INCLUDED | [9 empty] | Change made document updated - to discuss change Minor 'Comments' |  |  | y | Updated comment | 2
322 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.7 Consequence Table | 73, 74-79 (code list 22 & 23) |  |  |  |  |  Lack of clarity when rating risks (likelihood and consequence) around o For one Address versus Whole Housing Portfolio (How can one catch the latter using ratings on the former? Governance consequence level 5 – loss of permissions to operate - seems to require a portfolio view). o Physical impact on asset versus Community Impact (The consequence scale mixes both. Which is the thing we are rating? Is this the right place for Community impact?) | Risk | Each organisation needs to determine at what level risk will be determined. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | These are asset risks (likelihood and consequence), not cmmunity risks | 4.4 Risk Schema |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
323 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 7.6 & 7.7 | [5 empty] | à Consultation with affected Crown entities and Ministries essential – e.g. how to resolve questions above on 7.6, 7.7? | Risk | No action required. That is what this review is hoping to achieve. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. That is what this review is hoping to achieve. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
324 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 8 Resilience Schema | 82 |  |  |  |  | à HNZ asset maturity / record keeping is not is at this level of development. Very important in other asset companies (e.g. Network companies) but less critical in HNZ. | Resilience | No action required. Understood. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | No action required. Understood. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
325 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.3 Interface with Other Schema | 95 (table 13) |  |  |  |  | - Utilisation column à Insert ✓ under Utilisation column. Utilisation is a key measure on Financial Performance as it affects Revenue. | Financial Performance | Noted and Updated | Vol 2 |  |  | Included in draft |  |  | Included | Included | Changes in codelists have addresssed this submission | 3.2 Utilisation Schema | 1 | [8 empty] | 1 | [6 empty] | check if done | [9 empty] | Haydn |  | N/A | y | Updated comment | 2
326 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 97 (table 10) |  |  |  |  | - 10.03 Revenue_T à Change. In the case of Housing New Zealand you have 2 forms of rent (tenant based & IRR); and damage recoveries | Financial Performance | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | NoTotal revenue is what we are interested in. Other entities will have multiple revenue sources too. | Code List 50 Description of Financial Performance Funding Element |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | To discuss with technical Working Groups |  |  |  |  | 2
327 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 99 (table 10a) |  |  |  |  | –10.20 Image_ID à Change to be optional. We group all chattels together as a single asset for that property making it impossible to load a single image for the asset called chattels. | Financial Performance | The attribute is optional. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | The attribute is optional. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
328 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 104 (table 10d) |  |  |  |  | - 10.47 New_asset à Review/ consider potential practical issues with this – could become subjective especially in the case of replacement and possibly the default setting for New_Asset is “Yes” unless the asset it is replacing can be specifically identified. | Financial Performance | If you can't identify what it is replacing, it is default a new asset. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | If you can't identify what it is replacing, it is default a new asset. | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
329 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 10.4 Measurement of financial performance | 103 (table 10c) |  |  |  |  | - 10.35 to 10.38 à Necessary? Will all this information actually be used in practise – if so what for / subjectivity in 10.38? I would have thought not – just max of one or two records should suffice. | Financial Performance | Each organisation needs to determine at what levelof granularity will suffice. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | Each organisation needs to determine at what level of granularity will suffice. Financial Performance on assets is essential, for some providers - this is the attribute suite to enable it, | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
330 | Andy Walmsley | Housing NZ | Buildings | Vol 2 | 11.6 Service Performance Attributes | 109-112 |  |  |  |  | 11.05 Warm rating  Relevance for HNZ would depend on level of reporting/compliance required as this is a significant area of detail - 11.06 Placemaking rating  How do we interpret this? - 11.07 Use rate.  ‘How useable’ How do we interpret this? - 11.14 Culture requirements for community  Also questionable Mandatory - 11.15 Disabled access provision  What does this mean? - 11.15 to 11.18  Questionable Mandatory - 11.26 Geo-Con Questionable Mandatory | Service Performance | These items are scored in Table 11a & code lists following. They are very subjective assessments and most are optional. Some items should be easily scorable like accessibility. | Vol 2 |  |  | noted |  |  | Noted: no action required | Noted: no action required | These ar at the determination of each sector partner and specific to their context | Table 11: Service Performance Attributes & 5.4.7 Code Lists |  |  |  | 1 | [5 empty] | 1 | [10 empty] | NOTED | [5 empty] | No action |  |  |  |  | 2
331 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 1.5 | 2 | 1 |  |  |  | Add USB memory sticks/hard drives to this list. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | changed 28/2/2017, also for all other specs | Included | Included | changed 28/2/2017, also for all other specs | 1.5 Deliverables | 1 | [8 empty] | 1 | [5 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
332 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 1.5 | 3 | Construction Company |  |  |  | Question: Are there requirements for developers to retain information after transmission? |  |  | Vol 1 |  |  |  | Noted | relevance? We see this as something for the developer to make the call if they retain a copy or not. 28/2/2017 | Noted: no action required | Noted: no action required | relevance? We see this as something for the developer to make the call if they retain a copy or not. 28/2/2017 | 1.5 Deliverables |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
333 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.1.3 | 8 | Dates |  |  |  | Although this date format is fine for NZ, I might suggest consideration be given to explicitly using ISO8601 (YYYY-MM-DD) format to reduce ambiguity for machines and humans. Databases, regardless of configuration, should recognise ISO dates and treat them correctly. |  |  | Vol 1 |  |  |  | Noted | keep current practice. 28/2/2017 | Excluded | Excluded | keep current practice. 28/2/2017 | 2.1.5 Attribute Data Fields |  | 1 | [7 empty] | 1 | [7 empty] | no action | no action | no action | n/a | [5 empty] | No action
334 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.1.8 | 14 | Unique_ID |  |  |  | I'm interested in how this process operates. Council currently assigns IDs after assets are entered into our GIS. How will the developer know which unique ID to safely use? Or is it envisaged that we assign IDs to assets early? |  |  | Vol 1 |  |  |  | Noted | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. 28/2/2017 | Noted: no action required | Noted: no action required | The ID is assigned by the developer for their reference or to assist in clarifacition post delivery. 28/2/2017 | 2.1.10 Common Attributes |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
335 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.2.1 | 18 | Permit_No |  |  |  | Our current identifiers include non-alphanumeric characters (e.g. "-" and "/"). Will these be acceptable? |  |  | Vol 1 |  |  |  | Under Review | need to determine impact of including 'extended' alpha-numeric characters 28/2/2017 | Sector Discussion | Sector Discussion | need to determine impact of including 'extended' alpha-numeric characters 28/2/2017 | 2.2.1 Area of Work Extent |  |  | 1 | [6 empty] | 1 | [16 empty] | More information required for a decision
336 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.1 | 25 | Length_m |  |  |  | For circular assets, should length and width both be populated and be the same (diameter)? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | For circular assets, length is not required and will be made conditional 28/2/2017 | Included | Included | For circular assets, length is not required and will be made conditional 28/2/2017 | 2.3.1 Containment Structure | 1 | [8 empty] | 1 | [5 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
337 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.1 | 25 | Length_m |  |  |  | Rename to Length Metres for consistency |  |  | Vol 1 |  |  |  | INCLUDED - DOC | change all instances to length metres and length millimetres as appropriate 28/2/2017 | Included | Included | change all instances to length metres and length millimetres as appropriate 28/2/2017 | 2.3.1 Containment Structure | 1 | [8 empty] | 1 | [5 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
338 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.1 | 27 | OS_RL |  |  |  | Overflow = OS? What does OS stand for? Should this be OF? |  |  | Vol 1 |  |  |  | Noted | this term was agreed to by the TWG, retain 28/2/2017 | Noted: no action required | Noted: no action required | this term was agreed to by the TWG, retain 28/2/2017 | 2.3.1 Containment Structure |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
339 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.3.4 | 41 | 1 |  |  |  | Earlier wells were requested to be polygon type. Is the point supplementary? |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | typo corrected, should be polygon 28/2/2017 | Included | Included | typo corrected, should be polygon 28/2/2017 | 2.3.4 Well | 1 | [8 empty] | 1 | [5 empty] | done | change needed | done | come back to this as not included at moment | done | n/a |  |  |  |  | come back to this as not included at moment | Change made document updated
340 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.4.6 | 69 | Note |  |  |  | I support a clear separation between water authority infrastructure and on-property infrastructure. However, we often have non-council-owned pipe in rights-of-way, or to rear sections, which we are often given information on and would like to retain this (but not require it). Given the presence of an 'owner' field, could the possibility of a separate pipe asset with 'owner' as "Private" or similar be provided for? |  |  | Vol 1 |  |  |  | George/Haydn | need more information, 2.4.6 refers to a pumping station? 28/2/2016 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.4.6 Pump Station |  |  | 1 | [6 empty] | 1 |  |  |  | ok |  |  | It is upto each asset owner to determine the most appropriate way to manage non authority data | no action | no action | no action | n/a | [5 empty] | More information required for a decision
341 | Chris Stanley | Ashburton District Council | Potable water | Vol 1 | 2.5.1 | 92 | Manu |  |  |  | I believe this table and its attribute names have become mis-aligned. |  |  | Vol 1 |  |  |  | Under Review | Looks OK, need more information 28/2/2017 | Sector Discussion | Sector Discussion | Looks OK, need more information 28/2/2017 | 2.5.1 Equipment |  |  | 1 | [6 empty] | 1 | [16 empty] | More information required for a decision
342 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 1.6 | 3 | R&M/O |  |  |  | The wording here implies that if a pipe is replaced 1:1 with a newer but identically performing pipe, then the new pipe is not a new asset? |  |  | Vol 1 | Not the intention, all replacements are 'new assets' when replaced |  |  | Haydn | cant see that myself 10/03/2017 | Noted: no action required | Noted: no action required | Not the intention, all replacements are 'new assets' when replaced | 2.3.4 Pipe |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | n/a | [5 empty] | No action
343 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 1.8 | 3 | Pumping Station |  |  |  | Having drawn hundreds of these for our city, there are many unexpected ways to have to define the boundary of a pump station, and I would not want to require a contractor to redraw their pump station boundary because it doesn't follow the right fence, or the right garden, or because it should exclude a watercourse for example. If council is deciding what and where the stations are called, then surely it's more efficient to handle these management areas in-house? Also, at CCC we require these stations to already be created in the asset management system before the commissioning, which can be months or in some cases years ahead of the official project data supply. |  |  | Vol 1 | The standrds are recording as-constructed |  |  | Haydn | This is indicative and expect to be advised by Council 10/03/2017 | Noted: no action required | Noted: no action required | The standrds are recording as-constructed | 1.8 Theme Structure |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
344 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 1.8 | 3 | Valve |  |  |  | How do we deal with combinations of these features? An air valve inside a manhole on a pressure main is clearly two separate node features, but what about a pressure flush valve that's in a box the size of a hydrant? Or a vacuum maintenance riser? At what point does the box the valve sits within become too small to be recorded as an individual chamber asset? |  |  | Vol 1 | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID |  |  | Haydn | Is this a question of how each organisation will record and manage? 14/3/2017 | Noted: no action required | Noted: no action required | Each organisation will decise how it does this. A common response is to have different AssetIDs with the same LocationID | 1.8 Theme Structure |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
345 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.1.1 | 6 | 2 |  |  |  | I'm glad these distinctions are mentioned. It is all too common to have an extremely precise location of the wrong part of an asset. And it's only through relative accuracies that such errors can be spotted. |  |  | Vol 1 |  |  |  | Noted | 2017-03-10 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
346 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.1.1 | 6 | 6 |  |  |  | I'm happy to discuss our experience of this in Chch, where the earthquakes blew out the absolute accuracy of much of the network, and for a long time we had significant issues in integrating the new post-quake as built surveys into the old dataset. |  |  | Vol 1 | That is a special case, the spatial component is a standard requirement for all infrastructure |  |  | Haydn | would be happy to discuss with him 10/03/2017 | Noted: no action required | Noted: no action required | That is a special case, the spatial component is a standard requirement for all infrastructure | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
347 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.2.1 | 17 | 1 |  |  |  | This project ID is missing from the asset attribute tables. Planning, processing reporting, cost allocation on SCIRT projects at CCC would be severely hampered if all asset data was not designed and as built with a project number. It may seem obvious to suggest that all data in a submission is from a single project, but (especially) staged project submissions break this rule. The pipe from one project may connect into a manhole from an earlier project, but both will be surveyed and supplied under the later project. A project ID has to exist at the asset level to be certain of the asset's origin. |  |  | Vol 1 |  |  |  | George/Haydn | Can this be added into the comments field where from a different project? 14/03/2017 | Sector Discussion | Included | To be reviewed by Technical Working Groups - intent to include | 2.2.1 Area of Work Extent |  |  | 1 | [6 empty] | 1 |  |  |  | change to sector discussion for consideration for inclusion |  | make mention of change request | [9 empty] | request documented | More information required for a decision
348 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.2.1 | 17 | 1 |  |  |  | What is the expected timing of the submission of this project boundary? If it is for use where works "have been or are intended to be", then that implies this data could be submitted to Council before construction starts. Might it then require attributes to describe the expected gates or stages of the project, especially to "monitor progress" (e.g. construction start date, construction end date, defects liability end date)? |  |  | Vol 1 |  |  |  | Noted | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed 14/03/2017 | Noted: no action required | Noted: no action required | The project boundary is submitted at practical completion. It is only intended to record the area where works have been completed | 2.2.1 Area of Work Extent |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
349 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | 3 |  |  |  | For many vented manhole, large, or non-standard manholes, the centre of the lid is not positioned above the centre of the chamber. How can we ensure a surveyor does not survey the centre of the lid, claiming it to be the centre of the chamber? The standards must very clear about this, and leave zero room for interpretation. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. 14/3/2017 | Included | Included | The point is placed on the lid but is not intended to be the cetre of the lid. Diagram to be altered to reflect the actual requirement. While the point is requested to be the central location in practical terms it is likely to be at the intersection of the mains coming into the manhole. There is a requirement for a point and a polygon to be provided to be able to see the extents of the structure. | 2.3.1 Access Chamber | 1 | [7 empty] | 1 | [6 empty] | make mention of change request clarify comment |  | done | done | done | n/a |  |  |  |  | request documented | Change made document updated
350 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | Figure 4 |  |  |  | The Access node shown is not at the centre of the structure. You need to be clear about why is this allowed, when it is so clearly stated above that the access point must be at the centre. |  |  | Vol 1 |  |  |  | Noted | see comment 349 14/03/2017 | Noted: no action required | Noted: no action required | see ID 349 | 2.3.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
351 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 20 | Figure 4 |  |  |  | Does the access node represent the centre of the structure, or the lid? What if there are two lids? Three lids? What if like the wet well for the refurbished Pump Station 2 in Chch that still has an original manhole lid, but also two modern SIKA lids? How does that repair affect the representation of the asset under this model? |  |  | Vol 1 |  |  |  | Noted | see comment 349 14/03/2017 | Noted: no action required | Noted: no action required | see ID 349 | 2.3.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
352 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.1 | 21 | 2 |  |  |  | Does the polygon refer to the interior or exterior extent of the chamber? Earlier in this document, the word 'perimeter' is used for this, which would indicate the exterior edge is to be used. However, the attributes for chamber width below indicate internal diameters. There will be confusion if circular concrete manholes are specified by their internal diameter - i.e. DN1050 - but a 1050mm circle is not acceptable to represent it. |  |  | Vol 1 |  |  |  | Noted | The polygon refers to the interior of the structure 14/03/2017 | Noted: no action required | Noted: no action required | The polygon refers to the interior of the structure | 2.3.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
353 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.3 | 34 | 4 |  |  |  | If Pipes are snapped to Accesses, and Fittings are then snapped to pipes, survey accuracy will be reduced or even lost by doing this. A surveyed fitting will give a better position along a pipe than a straight line drawn between two manhole lids. |  |  | Vol 1 |  |  |  | Noted | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. 14/03/2017 | Noted: no action required | Noted: no action required | The difference between the two will not be significant as long as the instruction for placing the pipe feature is followed. E.g. the two points are not placed then a line drawn between them as this will not take into account any deviation from the edge of the sdtructure as per the example of an irregular shaped pit. | 2.3.3 Fitting |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
354 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.3 | 34 | Figure 8 |  |  |  | If the diagram represents one pipe, and the diamond is a reducer, then what would be the pipe's diameter? |  |  | Vol 1 |  |  |  | Noted | Whatever is stated in the attributes 14/03/2017 | Noted: no action required | Noted: no action required | Whatever is stated in the attributes | 2.3.3 Fitting |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
355 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.3 | 34 | Figure 8 |  |  |  | Pressure Main 138 crosses above a stormwater culvert. To do this, the DN400 PE100 PN10 pipe bends toward to road surface, gets a concrete capping, reduces to DN355, reduces again to a DN250 DI PN16 in a reinforced concrete surround, before bending back down deeper, back to a DN400 PE100 PN10. If this pressure main is managed as one asset, what is are its diameters? Material? Pressure class? Under this model how do we locate the Pipe Protection? We have a workaround at CCC of deriving a second pipe network, by merging similar pipes together into larger assets for easier management. These standards head straight for the end goal of representing the asset-management-focused asset, and not what's actually in the ground. |  |  | Vol 1 |  |  |  | George/Haydn | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | Sector Discussion | Sector Discussion | In this scenario a node will be placed at each change of pipe. Need to consider pipe protection layer? Possibly as a polygon to reflect the extent of it. | 2.3.3 Fitting |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
356 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 3 |  |  |  | Are each pipe types required to be captured to the same level of detail? Typically, laterals or private pipes are not so important to the function or value of the network, therefore not all attributes are mandatory like they would be for a Main. It would be an enormous burden with debatable benefit to require survey accurate XYZ for all new laterals. |  |  | Vol 1 |  |  |  | George/Haydn | It has been identified through the workshops that this level of detail is required to efefctively manage the asset. 14/03/2017 | Sector Discussion | Included | No - Not expected to capture the same level of detail (e.g. lateral and main) | 2.3.4 Pipe |  |  | 1 | [6 empty] | 1 |  |  |  | suggest that direction is provided otherwise it will be a smorgasbord or requirements suggested by each organisation creating uncertainty for the data providers | Will do that but how is a discussion with the sector | [11 empty] | More information required for a decision
357 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 6 |  |  |  | This should be expanded upon. List every possible asset or feature that can define the start or end node of a pipe. Gravity networks are the only ones with access chambers. Our wastewater model has issues with representing vacuum networks, and this standard doesn't address or solve those issues like I hoped they would. |  |  | Vol 1 |  |  |  | Under Review | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. 14/03/2017 | Sector Discussion | Sector Discussion | The intent is to provide the detail about the assets that are in the network for the asset owner to determine the most apprppriate way to manage them in their systems. Please advise what the issues are so that we can consider if they can be covered. | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
358 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 8 |  |  |  | I understand the intent of this, and how difficult it is to convey the sense of what a faithful representation is, but you must know that such loose wording will be abused by lazy contractors. Try to define the faithful representation in absolute terms, like all segments of the polyline must be 100% within a set tolerance/distance from the actual pipe, including around curves. |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-14 | Included | Included | Precision is defined in the standards | 2.3.4 Pipe | 1 | [8 empty] | 1 |  |  |  | what is to be included? | updated comment |  |  | done | done | done | n/a | [5 empty] | No action
359 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 10 |  |  |  | These two bullet points are not specific to pipes, and are more of a general requirement of the data submission. Maybe move them up to 1.8 or 1.9 with the general comments about the data structure. |  |  | Vol 1 |  |  |  | Under Review | Please be specific about which statements 14/03/2017 | Sector Discussion | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
360 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 11 |  |  |  | The obvious question is what if the centreline of the pipe doesn't line up with the centre of the chamber? Then snapping like this would artificially introduce error. |  |  | Vol 1 |  |  |  | Noted | Please refer to the example for the irregular shaped structures 14/03/2017 | Noted: no action required | Noted: no action required | Please refer to the example for the irregular shaped structures | 2.3.4 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
361 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 12 |  |  |  | These changes should be coded into the pipe geometry, not as separate notes about the pipe. |  |  | Vol 1 |  |  |  | Under Review | Please be specific about which statements 14/03/2017 | Sector Discussion | Sector Discussion | Please be specific about which statements | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
362 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 12 |  |  |  | From the water supply pipe definition: "Pressure main characteristics may change, such as pipe diameter, pipe type or pipe construction date. When this occurs a new section is to be created." If these standard's goals of "Providing a structure for the consistent recording of all council, utility and water authority owned assets" are to be met, then the definition of a pipe, any pipe regardless of network, must be the same. If a reducer on a potable water main splits the pipe feature, and a reducer on a wastewater pressure main doesn't split the pipe, then it will continue to be impossible for there to be consistent recording, management or analysis of those pipes. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Noted adjustments will be made for consistency. 14/3/2017 | Included | Included | Noted adjustments will be made for consistency. | 2.3.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Changes made documents updated
363 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.3.4 | 39 | 12 |  |  |  | This pipe definition is so far incompatible with representing a vacuum wastewater network. The requirements and features of a vacuum network are entirely different to those of a gravity or pressure network. The modality of vacuum-specific features like maintenance risers, lift points, interceptor/collector tanks etc. will need to be comprehensively defined. Or if, for example an engineer wants to identify all lengths of pipe where the grade is flatter than 1:500, that will be impossible unless inverts are recorded at all points. |  |  | Vol 1 |  |  |  | Under Review | Please provide examples of specific instances so they can be considered for inclusion 14/03/2017 | Sector Discussion | Sector Discussion | Please provide examples of specific instances so they can be considered for inclusion | 2.3.4 Pipe |  |  | 1 | [5 empty] | 1 | [11 empty] | n/a | [5 empty] | More information required for a decision
364 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 43 | Unique_ID |  |  |  | What if the pipe is a gravity collector? Or two syphons running in parallel, sharing the same nodes? The contractor's ID has to be unique, even if two pipes have the same nodes. |  |  | Vol 1 |  |  |  | Noted | There will be two assets provided therefore there will be two contractor ID's 14/03/2017 | Noted: no action required | Noted: no action required | There will be two assets provided therefore there will be two contractor ID's | 2.3.4 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
365 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 43 | Owner |  |  |  | This attribute will be incredibly unreliable. I would never trust a contractor to tell me who owns an asset. |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
366 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 44 | Cost |  |  |  | Please specify which cost is meant, and for which purpose? Purchase cost? Installation cost? Replacement cost? What if this information is commercially sensitive? Assume this data could be publicly available. |  |  | Vol 1 | ODRC / ORC / RC are included |  |  | Haydn | 2017-03-14 | Included | Included | ODRC / ORC / RC are included | Code List 47: Financial Performance Metrics | 1 | [7 empty] | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
367 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 51 | Grnd_Water |  |  |  | Many of the attributes from here to the end of the list can and will often change along the length of a pipe. If the pipe asset is not going to be split where those attributes change so that they can be accurately recorded, then I would argue that implies the pipe asset is not the appropriate place to record those attributes. |  |  | Vol 1 |  |  |  | George/Haydn | Have no view on this 14/03/2017 | Sector Discussion | Sector Discussion | Soil type is important and registered against each asset and Asset ID Required for analytical purposes | 2.3.4 Pipe |  |  | 1 | [6 empty] | 1 |  |  |  | this discussion is not aboput the actual pipe but about the attribute fields of soil etc in the pipe table. Please review and re draft response | updated comment not answered | [11 empty] | More information required for a decision
368 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 52 | RI_Rn_Mtd |  |  |  | This attribute cannot be simply added to the list of attributes as if it is unrelated to repairs and maintenance. It is crucially important to get the representation right. Is this a repair or a renewal? Does a renewal ever define a new asset? This example has happened (albeit in stormwater, but these standards apply cross-networks). If 60% of a pipe is relaid (CONC -> UPVC), and the remaining 40% is CIPP lined due to the terrain, then how much of the original asset remains? And if there is a new asset, how should it be tied back to the original? What is the pressure class of a DN150 EW pipe that has been burst by a DN180 PE100 PN10? To what extent does the pipe burst override the core attributes of the pipe asset? |  |  | Vol 1 |  |  |  | George/Haydn | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | Included | Included | The intent of the schema is to record what has been contructed at practical completeion of a subdivision development or capital project How it's treated after the data is provided is upto each asset owner. | 2.3.4 Pipe | 1 | [8 empty] | 1 |  |  |  | ok | [12 empty] | No action
369 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 4.3.4 | 53 | RI_RN_Mat |  |  |  | What about a Renewal date? For example there were changes in Cast Iron rejuvenating practices here during the 1990's, and if we didn't have that rejuvenation date recorded on the affected pipes we wouldn't have been able to accurately describe now what the true statuses of those pipes are. The method may be named the same, but the end result can be different. When the Chch brick barrels were CIPP lined, some have a lining thickness of more than 20 or 30mm, which is important to measure and record, especially for flow modeling purposes |  |  | Vol 1 |  |  |  | George/Haydn | The date of construction is to be used. Was the thickness recorded to address heat transfer? What is the impact of it not being recorded? 14/03/2017 | Sector Discussion | Sector Discussion | This is a refurbishment, and treated as a new asset, with new assetID and data set | 2.3.4 Pipe |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
370 | Chris Tredinnick | SCIRT | Wastewater | Vol 1 | 2.7.2 | 106 | 3 |  |  |  | This responsibility is back-to-front. It is the responsibility of the consultant to provide the best data they can within the standards, and for the Local Government to highlight any inaccuracies. Only the Local Govt can decide what level of discrepancy is worth querying. With the standards as they are, the consultant will either quietly 'fix' their survey to match an incorrect old survey, or blame the old survey for the inaccuracies in their new survey. |  |  | Vol 1 |  |  |  | George/Haydn | There is no obligation for the consultant to match their data to the existing infrastructure. The obligation is to show where existing infrastructurwe does not align with the new infrastruture from a mapping perspective. That is from mapping data they have been proviided with and are expected to align to. There are two aspects to this requirement. Firstly that the consultant identifies the anomaly and secondly that the Local Governmnet addresses the adjustment in their information systems. 14/03/2017 | Sector Discussion | Sector Discussion | Service provider is required to deliver survey data as required. Local government is required to manage the accuracy of their data sets, including geospatial data | General |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
371 | Gerri Waterkamp | Auckland Transport | Stormwater | Vol 1 & Vol 2 | General | [5 empty] | I have reviewed the docs for Stormwater. There is some good work, however it is very heavily focussed on the reticulation of Stormwater over the initial point capture of road run off. The absence of standard naming convention – i.e. generic names across asset types . i.e. Catchpit for all road located devices for collecting and redistributing road run off, not mud tanks, sumps, cesspits etc. is an area which needs developing, as it is these names that provide a barrier for understanding. It is one of the main things missing from Civils construction and data capture as a whole, and changes dependant on geographical location in NZ. Road Stormwater devices, versus the piped Stormwater network, are not well captured, and in the meeting I was present in, were not part of the discussion. I think there needs to be more or a separate discussion on data capture and metadata standards for road network devices. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Comments noted. Workshops will be held in May for further contribution | Sector Discussion | Sector Discussion | Comments noted. Workshops will be held in May for further contribution | General |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
372 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | What are the timeframes for this being adopted as mandatory? | Implementation | Business Case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case. | General |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | NO ACTION | NO ACTION | NO ACTION | NO ACTION | [5 empty] | No action
373 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Will there be a further round of submissions / comments? | Implementation | Yes. Seminars in November. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Yes. Seminars in November. | N/A |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | NO ACTION | NO ACTION | NO ACTION | NO ACTION | [5 empty] | No action
374 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | We need to know which data attributes are mandatory, aspirational, desired in order to implement. We’re going through an Asset Systems review and would like to implement mandatory requirements as soon as possible. | Mandatory Fields | Mandatory - industry best practice - optional to be included. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Mandatory, Optimal, Optional will be discussed with the sectors | General | 1 | [7 empty] | 1 |  |  |  |  | review with haydn when will optional be included and how selected | Mandatory vs Optimum vs Optional Data sets |  | action needed once agreed with haydn | action needed once agreed with haydn | action needed once agreed with haydn | action needed once agreed with haydn | action needed once agreed with haydn | [5 empty] | More information required for a decision |  | ? | y | Updated comment
375 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | This has been presented as a schema, seeming to indicate the preference for one particular system that adheres to this schema. Our current system can’t adhere to this as it hasn’t been built with this architecture and is impossible to modify. Are these requirements intended to be for reporting purposes only, so that all councils can report across common fields, or are they indicative of a mandatory set up of AMS systems? If the latter, we have all been set up to fail compliance in the short term, and long term we’ll all be moving to a single system. It would be good to know as soon as possible what this system is so that we can start budgeting and planning for the inevitable purchase and data migration. | Implementation | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case. Intention is for standard to be system agnostic. Data scientists to confirm. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
376 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Please combine 3 waters into one document so that there is less repetition. Most councils cover all three waters. Separate different asset types as appendices to the generic stuff. We’ve spent a lot of time studying all three documents to find out what the differences are, only to discover that there’s a lot of repetition. | Volume Interaction | Statement noted. HR to confirm. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Each document has it's own suite of specific content | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | Sector discussion |  |  |  |  | 2
377 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Preamble about treatment being / not being included in Water asbuilt is confusing and contradictory. (Potable Water Vol 2 page 11 on pdf, section 1.1) | Coverage | Action - to be looked at by Opus. | Vol 1 - Vol 2 |  | Treatment is not included |  |  |  | Noted: no action required | Noted: no action required | Treatment is not included | No Specific Reference |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action |  |  |  |  | 2
378 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Inconsistency in use of terminology “Asset type” (Potable Water Vol 1 page 17 on the pdf numbering) and “Asset class” (page 21 of the same). Also the latter has three extra Asset Types viz. Pumping station, Retaining structure, Wing wall. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Asset Classifications have been defined in the Standards | 1.7 Heirarchy & 1.8 Theme Structure | 1 | [8 empty] | 1 |  |  |  | ok |  | review against standard |  | done | done | done | n/a | [5 empty] | Changes made documents updated |  | N/A
379 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Where does Telemetry fit into the schema? Is this part of “instrumentation”? | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Treatment is not included |  |  |  | Noted: no action required | Noted: no action required | Included in Instruments | Instruments |  |  |  | 1 | [5 empty] | 1 | [16 empty] | No action
380 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | What do the colour codes mean? E.g. Potable Water Vol 1 page 29 section 2.1.7. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Endeavouring to differentiate information 26/3/2017 | Noted: no action required | Noted: no action required | Separate sections of data cohorts | General |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | No action
381 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Seems to follow Australian standards rather than NZ e.g. water meter arrangement (Potable Water Vol 1 page 148 section 2.7.1) | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | noted | Comments noted. Workshops will be held in May for further contribution. | Sector Discussion | Noted: no action required | Comments noted. Workshops will be held in May for further contribution. | 2.7.1 Instruments |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision
382 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | A lot of incorrect details in the documents seem to indicate that they are still a work in progress, e.g. page numbering incorrect, incomplete tables, references and contacts having xx placeholders instead of correct information. (hence question 2 about a further round of submissions as we can’t comment on incomplete data). | QA | Statement noted. To be actioned. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Statement noted. To be actioned. | General | 1 | [8 empty] | 1 |  |  |  | previously missed still some xx placegolders for haydn to address at start of document | Publishers edit completed | change needed in docs |  | done | done | done | done | [5 empty] | Changes made documents updated |  | ?
383 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Well / bore naming – we have separate Asset Types for Well and Bore as they are different assets. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | Sector Discussion | Sector Discussion | Comments noted. Assets that have similar attributes have been groupes to reduce the number of tables, however this will not prevent the asset owner to clasiffy the assets post deliver of data Workshops will be held in May for further contribution. | 2.3.4 Well |  |  | 1 | [6 empty] | 1 |  |  |  | ok |  |  |  | no action | no action | no action | no action | [5 empty] | No action |  | N/A
384 | Jenny Komarovsky | Tasman District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | USB and hard disk or e-mail / upload options are preferable to the old technology of CDs and DVDs. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Modify section 1.5 to remove CD label representation and include with section 1.5.1 table. 26/3/2017 | Included | Included | Standards will be updated | 1.5 Deliverables | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed in docs |  | done | done | done | done | [5 empty] | Changes made documents updated |  | N/A
385 | Jennifer Carew | Waipa Distric Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Rather than commenting on the PDFs themselves, I just have a few generic comments that I would like included for consideration. I am still concerned about the level of complexity that the standards have outlined, during the workshops we discussed the different levels that councils could work towards – what data was included in the bare mandatory requirements being important for smaller councils as the implementation of the ‘full suite’ of data would be unrealistic for many of us. If the standards could clearly outline the mandatory / intermediate / advanced levels, ensuring that the mandatory level is indeed achievable for small councils, I personally feel that they might be received with a little more enthusiasm. I have presented the concept of the standards to a few different groups now, and there was a significant concern around implementation and costs associated with such a significant step change in not only what data was being collected but also the implementation of the relationships between the tables driving the analysis (particularly from Volume 2 for each of the water standards). | Mandatory Fields | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | Vol 1 - Vol 2 |  | noted |  |  |  | Sector Discussion | Included | Mandatory - industry best practice - optional to be included - discussion with sector which applies where. | General | 1 | [8 empty] | 1 | [6 empty] | action needed once agreed with haydn | [9 empty] | More information required for a decision |  | ? | y | Updated comment
386 | Graham Clark | Christchurch City Council | Wastewater | Vol 1 | General | [5 empty] | As Constructed is not meta data standard it is a DATA standard for asset physical and location attributes. |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | no action | [5 empty] | No action
387 | Graham Clark | Christchurch City Council | Wastewater | Vol 1 | Abstract | i | 1 |  |  |  | a standardised approach to the collation of data relating to As Built (As Constructed) asset information |  |  | Vol 1 |  |  |  | Noted | 2017-03-14 | Noted: no action required | Noted: no action required | Reviewed and Noted only | Abstract |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | no action | [5 empty] | No action
388 | Graham Clark | Christchurch City Council | Wastewater | Vol 1 | Executive Summary | iv | 4 |  |  |  | Primary reason is missing. This provide the common language framework to facilitate the sharing of asset information throughout NZ. It enable the ability for wellington to d=share data with Christchurch and Auckland etc. through the ability to map to a common language The Standard. |  |  | Vol 1 | Could do yes - I can add in |  |  | Haydn | Do you want to include? 14/03/2017 | Included | Included | Will consdider for final edit - happy to add in. | Executive Summary | 1 | [8 empty] | 1 | [6 empty] | check with haydn | [9 empty] | Haydn |  |  | y | Updated comment
389 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 1.5 | 2 | 1 |  |  |  | This seems to be out of date. We do not want to receive cds or dvds and 5 MB seems like a very low limit for emails these days. |  |  | Vol 1 |  |  |  | Under Review | Need recommended maximum attachment size 28/2/2017 | Sector Discussion | Sector Discussion | Need recommended maximum attachment size 28/2/2017 | 1.5 Deliverables |  |  | 1 | [6 empty] | 1 | [6 empty] | each organisation to determine practical limits | done | done | done | done | [5 empty] | More information required for a decision
390 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.1.1 | 7 | 1 |  |  |  | We receive property boundaries from LINZ. We cannot adjust it even if a surveyor says it is in the wrong position. Do not see the purpose of this requirement. |  |  | Vol 1 |  |  |  | Noted | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. 28/2/2017 | Noted: no action required | Noted: no action required | Property boundaries are not to be moved. The objective is to maintain relative alignment and variations to 'actual' locations to potentially identify areas for LINZ (or similar agencies) for future enhancement. 28/2/2017 | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 | [5 empty] | 1 | [7 empty] | no action | no action | no action | no action | [5 empty] | No action
391 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.1.2 | 8 | 5 |  |  |  | This should not be NZ Vertical Datum 2009, This was superseded by NZVD 2016 in July 2016. |  |  | Vol 1 |  |  |  | Noted | picked up previously 28/2/2017 | Included | Included | picked up previously 28/2/2017 | 2.1.2 Projections and Datums | 1 | [16 empty] | done | done | done | done | [5 empty] | Change made document updated
392 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.4 | 65 | 7 |  |  |  | Node_Type is either From or To. All nodes are both, they are the from node for a pipe and the to node for another pipe. |  |  | Vol 1 |  |  |  | Noted | agreed, but per pipe section, there is a from-node and a to-node, one of each. 28/2/2017 | Noted: no action required | Noted: no action required | agreed, but per pipe section, there is a from-node and a to-node, one of each. 28/2/2017 | 2.4.4 Node |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
393 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.5 | 67 | 5 |  |  |  | We split pipes when there is a valve or hydrant on them. While other councils may not |  |  | Vol 1 |  |  |  | Noted | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. 28/2/2017 | Noted: no action required | Noted: no action required | instructions are for consultant's to collect data in a consistent manner. Council can then deal with asset in a manner for their circumstances. 28/2/2017 | 2.4.5 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
394 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.5 | 67 | 6 |  |  |  | This is a good idea and we support this but it is some times not possible. Some pipes flow in multiple directions. |  |  | Vol 1 |  |  |  | Under Review | need examples 28/2/2017 | Sector Discussion | Sector Discussion | need examples 28/2/2017 | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
395 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.4.6 | 74 | Pipe Attribute & Validation File Format Instructions Diameter |  |  |  | The attributes list Internal Diameter, Nominal Diameter, External Diameter and Nominal Bore. Are all these necessary. It appears to be a duplication of information. |  |  | Vol 1 |  |  |  | George/Haydn | this was agreed to by the TWG, what is your suggestion? 28/2/2017 | Included | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.3.4 Pipe | 1 | [8 empty] | 1 |  |  |  | ok | [12 empty] | No action
396 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.5.2 | 95 | Pump Attribute & Validation File Format Instructions |  |  |  | A lot of the attributes seem to be duplicated |  |  | Vol 1 |  |  |  | Noted | attributes are all different 28/2/2017 | Noted: no action required | Noted: no action required | attributes are all different 28/2/2017 | 2.5.2 Pump |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
397 | Coral-Lee Ertel | Western Bay of Plenty District Council | Potable water | Vol 1 | 2.7.1 | 132 | Figure 44 |  |  |  | The diagram shows a house connection with a node where the connection joins to the main. Earlier in the document it says that house connections do not have a node that splits the main. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | agreed, diagram will be corrected 28/2/2017 | Included | Included | agreed, diagram will be corrected 28/2/2017 | 2.7.1 Instruments | 1 | [7 empty] | 1 | [7 empty] | change needed DOC need to find or create new diagrams | [9 empty] | No action
398 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | It is noted that different revisions of the draft standards have been made available on the LINZ website over the period of seeking feedback and that these have not been issues with updated version numbers (some dated June 2016 some dated 14 July 2016, yet with the same version number). It is also noted that the cover page version number differs from the footer version number. This does not give a high degree of confidence that the development of these documents is being controlled to level as would be required for a national standard. | QA | Noted | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Updated | General | 1 | [7 empty] | 1 | [17 empty] | Changes made documents updated |  | ?
399 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | We also note that there are a lot of references to the transport and building standards that appear to be wrongly included in the 3 waters documents. There are also a numerous spelling and editing mistakes in the draft document, feedback from staff that have looked at the document is that it is not in a fit state to be reviewed. | QA | Updated | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Updated | General | 1 | [7 empty] | 1 | [17 empty] | Changes made documents updated |  | ?
400 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Purpose The scope of this document is unclear in terms of: • Type of document – It is currently referred to as a specification, standard, guidance document and working paper. This makes it unclear as to whether it will be mandatory or optional for 3 water utilities to adopt. | Implementation | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | To be considered in business case. Action: Clarify that the document is a standard. In the front end. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
401 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Purpose The scope of this document is unclear in terms of: • Purpose of the document – The documents are referred to as metadata standards, but based on the intended 5 volumes of the standard appear to cover more than just metadata. It is noted that the LINZ website says “remembering these standards are asset management data standards for analytical purposes”. We believe that it needs to be clear whether these are metadata standards or asset management standards. | Metadata terminology | This is a metadata standard not asset management standards. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | This is a metadata standard not asset management standards. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
402 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Purpose The scope of this document is unclear in terms of: • Use/ application of document – It is very confusing as to whether these documents are for asset owners (and management and use their systems and data) or for thirds parties (i.e.: suppliers, consultants and contractors) providing data to asset owners. Volume 1 is written as if the latter is the intent of how these document will be used, it is stated on page v that “the main objective of this standard specification is to provide information to the consultants who will be dealing with any public asset owner” and in Section 1 on page 1 “this document outlines the specifications for the delivery of digital data”. This seems to not be the actual intended use of this document and should be corrected so that it is more encompassing. | Implementation | Updated | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Updated | General | 1 | [7 empty] | 1 | [6 empty] | Use of Spec… change needed in docs |  | done | done | done | done | [5 empty] | Changes made documents updated |  | ?
403 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • Reference is made to “as-manufactured”, “as-constructed” and “as-built”. We considered that this should be just referred to as “as-built” which is the common terminology in New Zealand. | QA | These are differentr in some cases / in others they are not, not the same definitions across sectors | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | These are differentr in some cases / in others they are not, not the same definitions across sectors | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
404 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • As mentioned above volume 1 appears to be written as a specification for delivery of information. It includes instructions for delivery of information which are out of date (i.e.: labelling CD’s and providing fax numbers), which should be up to the individual councils to determine how they will receive information. | NA | This is a volume 3 exercise | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | This is a volume 3 exercise | 1.5 Deliverables |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
405 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • There is scope to avoid repetition in the asset tables where generic information is required. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action required: data scientists reviewed | No Specific Reference | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | No action |  |  |  |  | 1 | 1
406 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The structure of this document: • It appears that this document, particularly volume 1, is heavily based on the GISSA W-Spec. Background on the development and linkage with W-Spec should be included for transparency. | NA | References to be removed. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | References to be removed. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
407 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Treatment facilities – it is implied in Section 1.4.1 that treatment plants and large pumping facilities can be covered by other standards. We do not consider that these standards adequately cover what would be required to capture the assets data of such facilities. Note that reference to the building specification also needs to be included in the list. | Coverage | No action required. These standards do not cover treatment plants. Requirements for covering treatments plants will be developed later. Reference can be made to buildings, do not see if this will add value though | Vol 1 - Vol 2 |  | Treatment is not included |  |  |  | Noted: no action required | Noted: no action required | Treatment is not included | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
408 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Resource consents – are considered to be an asset within our Council and we record, track and monitor them within our AMS system. | Service Performance | Out of scope. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Out of scope. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
409 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Land – no parameters are set for the recoding of land information. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Not part of this scope. 26/3/2017 | Excluded | Excluded | Out of scope. | No Specific Reference |  | 1 | [7 empty] | 1 |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
410 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Vulnerability – is mentioned under Section 1.2 on page 1, but not included in this list of asset management attributes on page 3. It is missing from volume 2 altogether and is a key part of asset management. | Vulnerability | Action required. Vulnerability is developed as a separate schema. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Changes in codelists have addresssed this submission | 4 Vulnerability, Criticality, Risk and Resilience 4.2 Vulnerability Schema | Vulnerability, Criticality, Risk and Resilience | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | Haydn | No action |  | ? | y | Updated comment | 1 | 1
411 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: • Criticality – only a basic incomplete overview of criticality is given in Section 6 of volume 2. Criticality is not only about how significant an asset is to deliver the service but also how critical the asset is for other interdependences and community functions (e.g.: a water main in front of a fire station may be consider critical because if it fails it could affect the fire service access and operation). Criticality can also interface with how we design and operate an asset (refer Table 9). | Criticality | Other critical infrastructure is already being considered in a later edition. No action required. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | 4 Vulnerability, Criticality, Risk and Resilience 4.3 Criticality Schema | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A |  |  | 1 | 1
412 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • There is no information or tools for asset owners to work out an appropriate level of effort to implement this standard, particularly in terms of collecting information on existing assets. It would be good to have some tools to be able to assess the benefit / cost of collecting existing data. We understand that a business case was presented to Treasury for this work. It would be good if this was set out in the preamble to this document such that the intent and benefits were known. | Implementation | Covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Detailed in business case only | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
413 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • It is unclear to what extent this document will be mandatory or whether only parts will be mandatory. Does this document just apply to new assets or does it apply to all assets? It is considered that it would be good to set out what are the core, optional and desirable attributes that should be held by an asset owner in order to effectively manage and analyse asset performance. It is however noted that there are some assets that the value is collecting information is not outweighed by the benefit (due to the size, location and criticality) – such assets are just replaced on failure. | Mandatory Fields | Standards covers mandatory and optional field. The benefits to costs covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Standards covers mandatory and optional field. The benefits to costs covered in business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
414 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • There is no reference to implementation of this standard to councils of varying sizes. This should be recognised and accounted for in some way. | Mandatory Fields | Covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Covered in business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
415 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: • Updating and communicating changes to the specification appears like it can occur at any stage and it is up to individual councils to check for changes. The updating of the standard needs to be controlled and on a stated frequency and the updates well communicated to the industry. | Implementation | Covered in business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Covered in business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
416 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation: It is considered that the best approach to see how useable this document would be is to undertaken some implementation / pilot testing. There are many councils that have developed in-house metadata standards which have been tested and developed over time. We would have liked to have seen some of learnings from these councils (such as Watercare (Auckland Council), SCRIT (Christchurch City Council, etc.) incorporated into this work. | Implementation | Covered in business case. Pilot testing currently being undertaken. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Covered in business case. Pilot testing currently being undertaken. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
417 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: As-Built File Structure The document is written with a consultant/contractor focus for supplying the data but does not spell out how the data is to be delivered to Council. Mention is made of CAD layers and attribute tags as being the preferred data format. Presumably the data is to be delivered in either a GIS or CAD spatial format with attribute tags that give the information about each assets metadata. This would then need to be extracted and loaded in the Council bases using a file translation programme. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | Noted | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
418 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: As-Built File Structure There is mention of a validation process to prevent unverified data entering the system but no details of how this would be achieved. Some more detail on this would be useful. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
419 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Spatial Accuracy Requirements The importance of incorporating newly captured high accuracy GPS quality asset data with existing lesser accurate asset data while still maintaining relativity between the assets was highlighted as an issue. There needs to be best practice rules created to deal with such issues as we move to an accurate x,y spatial representation of asset rather than traditionally being measured off existing property boundaries that may be incorrectly show. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
420 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Spatial Accuracy Requirements No mention of acceptable levels of spatial data capture in relation to spatial accuracies for capturing assets have been outlined (e.g.: high quality survey as-built accuracies generally being + / - 20mm). It would be useful to have outlined the levels of acceptable accuracies tolerances for the various asset types (e.g.: say pipe inverts or valve lids that would require a different level of vertical accuracy). | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | George |  | Noted | Accuracies Incorporated in updated version. | Included | Included | Accuracies Incorporated in updated version. | 2.1.1 Accuracy Requirements for Locating Assets | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed - add precision tables | do we add for buildings? Speak with haydn | done | done | done | do we add for buildings? Speak with haydn | [5 empty] | No action |  | N/A | y | I have not updated in Vol 2, it should be the same 'paragraph' content as Vol 1, ead your comment as though you had
421 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Spatial Accuracy Requirements No information was provided outlining rules for where to GPS a captured asset (e.g.: an access chamber or hydrant valve – should you GPS the center of the lids or edges of the structure frame). A clearer guideline of the exact capture requirement would also be useful. | NA | Action on volume 1 and data specialist | Vol 1 - Vol 2 |  | George |  | Under Review | Clarify description of requirement. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General |  |  | 1 | [6 empty] | 1 |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
422 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Projection & Datums New Zealand Transverse Mercator has been defined as the preferred co-ordinate system for the supply of digital data in relation to northing and eastings co-ordinate values. This is the same as we use with Council. | Spatial | Action on volume 1. In Volume 2, the use can select coordinate system. Specifying a singular system is not required | Vol 1 - Vol 2 |  | George |  | Noted | Please refer to updated documents sections 2.1.3 & 2.1.4. 26/3/2017 | Noted: no action required | Noted: no action required | Included in the draft Standards | General |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | No action
424 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Projection & Datums The levels are very similar in value so there is the potential there for some confusion with dealing with two datums in the future if the supplied information is not clear as to its source datum. Most surveyors in Christchurch have used the Lyttleton 1937 local Datum historically for a long time and continue to do so. | Spatial | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | Noted: no action required | Noted: no action required | The requirement will be for a uniform method of data supply to a national datum - without this benchmarking will not be possible. Further without this standardisation errors will occur when data is being distributed/shared. 25/3/2017 | 2.1.2 Projections and Datums |  |  |  | 1 | [5 empty] | 1 |  |  |  | ok | [12 empty] | No action
425 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Projection & Datums The New Zealand Vertical Datum 2009 was also in June this year superseded by The New Zealand Vertical Datum 2016, this may need to be reflected in this document also. | Spatial | Action on volume 1. In Volume 2, the use can select coordinate system. Specifying a singular system is not required | Vol 1 - Vol 2 |  | George |  | Noted | Included in updated documents. 26/3/2017 | Included | Included | Included in the draft Standards | 2.1.2 Projections and Datums | 1 | [8 empty] | 1 |  |  |  | ok |  | change needed |  | done | done | done | done | [5 empty] | Changes made documents updated |  | N/A
426 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. | Coverage | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. Action: make clear in the standard. | Vol 1 - Vol 2 |  | George |  | Noted | 26/3/2017 | Included | Noted: no action required | Included in the draft Standards Asset categories included as guidance for each organisation | General | 1 | [7 empty] | 1 |  |  |  |  | change your comment to "Asset categories included as guidance for each organisation" | Added | [11 empty] | No action |  | N/A
427 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Theme / Structure A comprehensive list of asset types for potable water have been defined in the document. The following asset categories that are in the document are not currently recorded in our system for potable water are as follows: Embankments, Channels, Tunnels, Equipment, Cabling, Cathodic Protection, Instruments, Area Of Work. The following asset categories that are in the document that we are currently recording for Potable water are as follows: Pipe, Fittings, Pump Stations, Valves, Containment Structures, Access Chambers, Wells, Nodes. These asset types are currently capture but our Tech 1 asset management system but would need to be customized to accommodate many of the new fields defined in this document for each asset or additional database repositories would need to be created to accommodate where Tech 1 cannot. | Coverage | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. Action: make clear in the standard. | Vol 1 - Vol 2 |  | To discuss - AMIS constraints are not within the considerations of these standards |  |  |  | Noted: no action required | Noted: no action required | To discuss - AMIS constraints are not within the considerations of these standards | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
428 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe Many of the physical attributes will need to be derived from a controlled pick list option that still need developing in the document as there were not mentioned in the latest copy. These lists help control and constrain the data from accepting error entries into the register. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
429 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The metadata attributes will be able to be delivered primarily from the contractor with construction dates, assets status, accuracy precision. Fields like ‘owner’ may need more thought or additional entries where we have multiple departments with an interest in an asset e.g. one department owns an asset but it is maintained by another (this needs to be known for funding/maintenance costs). | Maintenance, Repairs and Maintenance | Action: Include attribute for "Maintenance Responsibility" | Vol 1 - Vol 2 |  | Included in the draft standards |  |  |  | Included | Included | Included in the draft standards | General | 1 | [7 empty] | 1 | [6 empty] | late pickup can be dealt by the asset owner after asset data is provided | [10 empty] | No action |  | ?
430 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Content: Attribute Specifics The metadata attributes for each asset types are extensive for each asset type. Each asset has three types of attribute data, they are as follows: • Physical – e.g. Pipe Material • Metadata – e.g. Asset ID for pipe • Asset Management – e.g. Criticality of pipe The asset management attributes will largely need to be back populated after the asset is with Council system due to the complexity of GIS / modelling software used to derive the risk or criticality of an asset. We don’t consider it appropriate to store Asset Management attributes within an Asset Register table as these change in response to new information and changes within the network. This information should instead be stored and maintained within separate databases maintained by Council and linked to the Asset Register through the Asset ID. Consideration could be given for populating the Asset Register with the results of any new analysis but this could be problematic ensuring the two data sources match up. | Implementation | Agreed. Action on volume 1. | Vol 1 - Vol 2 |  | To discuss - optioneering system structure is not within the structure of these standards |  |  |  | Noted: no action required | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
431 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Unique ID: In this document the pipe asset has a unique ID generated from To and From Nodes at each end of the asset. We have moved away from using nodes to generate the asset IDs. Tech 1 generates an ID for each new asset. Consideration could be given to this method rather than node Id’s at each end of an asset. We believe the current WDC method of assigning an unique ID to a pipe is the most robust way to identify pipes when undertaking analysis. | NA | Action ono volume 1 and data scientist. In the case of establishing condition of pipe, it would matter how big an asset is etc. So you know what length of pipe the condition relates to . | Vol 1 - Vol 2 |  | To discuss - optioneering system structure is not within the structure of these standards |  |  |  | Noted: no action required | Noted: no action required | To discuss - optioneering system structure is not within the structure of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
432 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Owner: The Owner field was defined as one attribute in the document. We have assets where a managing department and a maintaining department can differ within a Council. Additional fields are needed to accommodate multiple ownership. Better clarification on the purpose of the ‘Owner’ field would be useful, i.e. is it ownership at Council level, department level? | Maintenance, Repairs and Maintenance | Action: Include attribute in maintenance | Vol 1 - Vol 2 |  | George |  | Noted | The ownership is at Council level. 26/3/2017 | Included | Noted: no action required | Owner vs manager fields available in the draft standard Catenate multiple oners in one field | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | your suggested response does not answer the question is it to define council departments or that its council's vs someone elses. Please use the response in column T |  | late pickup can be dealt by the asset owner after asset data is provided | [10 empty] | No action |  | ?
433 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Pipe Diameters: We don’t currently record all four of the pipe diameters for a pipe as detailed in the standard, rather we record the nominal diameter only. If we were to record the diameter, nominal bore, external diameter and nominal diameter maybe this could be derived from manufacturers information to auto populate the fields. We don’t consider it necessary or appropriate to specify four different pipe diameters for each pipe asset. If the nominal diameter is known then OD, ID and thickness can be determined based on manufacturer pipe tables (provided of course the pipe materials and pipe class are specified). In summary, nominal diameter, pipe material and pipe class are the only fields required to identify a pipe, other physical dimensions and characteristics can be derived from those three fields. | NA | Organisations will record the level of granularity as required | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Pipes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
434 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Asset Metadata: Pipes • Ground water: If we were to record this at an asset related data some more useful data stating actual ground water depths may be more useful rather than a Y/N field as defined in this document or we could use spatial modelling to populate this field. We don’t believe this field is appropriate within an asset register table. Groundwater by its very nature is dynamic and often poorly understood or mapped. We believe this information is better sitting in a spatial geodatabase that can be updated over time. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Sector Discussion | Sector Discussion | Likely this field lives in another data set (geospatial later called 'Groundwater) | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
435 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Fittings The level of detail for recording fittings in this document far exceeds our current recording methods. Below is a list of types that were outlined in the initial first draft document. Fitting Type: The fitting types for reducers, bends, expansion joints, gault joints are not currently recorded in either our GIS or Tech 1 system. We would need to outline in our standards a lot more requirements to capture this data. We should consider if there is any benefit in capturing some of these asset types also like bends or reducers. It is questionable whether the benefits of managing assets down to this level of detail would outweigh the costs. Definitely should not part of a ‘minimum’ data standard. | NA | Organisations will record the level of granularity as required | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General for Fittings |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
436 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Link ID • This attribute could be onerous to maintain unless it can set up with automation. If pipes get split and new ID’s are generated, then this link ID will need updating. Ongoing maintenance of this field would need some consideration to keep accuracy if the links could not be automated. | NA | Organisations will record the level of granularity as required | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Organisations will determine and record the level of granularity (detail) as required | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
437 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Node • Introducing nodes back into our system to generate asset ID’s for pipes has not been recorded with Council for almost two years. There is however benefit in using nodes to identify a tee or a pipe change. | NA | Nodes are required for analytical differentiation purposes | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Nodes are required for analytical differentiation purposes | General for Nodes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
438 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Node • A little more detail on when a node should be used to differentiate where there has been a pipe change by date or size or material would be useful and the rules around this should be documented. This would assist in removing any ambiguity when is appropriate to use this feature. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Clarify description of requirement. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Nodes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
439 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Format Reference is made in section 1.8 automatic acceptance testing of data supplied; however there is no detail on how this is to be implemented. Caution suggested as acceptance of this could impact on Council being forced into purchasing some software that does not meet our Information Technology Strategy process and programme. Do we have any indication of when the acceptance testing would be undertaken? Currently as-built are received by the appropriate project manager and checks are undertaken by them then files are forwarded onto AIM team for loading into systems. There have been situations where hardcopy (PDFs) have differed from the Electronic CAD data provided. Which is correct? It would be good to see something that requires confirmation that they are the same version. Development of standard code lists for fields that require is an excellent idea. Code lists should be able to be utilised by the whole of the Asset Management System not specific components. For example, construction material which can be used by any asset group within the register that requires this information, such as Green Space assets. There may be a need to recognise area variation for some code lists, but this should be an exception. And any additions should be documented within corporate systems detailing the reasoning behind such. | Implementation | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. The intent of the standard is that data flows from the BIM model created during construction through to the standard, due to the standardisation of attributes. | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
440 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o A number of numeric fields appear to have defaults of -9999, unsure of why this would be unless it is to enable extraction of data with this number that could be consider very wrong. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | George |  | Noted | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | Noted: no action required | Noted: no action required | A numeric value was selected that would indicate an impractical value so as not to be incorporated wirth any analysis. When incorproating this data each organisation can adopt their own value foranalysis. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
441 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Costs are noted as a generic field to be included in the data provided, from a WDC point of view, this is not cost of the asset from a capitalisation point of view, as additional values are added to enable processing by Council to be completed and balanced. Our Engineering Code of Practice asks for this but most subdivision as-builts supplied do not provide this. Contracts prepared by Council document the actual cost from the payment certificates etc. | Financial Performance | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | The cost of the asset should be recorded against the asset regardless. The cost data may be gathered from the subdvision as-builts or from council contracts. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
442 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard includes a number of asset groups that we do not currently record such as Containment Structures, Embankments, Retaining Structures. | Mandatory Fields | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Councils do not need to collect data on all\ listed assets,/categories. However, if they chose to collect data on a particular asset, it should be as per the standard. | 1.8 Theme Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
443 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The digitisation aspect of the various asset groups also need to be reviewed as current process within WDC for 3 water assets only allow for either Point or Line asset types. Adding a Polygon feature type is able to occur, but will require a clear definition of asset types. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | Noted: no action required | Noted: no action required | Please review the specific requirements identified for each asset type and provide your feedback. Workshops will be held in May for further contribution. | 1.10 Graphical Data Construction Principles |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
444 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard indicates that Wells are to be digitised as Polygons, WDC records as a single point feature identifying the location of the well source. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | Noted: no action required | Noted: no action required | This detail was identified at the previous workshops and determined to be appropriate - however it does not preclude asset owners from creating the asset as required once the data is delivered. Organisations may utilise a point symbol from the centroid of the polygon as required. | 2.3.4 Well - PW |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
445 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard also indicates the digitisation of assets within buildings, unsure how GPS co-ordinates would be expected to be obtained. For assets within a building or headworks, it would be more appropriate for a schematic be provided, which would be linked to the relevant assets within the building. Ensuring that there is some unique ID supplied by the developer or provider of data. This asset ID could then be recorded against the asset within the Asset Management System for cross-referencing purposes. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Data collection is out of scope from these standards |  |  |  | Noted: no action required | Noted: no action required | Data collection is out of scope from these standards | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
446 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Development of criticality, risk assessment, condition ratings are undertaken outside of the AMS, however the final scores should be recorded within the AMS to allow a single source of truth for reporting purposes. | General | Included in standard. | Vol 1 - Vol 2 |  | noted |  |  |  | Included | Included | Reviewed and included in standards, data standards are not prescriptive of where analytics is completed | No Specific Reference | 1 | [7 empty] | 1 | [19 empty] | ? |  |  | 1 | 1
447 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard is suggesting the creation of non-physical nodes, this is additional work for what purpose? If there is a need to record a “to” and “from” asset id, then we should be using a physical asset, not something made up. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | This requirement will generally only apply to Potable Water. | Noted: no action required | Noted: no action required | This requirement will generally only apply to Potable Water. | 2.4.4 Node |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
448 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Junctions/end points etc are appropriate to record as assets, clarification on whether to record costs against these need to be considered from the a valuation point. | Financial Performance | Action: Granularity to be decided by organisation. To be clarified further in Volume 1 or Volume 2. | Vol 1 - Vol 2 |  | Junctions / end points are not assets. |  |  |  | Excluded | Excluded | Junctions / end points are not assets. | General |  | 1 | [6 empty] | 1 | [8 empty] | no action | no action | no action | n/a | [5 empty] | No action
449 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o The standard should consider what assets should be included in the valuation process and indicate to what level of component breakdown is appropriate. Currently WDC do not value nodes, such as junctions/endpoints, they are considered part of the main. | Financial Performance | Action: Granularity to be decided by organisation. To be clarified further in Volume 1 or Volume 2. | Vol 1 - Vol 2 |  | Junctions / end points are not assets. |  |  |  |  | Excluded | Junctions / end points are not assets. | No Specific Reference |  | 1 | [6 empty] | 1 | [8 empty] | no action | no action | no action | n/a | [5 empty] | No action |  |  |  |  | 1 | 1
450 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Pipes have indicated a need for recording 3 diameters, discussions have been undertaken and the organisation view is a single diameter is only required as the other values are able to be defined from generally available sources, recording the additional values will not add value to the data. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | George |  | Under Review | Please provide details of which value is preferred. To be reviewed by the TWG for consideration. 26/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision |  | N/A
451 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Pipes suggest an asset ID comprising of the from and to node connections, current AMS now issues a single asset ID for each main, the use of the from and to details to generate an asset ID becomes a challenge in the future when new mains cut into existing pipes necessitating a need to change the asset ID as the from or to node is now incorrect. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | The lowest granularity for a pipe asset is piece of asset pipe and recorded as such with a specific pipe asset AssetID. Canenated pipe pieces make up a Mains Pipe. And, allow for 'pieces of pipe to be replaced, again at an AssetID. |  |  |  | Noted: no action required | Noted: no action required | The Idv proposed is for the data provider to create an identifier. Once the data is provided it is then upto the asset owner to incorporate into their systems in the most appropriate way. | General for Pipes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
452 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Further detail on assets within Headworks sites may be required as not all attributes could be relevant dependant on the asset type. Seeing the full code lists may assist in this. | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft standards Cod lists have been supplied | General | 1 | [7 empty] | 1 | [6 empty] | add codelsits |  | done | done | done | done | [5 empty] | Change made document updated |  | N/A
453 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o A full restructure of our current database will be required when/if the standard is implemented and WDC agree to move to the structure. This may also assist where a section could have duplicates, noted that nodes indicated meters, as well as instruments. What is the difference? Clarification needs to be provided when to use. | Implementation | Action on volume 1 and business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action on volume 1 and business case. | General |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | Nodes do not indicate meters |  |  |  | n/a | [5 empty] | No action
454 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o A large number of fields will require investigation to enable completion of data as many fields identified have never been recorded. | Implementation | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
455 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | o Attachment 1 sets out request for digital water asset data, needs to include an option for direct download of data from Cloud/FTP site by consultants. We have this functionality and are moving people to that rather than us having to extract and manipulate for them. | Implementation | Statement noted. Action on volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Data transfer is not in scope. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
456 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | What detail is really needed for National reporting purposes vs organisational? We do not understand the purpose behind a number of the fields identified. | Granularity | No action required. Metadata standard is more than meeting minimum national reporting purposes. Granularity question. | Vol 1 - Vol 2 |  | The reporting granularity so for an asset manager managing any single or number of assets |  |  |  | Noted: no action required | Noted: no action required | The reporting granularity is for an asset manager managing any single or number of assets, at the circumsatances for any asset manager | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
457 | Kalley Simpson | Waimakariri District Council | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Summary 1. We need to define the spatial accuracy and data capture methods little more in the document so it is clear how data should be captured and to what level of accuracy is needed. 2. The asset attribute data while it Is very comprehensive needs some code list definitions to help with accurate data entry. Some fields need more detail where they really are not giving us more than a yes /no entry allowing for interrogation of the data. 3. There are also some fields that will create ongoing work having linkages to other assets. These need to be carefully considered so as to have robust updating processes to maintain data accuracy when data changes. 4. There are many asset attributes that are required in this standard that don’t fit in the current Tech1 system so it will need to be customized considerably or additional database repositories will need to be created to accommodate these additional fields. 5. The metadata standards should be setting minimum guidelines or requirements as well as more advanced optional standards. It is unreasonable to expect all Asset Owners to meet the same standard. | General | 1. Completed 2. Further information required from respondent. 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | 1. Completed 2. Further information required from respondent. 3. Business case - implementation. 4. Data scientist. 5. Business case - implementation. Further clarification in mandatory - optional and industry attributes. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
458 | Kerry Thompson | KTA | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Outline Comments: • The AEC data space is quite fragmented and very distributed. • BIM is primarily about data. 3D geometry, 2D geometry is about the representation of the data and is secondary. • Metadata should be based on a pattern language that is consistent, discreetly named, predictable in structure. • It is difficult to impose a structure across an industry where the focus of the various metadata models are specific to the reason they are produced. The key is to provide a metadata requirements definition but not compromise the operation of data production. i.e. what is wanted rather than prescribing how to do it. • The major cost of a facility management system relates to its operation over time rather than its establishment. • Synchronising reality and a facility management database is problematic – they are out of date as soon as they are issued. • In terms of FM, the best database is reality and advances in data capture and remote sensing is further promoting this. Data is acquired as required • It is also difficult to have a single database model to cover all situations – In my opinion, a data aggregator that can provide a logical single database made up am many physical database tables would be the better approach. New tools, such as Microsoft’s Power BI, promotes this trend. We are also seeing Cloud based implementation of this concept in products such as Autodesk’s BIM 360 Glue and Revit C4R collaboration technologies. | General | Statement noted. Consideration for Volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Consideration for Volume 1. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
459 | Kerry Thompson | KTA | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | BIM In my experience there are three types of BIM Models that are currently being produced. • The Design Intent Model (the pretty pictures) • The Construction Model (Simulation of the project delivery) • The Operating Model (Operating of the Asset) They all have different levels information density and while they can flow one in sequence, they tend to be aggregated rather than be contained in the one model. Models are also split between discipline and are often broken up to manage the large volume of data that is contained within a building project BIM model. BIM data, to be of value, has to be well crafted and consistently defined to a data pattern language. BIMable data can be counted, and, in my experience, some 3D models do not necessarily provide this. | NA | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. No action required. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
460 | Kerry Thompson | KTA | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | The Proposed Standard As far as the proposed standard was concerned, it seemed to me that there was a single core data frame work table that was expanded across a range of perceived Building situations and objects. I guess the question is how far do we go. A BIM authoring program, such as Revit, has around 400 element types across the various disciplines that are predefined and implicit to its operation. We can add additional metadata on a project basis. In my opinion, the standard should focus on the core data framework, identify the core elements that are relevant and provide a performance requirement in terms of metadata performance. BIM data authoring metadata systems may be augmented and remapped to support the standard on a project or organisational basis. The document is quite long and I recommend that it is condensed to the standard core data table and a list of ,say, the 20 building objects and situations important enough to justify the use of the metadata for asset management. Issuing a data standard with hundreds of variables is also not very usable and would have little change of take up, or provide an additional cost implication if imposed. | NA | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. No action required. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
461 | Myles Lind | Queenstown Lakes District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Background of Submitter 1. The QLDC is a medium sized local government council which services the community and businesses of the Queenstown Lakes District. 2. The Queenstown Lakes District is New Zealand’s adventure capital and our economy is highly reliant on our natural environment supporting tourism and a high quality of family life. 3. The efficient and effective provision of our infrastructure is fundamental to the strength of our economy, the remaining high quality of our natural environment and the future resilience of our community. 4. The Property and Infrastructure Department of QLDC has a vision to be leaders in asset management. To that end we have commenced a transition to standards based asset management. 5. A key supporting element of standards based asset management is the ability to benchmark and continuously improve our practices and our overall asset management outcomes. 6. QLDC has chosen to use ISO55000:2014 Asset Management Standard as the framework of its asset management approach. 7. One of the elements of our approach is utilising the IPWEA NZ National Asset Management Systems (NAMS) programme which has been a highly recognised and widely utilised service throughout Australia and New Zealand. 8. The Property and Infrastructure Department of QLDC actively seeks out new and emerging practices and approaches that advance and improve our asset management outcomes. | NA | Statement noted. No action required. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. No action required. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
462 | Myles Lind | Queenstown Lakes District Council | 3-Waters & Buildings | Vol 1 & Vol 2 | General | [5 empty] | Submission 9. The QLDC appreciates the opportunity to make a submission on the draft Metadata Standards (the standards). 10. QLDC supports the intent of the standards to better leverage the benefits of data (and analytics) in the progressive advancement of asset management and broader investment decision making. 11. It is evident that the full benefits of the standards will not be realised unless organisations have the capacity, skills and competence to carry out the analytics that the programme will provide. 12. Embedding the real benefits of data will require a change in culture in organisations. 13. In particular it signals the rise of the Data Scientist/Analyst function within local councils. 14. To ensure consistent and timely implementation of the standards, this will also require an increased focus on raising of the capacity and competency of staff and supporting Information Technology resources. 15. It will also involve enabling a change in delivery of the services – including operational, professional engineering and management behaviours, and potentially community engagement / understanding. 16. Support and collaboration between organisations will also be crucial to the success of the project, and ensuring ‘data fatigue’ doesn’t occur. 17. A key aspect of this must be the free and open sharing of resources, learnings and other IP, between organisations. The opportunity for a middle-person/organisation to clip the ticket in sharing learnings must be minimised. 18. As a final comment, a system of guidance and incentives may be required to support organisations embed the standards and ensure that embedding of the standards, nationally is consistent and within a similar timeframe. CONCLUSION 19. QLDC supports the intent of the standards to better leverage the benefits of data in the advancement of asset management and investment decision making. | NA | Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business case. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
463 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Water New Zealand confirms its support for the creation of a National Standard in relation to asset data, and generally feels that the development of Volume 1 to date is a key step to achieve this. The Standard promotes standardisation of core data across New Zealand allowing consistency between councils. The LINZ publishing site confirms previous reassurance that LINZ and MBIE have worked closely across local government organisations in the production of these standards however there is apprehension amongst some members that the draft standards do not accurately reflect the industry’s contributions and views. We acknowledge the request for review comments to be limited to the content of each volume and to refrain from comments on implementation. However given the importance and status of this project believe this limitation to be unrealistic. | NA | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
464 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard The production of three separate volumes on as-built data (water, wastewater and stormwater) and another three for asset management performance is considered to be adding unnecessary volumes and complexity. There is also an overlap of data that is repeated within the volumes. This creates ambiguity and loses transparency of the data structures. The working group considered that a single document focussed on as-built data be produced. Fundamentally the structures under 3-waters are identical but for the physical properties of the media being transported through each system and some minor structural differences. The working group proposed hierarchy, selection lists and the allowance for some open fields negates the need for separate volumes. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Volume Interaction | Statement noted. To be considered. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. |  |  |  | Noted: no action required | Noted: no action required | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
465 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard The two volumes seek to differentiate between derived data and field captured data, however there is confusion between the locations of the data sets between the volumes. A number of derived data sets are found in the as-built set and similarly design data and financial data, captured at delivery, is incorrectly listed in the derived data set. The scope of the volumes produced has been extended beyond the scope of the working groups. This project was originally presented as an as-built data set for industry that can be used to collect field data. Volume 2 for derived data has had limited industry input and is not considered ready to be published. Further work on this volume is therefore required. | Volume Interaction | The introduction of cohorts and schemas should help clarify this situation. Action Required for volume 1 to identify the three schema's. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. Action to look at this. | Vol 1 - Vol 2 |  | These inconsistencies have been actioned in the draft standards |  |  |  | Included | Included | These inconsistencies have been actioned in the draft standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | ?
466 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard The structure of the standard should also be “normalised” to take into account common data attributes across all asset classes and preferably a tool provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was a key input provided during the workshops into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Normalisation | Data tables being looked at by data scientist. | Vol 1 - Vol 2 |  | These inconsistencies have been actioned in the draft standards |  |  |  | Included | Included | These inconsistencies have been actioned in the draft standards | General | 1 | [7 empty] | 1 | [6 empty] | Note: while the structure is normalised in the standard it is opfetn de-normalised to accommodate organisations needs. |  | no action required | no action required | no action required | no action required | work required | work required | work required | work required |  | No action |  | N/A
467 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Structure and Scope of the Standard Also there is much confusion regarding the proposed Volume 3 – Intervention Methodologies, 4 – Decision Making analytics and 5 – Asset management Frameworks. Are these volumes part of this project, confirmation that they will be produced and if so who is making that commitment? Also there is no “Volume 6 – Implementation Plan” that would allow Volumes 1 & 2 to be useful. Further definition and clarity around this is also required. | NA | Not in scope | Vol 1 - Vol 2 |  | To discuss |  |  |  | Sector Discussion | Sector Discussion | To discuss | No Specific Reference |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision |  | N/A |  |  | 1 | 1
468 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However:  Greater Clarity and Definition is required to determine the scope of each asset class defined within the Standard – the focus group workshops uncovered examples where practitioners were uncertain as to where particular assets should be located. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Action for volume 1. | 1.7 Heirarchy |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
469 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: The current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”, both of which exist in practice. | Coverage | Out of scope. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Sector Discussion | Included | Tables to be discussed in Final Version Vol 1 | No Specific Reference | 1 | [7 empty] | 1 | [6 empty] | change needed | change category and response to sector discussion | n/a | further information required from workshops not to include treatment plants tunnels added | n/a | n/a |  |  |  |  | document request | More information required for a decision Tunnels have been included |  | N/A | y | no change
470 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. However: Same Hierarchy: A key part of the input provided at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard, but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | George |  | Noted | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | Noted: no action required | Noted: no action required | The hierachies (classifications) have been applied to each network type. Therefore if it has not been deemed to be appropriate or relevant to the network it has been excluded. If there are examples of those specific assets that should be included but have been omitted please provide details. Additional asset clases can be incorporated as required. | 1.7 Heirarchy |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
471 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions The data hierarchy is essential in producing a cohesive data structure to organise data for the purpose of common elemental mapping across organisational systems. The hierarchy also bind the data together which has unfortunately been separated by the three volumes based on a network type. The hierarchy that has been setup is not correctly represented and has not been carried through to the data attribute tables. | NA | Data hierarchy to be look at by data scientists. Think this comment applies mostly to Volume 1, but data hierarchy needs to be considered for Vol 2 also | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards |  |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | 1 | [7 empty] | 1 | [6 empty] | review against notes | haydn please note these has been no work to harmonise Vol 2's with Vol 1's | no action required | no action required | no action required | no action required |  |  |  |  | follow up with Nick Walmsley for further information To note that organisations may have different hierarchies - the purpose of this document is to standardise the requirements for the data service providers and provide consistency in data delivery to the asset owners | No action |  | ? | y | Yes there has….. They are harmonised by the primary key fields of each of the decision elements and the tables 'nested' within them No need to standardise across Vol 1 & 2
472 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Hierarchy and Definitions The development of this standard sought to normalise the data across New Zealand. In order to achieve normalisation the data needs to be understood in common definitions. Common definitions across the organisations need further development. | Terminology | Action: check definitions are consistent across both volumes 1 and 2. | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards |  |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | 1.7 Heirarchy | No action | [7 empty] | 1 | [7 empty] | haydn please note these has been no work to harmonise Vol 2's with Vol 1's | no action required | no action required | no action required | no action required | [5 empty] | No action |  | ? | y | Yes there has….. They are harmonised by the primary key fields of each of the decision elements and the tables 'nested' within them No need to standardise across Vol 1 & 2
473 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed above. | Data | Action required: data scientists to review Volume 1. Heierarchy question | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Tables will be referenced in Final Versions | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action |  | N/A
474 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Graphical representation and its accuracy Each of the current three documents makes broad statements about the recording of data within a GIS application. GIS is a critical methodology for how a utility chooses to represent asset data. The role of the Standards is to define as-constructed spatially aware data; spatial data should form a part of the data specifications in Volume 1. It is not agreed that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). We understand that this subject was not in the scope of this development. Currently each organisation retains its own rules and depending on the asset location the representation rules may differ i.e. a cable within a pump station versus a buried cable for cathodic protection along a pipe. It is questionable whether graphical representation should be within the document since the purpose of the standard is collecting metadata of asset physical properties. Geospatial requirements would form a standard in its own right. | Spatial | Action on volume 1 | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | Accuracy is precision - precision is defined in the standards The standards define the attributes and graphical representations required (line, point, polygon only) no symbology as that is left to each organisation. | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action |  | N/A
475 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. | Implementation | Statement Noted. Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement Noted. Business case. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
476 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also acknowledge that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. | Implementation | Statement noted. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
477 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues However there is a preference to see flexibility within the Standards for each council to: 1. Specify their commitment to the end-state; 2. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; 3. Maintain a “translation ability” within each organization to map data and information from current systems and processes to the new Standard; 4. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. | Implementation | Business case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business case. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
478 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues We support the direction espoused for Volume 2 – but do not believe that the standards as produced to date are fit for purpose, and neither have they yet had an adequate level of input through workshops. Also Sections 1.5-1.8 of Volume 2 discuss analytical methods, which is not relevant to this volume and therefore should be deleted. | Implementation | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Statement noted. Numerous industry attended workshops conducted in support of Volume 2. Volume 2 as it stands reflects outcomes of the workshops. Some overlap may be present between data included in the 2 volumes. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
479 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues The document demonstrates competence in listing a large number of attributes and the purposes of data collection however it does not demonstrate what implementation should look like. All of the fields in the attribute lists are mandated. The practicality of this mandate should be considered where organisations may choose not to collect certain information for low risk assets. | Mandatory Fields | Action required: Give further thought to what fields are mandatory with consideration to data maturity and sophistication. Implementation issues are covered under the Business Case | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Implenmentation is not within scope | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
480 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues An implementation strategy should reflect a data collection matrix that takes the organisation’s risk profile into consideration. The interaction of data and how an organisation will demonstrate compliance or move through the implementation phases to reach the standard’s objectives should be reflected. | Implementation | Business Case | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
481 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Implementation Issues How will the material in the standard be used when the material is copyright? In order for implementation to happen the standard would need to be embedded within an organisation, ultimately in the long term using field names and processes as closely as possible to that prescribed by the standard. This will require software system suppliers to adopt the material in the development of asset information and management systems without the restriction of copyrights across the content of the standard. | Implementation | Business Case. | Vol 1 - Vol 2 |  | noted |  |  |  | Noted: no action required | Noted: no action required | Business Case. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
482 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. 1. Has it been demonstrated that the schemata will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? 2. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Is that correct? 3. Any Asset Management practice has improvement as a key result area. How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards; the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial? A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess whether all the data and information requirements of asset owners, service providers and customers are satisfied. | Implementation | These comments are identical to Oliver Mander See comments Haydn | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. |  |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
483 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | IT Systems and Migration It is recognised that this is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document; if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this will likely involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We would expect some history and attributes to be lost or stranded in other systems. At a recent workshop on our National Performance Review we created a partial list of software that is currently in use within local government utilities. We attach a summary table of this to indicate how many systems are involved that would need to “talk to each other” with the proposed metadata standards. | Implementation | These comments are identical to Oliver Mander See comments Haydn | Vol 1 - Vol 2 |  | This is not within the scope of these standards |  |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
484 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | General content “Data types” or pick lists differ from those nominated during the workshops. These have since been removed from the original documents published, directing the reader to a separate volume that has yet to be released. This will need to be reviewed and reinstated to allow constructive feedback. | NA | Action for volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards |  |  |  | Included | Included | Included in the draft Standards | General | 1 | [7 empty] | 1 | [7 empty] | add codelists need specific instances where this has occurred to check against master | codelists added | codelists added | codelists added | codelists added | [5 empty] | No action |  | N/A
485 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Data field lengths, minimum or maximum cannot be set due to the various systems in use. These are mapping exercises that are organisational specific. It is unclear what this standard wants to achieve by setting these limits and whether the implementation will be practical. | Data | Action required: data scientists to review | Vol 1 - Vol 2 |  | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards |  |  |  | Included | Included | To discuss - known systems constraints and analytical implications have been considered as part of the development of these standards | General | 1 | [7 empty] | 1 | [17 empty] | No action
486 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | The current drafts need additional work at the hierarchy level and better definition / guidance. | NA | Hierarchy is Volume 1. Definition may apply to Volume 2. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Sector Discussion | Included | Asset Classifications have been defined in the Standards | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest change status to Sector discussion and change response to More information is required to inform a way forward | Changed | [11 empty] | More information required for a decision
487 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Roles and responsibility assignment to contractors and consultants are not prudent in a standard. These are best left for the organisations to define under terms of contracts. Australian examples and photos should be replaced by New Zealand examples and slang words such as “savvy” removed. | Implementation | Action: to be clarified in "In Summary" chapter. | Vol 1 - Vol 2 |  | Haydn & George |  |  |  | Included | Included | This is about conext for using the standards - setting up expectation across the sector to allow innovation and productivity gains and hence ceratinty. | No Specific Reference | 1 | [7 empty] | 1 |  |  |  |  | ok |  |  | general roles and responsibilities are part of creating a standardised way of developing best practice | [9 empty] | Further discussion with Sector |  | N/A |  |  | 1 | 1
488 | Nick Walmsley | Water NZ | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | We have added comment into the Water Supply Volume 1 to illustrate some of the issues mentioned above. Similar comments would apply to the other Volume 1s. | NA | Volume 1 only. | Vol 1 - Vol 2 |  | George |  | Noted | 26/3/2017 | Noted: no action required | Noted: no action required | Included in the draft Standards | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
489 | Nick Walmsley | Water NZ | Potable water | Vol 1 | Executive Summary | iv | 3 |  |  |  | savvy - edit out slang words like this |  |  | Vol 1 |  |  |  | Noted | removed in current version 28/2/2017 | Included | Included | removed in current version 28/2/2017 | Executive Summary | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | n/a | n/a | n/a | [5 empty] | Change made document updated
490 | Nick Walmsley | Water NZ | Potable water | Vol 1 | Executive Summary | v | In Summary - 2 |  |  |  | While all care has been taken with the preparation of this document, it is the responsibility of the consultants to confirm that all details are current and relevant - what does this mean? |  |  | Vol 1 |  |  |  | INCLUDED - DOC | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. 28/2/2017 | Included | Included | consultants are responsible to ensure they are using the latest document. Wording to be changed to make this more obvious. 28/2/2017 | In Summary | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | done | [5 empty] | Change made document updated
491 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.1 | 1 | 2 |  |  |  | Consultants - Replace by organisations? |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | Term consultants now included in glossary. 28/2/2017 | Included | Included | Term consultants now included in glossary. 28/2/2017 | 1.1 Register | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
492 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.4 | 1 | 1 |  |  |  | Again, misuse of term 'consultants. edit through the document to correct this. |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | Term consultants now included in glossary. 28/2/2017 | Included | Included | Term consultants now included in glossary. 28/2/2017 | 1.4 Disclaimer | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
493 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.5 | 3 | Facsimile |  |  |  | Is this still used? |  |  | Vol 1 |  |  |  | Noted | optional supply 28/2/2017 | Noted: no action required | Noted: no action required | optional supply 28/2/2017 | 1.5 Deliverables |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
494 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 1 | 1 |  |  |  | shouldn't this be schemata i.e. plural? In which case shouldn't we have schema and schemata and not use 'schemas'? |  |  | Vol 1 |  |  |  | Noted | both schemata and schemas are both acceptible words for the plural of schema. 28/2/2017 | Noted: no action required | Noted: no action required | both schemata and schemas are both acceptible words for the plural of schema. 28/2/2017 | 1.6 Global Schemas |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
495 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 4 | Volume 3 - 1 |  |  |  | Is it part of this metadata project or to be done by others? Very confusing. Also there is no mention of a volume about how to introduce the metadata standards which is the subject of another proposal but will be a major issue. why doesn't it get a mention? |  |  | Vol 1 | This is not within the remit of the standards |  |  | Haydn | need a direct response 28/2/2017 | Noted: no action required | Noted: no action required | This is not within the remit of the standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
496 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 4 | Volume 4 - 1 |  |  |  | how can the analytics standardise the data that has already been standardised? |  |  | Vol 1 | The data definitions have been standardised, the actual data can be standardised against that. |  |  | Haydn | need a direct response 28/2/2017 | Included | Included | The data definitions have been standardised, the actual data can be standardised against that. | General | 1 | [7 empty] | 1 | [17 empty] | No action
497 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.6 | 5 | Volume 5 - 1 |  |  |  | Is this project intending to re-write an asset management manual i.e.. IIMM lookalike? |  |  | Vol 1 | No, this is not an asset Management Standard - it is an asset data standard |  |  | Haydn | need a direct response 28/2/2017 | Noted: no action required | Noted: no action required | No, this is not an asset Management Standard - it is an asset data standard | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
498 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.8 | 1 | 1 |  |  |  | i.e. not fixed and topics can be added? |  |  | Vol 1 |  |  |  | Noted | Agree, asset classes can be added as agreed to 28/2/2017 | Included | Included | Agree, asset classes can be added as agreed to 28/2/2017 | 1.8 Theme Structure | 1 | [7 empty] | 1 | [17 empty] | No action
499 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 1.9 | 4 | Potable water Asset class Table |  |  |  | what does this mean? No? but no Y for yes? |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | N changed to N/A 28/2/2017 | Included | Included | N changed to N/A 28/2/2017 | 1.9 Data Principles | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
500 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.1 | 6 | 2 |  |  |  | perhaps the sector should derive one preferred conceptual practice i.e.. is absolute accuracy more important than relative accuracy? Whose data has primacy? e.g.. LINZ spatial data with asset data associated by relative accuracy? |  |  | Vol 1 |  |  |  | Noted | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time 28/2/2017 | Noted: no action required | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time 28/2/2017 | 2.1.1 Accuracy Requirements for Locating Assets |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
501 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.1 | 6 | 2 |  |  |  | precisely? 'well' is a subjective term |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | changed 7/3/2017 | Included | Included | changed | 2.1.1 Accuracy Requirements for Locating Assets | 1 | [7 empty] | 1 | [6 empty] | change needed |  | done | done | done | done | [5 empty] | Change made document updated
502 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.1 | 6 | 5 |  |  |  | no 's' |  |  | Vol 1 |  |  |  | Under Review | cannot identify 7/3/2017 | Sector Discussion | Sector Discussion | cannot identify | 2.1.1 Accuracy Requirements for Locating Assets |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
503 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.1.8 | 15 | Common Attribute & Validation File Format Instructions Hlth_Sfty |  |  |  | change 'issues' to 'risks' throughout document |  |  | Vol 1 |  |  |  | Noted | not a risk but an issue 7/3/2017 | Noted: no action required | Noted: no action required | not a risk but an issue | 2.1.10 Common Attributes |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
504 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.3.4 | 40 | 1 |  |  |  | Well - change to 'bore' |  |  | Vol 1 |  |  |  | Noted | term agreed to by TWG 7/3/2017 | Noted: no action required | Noted: no action required | term agreed to by TWG | 2.3.4 Well |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
505 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.4.3 | 60 | 4 |  |  |  | does this create a 'node'/ if not then it is a problem for modelling. |  |  | Vol 1 |  |  |  | George/Haydn | Can be post processed to be a node by the agency 7/3/2017 | Included | Included | Can be post processed to be a node by the agency | 2.4.3 Fitting | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
506 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.4.5 | 67 | 13 |  |  |  | how is a locator or IP cable taped to the pipe represented? |  |  | Vol 1 |  |  |  | Under Review | Need more information and example 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and example | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
507 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.4.6 | 74 | Pipe Attribute & Validation File Format Instructions Diameter |  |  |  | I assume that you don't need all of dia, nominal dia, external dia, nominal bore etc as if one is incorrect life will be confusing and an overkill? |  |  | Vol 1 |  |  |  | George/Haydn | this was agreed to by the TWG, what is your suggestion? Needs to be appropriate to pipe type and ability of person capturing the detail to supply the data 7/3/2017 | Included | Included | The level of detail is required for analytical purposes, all organisations will deciode on the level of detail to suit their curcumstances | 2.4.6 Pump Station | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
508 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.5.1 | 93 | Mechanical Equipment Attribute & Validation File Format Instructions |  |  |  | Is a backflow preventer a mechanical equipment asset or a valve/ |  |  | Vol 1 |  |  |  | Under Review | Need more information and recommendation 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and recommendation | 2.5.1 Equipment |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
509 | Nick Walmsley | Water NZ | Potable water | Vol 1 | 2.8.2 | 140 | 1 |  |  |  | reporting mismatches could be a problem depending on the spatial base used see 2.1.1 comments re accuracy. |  |  | Vol 1 |  |  |  | Noted | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time 7/3/2017 | Noted: no action required | Noted: no action required | absolute accuracy is aimed for but a balanced approach needs to be adopted, identifying areas for LINZ to improve over time | 2.8.2 Matching to Existing Infrastructure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
510 | Nick Walmsley | Water NZ | Potable water | Vol 1 | Glossary | 145 | 1 |  |  |  | this could be much larger with additional definitions e.g.. 'trunk main' |  |  | Vol 1 |  |  |  | Noted | wil expand over time 7/3/2017 | Noted: no action required | Noted: no action required | wil expand over time | Glossary |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
511 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | One Document Currently, the standards for each network are contained in separate documents. There is, however a high degree of commonality across the three networks in terms of the underlying asset classes and the attributes that describe them. The current format leads to a high degree of repetition across the documents. This is particularly relevant when considering that the documents will be used by consultants and contractors to provide data back to relevant water authorities; it should be a key objective to make them as useable as possible by all stakeholders. | Volume Interaction | Statement noted. To be considered. | Vol 1 - Vol 2 |  | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | Yes. Key objective to make them as useable as possible by all stakeholders: what is the solution then? |  |  | Included | Included | To discuss - The ease and use of the standards are best suited to being separated for Stormwater experts verses wastewater experts and potable water experts. It is noted there are many 'overlaps', but in many instances in scope, design, construct and operate, the information is best kept 'discrete' for those who require the specifics of the information related to the specific operating environment. The counterfactual is to combine them all. The resulting confusion, and the size of the documents that would result were deemed to be less appropriate than the replication noted here. | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
512 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Common Data and Useability Common data applicable to all asset classes is repeated throughout the standard associated with each asset class. Similar to point (1) above, this impacts useability of the standard – particularly when contractors are providing data on multiple assets and/or networks as part of a single project. - The structure of the standard should be “normalised” to take into account common data attributes across all asset classes - A tool should be provided to reflect this “normalised” view and to make it simple for contractors to enter relevant data. We note that the creation of a normalised data standard was key input provided by Wellington Water and other local authorities into the development of these standards. The risks associated with a “de-normalised” structure include errors and inconsistencies in entering the ‘same’ data in multiple fields. This, in turn, can lead to a lack of confidence in the data. | Normalisation | This will be looked at by the Data scientists? | Vol 1 - Vol 2 |  | The standards have harmonised and standardised data and hierarchies across the standards | Common data: The antithesis applies where designers are designing a 'stormwater' solution. Risk advocated with a 'de-normalised' structure: Agreed: note work being completed by Metaconnect. |  |  | Included | Included | The standards have harmonised and standardised data and hierarchies across the standards | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
513 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | “What does implementation look like?” We note that the text associated with Volume 1 refers to the development of specific roles and processes. While laudable, the Standards should recognise that different councils are in different places with respect to a full implementation of these standards; i.e. an implementation supported by systems, processes and people. Providing a “specific” regulatory implementation path may not allow councils to make the most of their existing investments in systems, processes and people. We recognise a “trade-off” between a consistent structure applied by all users and “current state” systems that prescribe how asset data is collected and stored. We also recognise that if the Standard is not applied by all users, the outcomes and benefits that may be gained from the adoption of the standard are at risk. Wellington Water would prefer to see flexibility within the Standards for each council to: i. Specify their commitment to the end-state; ii. Create a roadmap to achieve that standard; this may include specific data collection programmes, ongoing “organic” improvement in data quality and specific system investment; iii. Maintain a “translation ability” within each organization to map data & information from current systems and processes to the new Standard; iv. Statements relating to the ‘cost vs benefit” and “pace” of data collection to support the Standard’s minimum requirements should be included in the Standard. This approach recognises the trade-off between existing systems & processes, and a future state. Note that Wellington Water itself is likely to be an early adopter of the Standard. | Implementation | See comments Haydn | Vol 1 - Vol 2 |  | This is not within the scope of these standards | Specific roles: not specified. Different places: agreed, more about how… not so much if. "specific" regulatory implementation: noted, probably need to think about what if scenarios, i.e.. What if not adopt? Application by all users: noted and agreed. Flexibility within the standard: agreed with all this. |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
514 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Volume 2 is not yet suitable for any implementation Wellington Water is supportive of the direction espoused for Volume 2 – but does not believe that the standards as produced to date are fit for purpose, nor do we believe that there has been the correct level of input from our staff to date. WWL believe there are changes needed before Wellington Water could use the schemas in Volume 2 of the standards. Wellington Water requests more collaborative work and engagement at working group level. In the current state we would certainly not endorse mandatory use of the standards that includes Volume 2. We believe Sections 1.5-1.8 of Volume 2 should be deleted from this document. This text, which discusses analytical methods, is not relevant to this volume. | General | Further discussion with Wellington Water. Business Case. Details discussed in further feedback from Wellington Water. | Vol 1 - Vol 2 |  | Volume 2 is complete in these draft standards | Good for discussions - guideline first, but also need 'analytical consistency'… |  |  | Noted: no action required | Noted: no action required | Volume 2 is now complete | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action |  |  |  |  | 1 | 1
515 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | Relevance of Geospatial Statements Each of the current three documents makes some broad statements about the recording of data within a GIS application.GIS is a critical methodology for how we choose to represent asset data. At WWL, we believe that the role of the Standards is to define as-constructed spatially aware data – spatial data should form a part of the data specifications in Volume 1. We do not believe that it is the role of this document to determine how spatial data is represented within individual organisations (e.g., symbology). | NA | Action on volume 1. | Vol 1 - Vol 2 |  | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | Data specifications in volume 1: it does - as co-ordinates in x-y & height (z). Not the role of the document to determine how spatial data is represented: agree (but should point to international standard OGC) |  |  | Noted: no action required | Noted: no action required | Spatial definitions for asset management purposes is no less important than attribute data. These standards spatial component meet the test for OGC standards (NZ Spatial Standards) | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
516 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 6. Hierarchy and Definitions It’s a positive development to see the emergence of a common hierarchy across water assets. a. We do feel that greater clarity and definition is required to determine the scope of each asset class defined within the Standard – our focus group workshops uncovered some examples where practitioners were uncertain as to where particular assets should be located. As a suggestion, a table describing asset examples included together with the hierarchy contained in the pre-amble to the Standard will help to overcome this. b. It was also noted that the current Wastewater Standard has no allowance for “Civil Structures” at all, nor “Tunnels”. We have examples in Wellington Water of both, within the Wastewater network. c. Same Hierarchy: A key part of the input provided by Wellington Water at the working sessions was that the same hierarchy should be applied to ALL networks, recognising that there may be a small number of non-populated asset classes in some networks. This approach seems to be supported by the diagram inserted in the preamble to each Standard – but is at odds with how the Standards are structured into 3 volumes, and missing some asset classes. | NA | a. Action on volume 1. Possible flow on to volume 2. b. These structures are outside of scope of the structure as agreed in technical workgroup. C. action on volume 1. | Vol 1 - Vol 2 |  | Included in the draft Standards | a. noted. B. noted will include. C. same hierarchy: note, there are some ISO (IFC - Industry Federation Class) developments in the UK which deal with this too. C. preamble at odds with structure into 3 volumes - can we understand where/how - this is not the intent. |  |  | Sector Discussion | Included | Included in the draft Standards | 1.7 Heirarchy | 1 | [7 empty] | 1 | [16 empty] | MAY NEED FURTEHR DISCUSSION WITH Oliver Same hierarchy has been ap[plied and only assets that are in the network are included are these additional assets in tretament plants ? | More information required for a decision |  | n/A
517 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 7. Conflict with other Standards or by-laws There are a number of standards that can be utilised to form a set of data requirements for use by water authorities. Our feedback sessions raised the question as to whether any research had been done as to whether these proposed Standards were in conflict with any existing Standard and/or by-law used within New Zealand. | Other standards | Statement noted. The standards as they are reflect the feedback from the technical working groups (industry feedback and experts advisors) | Vol 1 - Vol 2 |  | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | Yes, building code, ISO Metadata, OGG (spatial). |  |  | Included | Included | Conflicts were investigated and none were identified A number of standards were reviewed (for example, spatial) | General | 1 | [7 empty] | 1 | [17 empty] | No action |  | N/A
518 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 8. Data Relationships The linkages between Volume 1 and 2 are shown in the specification related to each asset class; however, this can be more easily represented by creating a simple relational data model at the front of the standards, with each element of the table then referring users to the appropriate standard sub-table for further definition. This would show users how different elements of asset and asset-related data & information are related to each other, and help to overcome some of the issues related to definition discussed in section 1.6 above. | Data | Action required: data scientists to review Volume 1. Heierarchy question | Vol 1 - Vol 2 |  | Haydn & George | Haydn & George |  |  | Included | Included | Tables will be referenced in Final Versions | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action |  | N/A
519 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 9. Degree of ‘Prescription’ The metadata schema appears to be based on an implicit assumption as to how assets will be managed, how activities will be carried out in the future and the desired outcomes. These have been effectively hardcoded into the standard and implicitly limit the Asset Management decisions and practices that can be carried out within three waters organisations. a. Has it been demonstrated that the schema will deliver good asset management in practice or is the delivery of benefits based on theoretical prediction from future outcomes? b. There is an implicit assumption that life, condition and service delivery all follow the same path for all assets and so a deterministic outcome can be predicted for all assets based on observed condition. Has the same mechanism been shown to apply to all assets e.g. PE pipes, control systems, etc? c. Any Asset Management practice has improvement as a key result area (KRA). How will the metadata standards reflect changes and improvements and what is the implication for organisations that have invested in systems and processes to meet the standards - the impact of making changes to an MMS, GIS, CRM or other business systems is not trivial. A possible solution would be to show how Asset Management processes are supported by the data standards. At present it is difficult to assess all the data and information requirements of asset owners, service providers and customers are satisfied. An Outcome-Based Standard rather than a prescriptive Standard may offer a better approach - similar to safety or quality management systems. | Implementation | Raises some important points. Implementation question to be considered. Outside the scope of this current standard. | Vol 1 - Vol 2 |  | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | Asset Management decisions and practices limitations: it is to a point - but in an analytical sense - this is a data standard for algorithms and evidence for evidence base decision-making. If there are more analytical outputs which require more attribute/data the lets discuss. a. yes - analytics in many divers instances (evidence) b. not so - for discussion - this is about analytical engines - then decisions. c. few options - but less discuss (e.g.. data completeness, or stochasticity values etc...) Outcome based standard: all outcomes are underpinned by measureable outputs first... at least complimenting for evidence. |  |  | Noted: no action required | Noted: no action required | These standards are about an analytical platform to produce analytics for evidence-based investment decision-making. There is no guarantee everyone will use evidenced-based investment decisions - but if they wish, these standards enable that. The next step is the analytics that provide the insights into these circumstances for those decisions. | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
520 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 & Vol 2 | General | [5 empty] | 10. IT Systems and Migration WWL recognises this is is not an “IT” conversation. Nonetheless, we believe the impacts of potential IT changes should be addressed in the document – if only to set appropriate expectations as to the risks associated with full-scale implementation. In moving to a new data standard, this may involve the transfer of data from existing systems to another. Regardless of intent, there will be data loss and integrity issues from this process. We should expect some history and attributes to be lost (piecemeal or wholesale) or stranded in other systems. | Implementation | See comments Haydn | Vol 1 - Vol 2 |  | This is not within the scope of these standards | Only to set appropriate expectations: not so sure - but certainly an implementation questions - to discuss. Data loss and integrity issues: not necessarily - FME tools etc. |  |  | Noted: no action required | Noted: no action required | This is not within the scope of these standards | No Specific Reference |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
521 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 1. Date Range & Traceability: Ensure any attributes that do change with time but do not result in a new asset are recorded against the asset – with knowledge of date, time and who made the change to the asset. For example if coatings, jointing or sealing systems or surrounding environment such as ground and loading conditions change with time, there is facility to record changes of these attributes with time. Operational risks for an asset may change if changes occur to asset attributes over time – e.g., ground stability, use of spares, different connections, external loading conditions such as traffic or trench support, imposed pressure. It is important to record these changes with knowledge of when and where and who imposed the changes. In short, the requirement to reflect a date range and trace ‘who’ made the changes applies to nearly all asset data attributes, and should be reflected in the Standard. |  |  | Vol 1 |  |  |  | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | Noted: no action required | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded will be determined by each organisation. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
522 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 2. Relationship to Customer Service: There has to be recognition within the standard that customer service issues retained on a customer service database that are verified as attributable to asset attributes are linked to the asset. These issues may be associated with continuity of service, quality or financial. While the schema containing ‘Customer Service’ type data is likely to fall within Volume 2 of these Standards, allowance should be made in Volume 1 to ‘link’ to this schema. This is related to the comments made on “data relationships” in section 1.8 of this document. |  |  | Vol 1 | [5 empty] | Noted: no action required | Noted: no action required | Service level performance is included in Volume 2 | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
523 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 3. Detail Code Lists: We note that there are no code lists provided with Volume 1 of the Standard. Therefore, we submit that further work is required on determining the codes associated with each asset data attribute. For example, Volume 1 holds good attribute detail in relation to ‘Pipes’ – including material, manufacturer and construction date. However, WWL believes that the detail on attribute fields such as ‘material’ should be explicitly included in the standard. In this example, the difference between “rolled” vs “spun” concrete pipes makes for a material difference in asset performance. |  |  | Vol 1 |  |  |  | Under Review | Have the code lists been distributed? Can be assigned as sector discussion This detail was identified at the previous workshops and determined to be appropriate . 26/3/2017 | Sector Discussion | Sector Discussion | Code lists are included Attributes to be discussed | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok |  | change needed in docs |  | codelists added | codelists added | codelists added | n/a | [5 empty] | More information required for a decision
524 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 4. Asset Disposal: Disposal of assets (particularly network assets) can become significant issues especially when they are difficult to remove or unsafe to leave in their installed position. Changes to asset attributes or surrounding environment (such as ground, traffic, building locations, loading conditions) can force a disposal decision. Again changes to asset or asset component attributes as well as asset environment over time should be recorded. |  |  | Vol 1 |  |  |  | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | Noted: no action required | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
525 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 5. Acquisition Type: Where an asset is not constructed, ‘acquisition’ data is fundamental as-built information necessary for the accurate valuation and depreciation of assets. Fields such as acquisition type (e.g.: Vested, Found, Capital renewal or upgrade) and acquisition date, are not apparent in the schema. |  |  | Vol 1 |  |  |  | Noted | Please refer to Project and common data | Noted: no action required | Noted: no action required | Please refer to Project and common data | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
526 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 6. Ownership Change: Knowledge of ownership change and when the impacts on planning for growth and network capacity reinforcing the importance of linking attribute changes with time. |  |  | Vol 1 |  |  |  | Noted | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | Noted: no action required | Noted: no action required | The purpose of these standards is to capture data about specific assets at a particular point in time for incorporation into asset woners systems. It is not in the scope to create a schema for mainteance purposes. How changes are recorded or decisions made will be determined by each organisation. | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
527 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 7. Resource Consent: Where assets and asset performance are linked to resource consent conditions, there must be an ability to link to specific consents consent conditions (e.g., a scour pipe for a watermain and a discharge consent). References to consents beyond construction are contained within s2.3.4 of the Potable Water Standard (Wells), but there is no reference in the Wastewater Standard or the Stormwater Standard. |  |  | Vol 1 |  |  |  | Noted | Please refer to Project and common data | Noted: no action required | Noted: no action required | Please refer to Project and common data | 2.1.7 Project Attributes |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | ok | [12 empty] | No action
528 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 8. External conditions: In addition to the traditional asset attributes such as pipe materials and joint types, there will be many asset attributes that affect hazard resilience planning. (soil, groundwater, loading, soil stability, etc). |  |  | Vol 1 |  |  |  | Under Review | Please provide details for the specific tables and the relevant attributes to be considered Workshops will be held in May for further contribution. 26/3/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pipes |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
529 | Oliver Mander | Wellington Water | 3-Waters | Vol 1 | General | [5 empty] | 9. Pump Stations: There is a parent-child relationship between pump stations and the assets they contain, that is not fully reflected in how the Standard has been constructed. |  |  | Vol 1 |  |  |  | Under Review | Please provide details for the specific tables and the relevant attributes to be considered Workshops will be held in May for further contribution | Sector Discussion | Sector Discussion | More information is required to inform a way forward | General for Pump Station |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
530 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes General feedback from the Wastewater and Potable Water sections should be treated as relevant to Stormwater. b. Validation flags would be a useful addition to all asset classes, to separate ‘observed’ data from ‘inferred’ data. This will allow a measure of confidence to be assigned to asset-related data. |  |  | Vol 1 |  |  |  | Noted | This will be catered for through recording the "Source" 14/03/2017 | Noted: no action required | Noted: no action required | This will be catered for through recording the "Source" | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
531 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes c. Data Accuracy should be recorded as part of the data acquisition. |  |  | Vol 1 |  |  |  | George/Haydn | Say more about this. Which aspect of data accuracy the completeness of the data or the spatial accuracy of the data? 14/03/2017 | Included | Included | This is a derivation for Volume 3, including precision of survey data | General | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
532 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes d. There is a role for the ‘normalisation’ of data – attributes were often repeated, increasing the complexity of the standard and hampering functionality for use by consultants, contractors and suppliers updating many assets classes at the same time. This is related to the comments made on “data relationships” in section 1.8 of this document. |  |  | Vol 1 | Now normalised and standardsed with Metaconnect |  |  | Haydn | which document is this referring to? 14/03/2017 | Included | Included | Now normalised and standardsed with Metaconnect | General | No action | [7 empty] | 1 | [17 empty] | No action
533 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes e. Natural features were regarded as “out of scope” for the Standard. However, natural features, such as streams, lakes and rivers form a key part of a holistic stormwater system. Allowance should be made within the Stormwater standard for data associated with natural features. It was noted that natural features can impact “system-wide” asset renewal decisions and associated costs; their inclusion would help further the overall goals of the Standard. |  |  | Vol 1 |  |  |  | George/Haydn | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | Excluded | Excluded | These features are described by LINZ in their New Zealand physiographic datasets and themes. Discussion required as to the type of data required and how they are to be referenced as part of an overall model. | General |  | 1 | [6 empty] | 1 |  |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
534 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | General | [5 empty] | All Asset Classes f. Some gaps in asset classes and/or attributes were discussed by the focus group at Wellington Water. These included: o Keys (an attribute associated with an asset) o Ladders o Fences o Bridges o Tracks |  |  | Vol 1 |  |  |  | George/Haydn | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | Sector Discussion | Sector Discussion | Reference to be made to other standards that would contain this detail Possibly create an overarching list of all asset classes covered and which standard they are recorded | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
535 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. UID field is 20 characters long, while ‘Owner’ is 100 characters long. This is excessive. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.3.1 Containment Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
536 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. While a ‘volume’ is provided, there is no allowance for internal measurement fields. The group felt that it would be better to represent the source data (height, length, width) rather than the calculated field (volume). |  |  | Vol 1 |  |  |  | Noted | Already incorproated into the table 16/03/2017 | Included | Included | Already incorproated into the table | 2.3.1 Containment Structure | 1 | [7 empty] | 1 | [17 empty] | No action
537 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE a. A practical definition should be included as to what constitutes a retaining structure. At first reading, the feedback group struggled to understand whether sumps, intake and outlet structures should be included in this. |  |  | Vol 1 |  |  |  | Noted | To be read in conjunction with the codelist specified Retaining Structure Type 16/03/2017 | Noted: no action required | Noted: no action required | To be read in conjunction with the codelist specified Retaining Structure Type | 2.3.3 Retaining Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
538 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE b. Terminology – there was some disquiet with the term “retaining structure” as this could also cover a “treatment structure” – which exists for other reasons not associated with retaining water. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.3.3 Retaining Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
539 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE c. This may also apply a requirement for an attribute describing “asset function” within this asset class. |  |  | Vol 1 |  |  |  | Noted | Please refer to the field "Purpose" and the code list Retaining Structure Purpose 16/03/2017 | Noted: no action required | Noted: no action required | Please refer to the field "Purpose" and the code list Retaining Structure Purpose | 2.3.3 Retaining Structure |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
540 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  RETAINING STRUCTURE d. A number of attributes were felt to be relevant to this asset class, that were not included within the standard. This includes (but is not limited to): o soil type o grass type o permeability o infiltration rate o depth o vegetation type |  |  | Vol 1 |  |  |  | under review | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | These elements were reviewed at the prevuious workshops and determined to not be required. However will address again forconsideration and adoption or not at the next workshops. There are a number of fields already included that could cover, soil type (Bank material), grass type, vegeatation type (lining material) - are these suitable? Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.3.3 Retaining Structure |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
541 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  WING WALLS a. The Standard makes no allowance for ‘Aprons’ – merely the wall! |  |  | Vol 1 |  |  |  | George/Haydn | The attributes in this asset class were reviewed and agreed to at the previous workshops. Please identify what allowance is required - as in what additional data and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | More information is required to inform a way forward | 2.3.4 Wing Wall |  |  | 1 | [5 empty] | 1 |  |  |  |  | change response to More information is required to inform a way forward | Changed | [11 empty] | More information required for a decision
542 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  WING WALLS b. As part of the asset, a fence is often constructed for H&S reasons – it is inherently part of the asset, as it is a legal requirement. Is this a separate asset? How is it recorded? |  |  | Vol 1 |  |  |  | George/Haydn | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | Included | Included | Yes a fence is a separarte asset. Please refer to the Roading asset metadata standards. | 2.3.4 Wing Wall | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
543 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Civil Structures  EMBANKMENT a. The Standard makes no allowance for any attributes associated with ‘V Notches’ – such as elevation or width. This is a typical attribute associated with a weir, which is included in this asset class according to the Standard. |  |  | Vol 1 |  |  |  | George/Haydn | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | Sector Discussion | Sector Discussion | Please identify what allowance is required - as in what additional data and the impact of not having the data available. | 2.3.2 Embankment |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
544 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER a. This feature is to represent the location of Access Chambers such as manholes related to the Stormwater network. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.1 Access Chamber |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
545 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER b. The point used to represent the location of the access point must be positioned on the access point centroid, not the access point lid location. Failure to do this will corrupt linear assets related to the feature. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard 16/03/2017 | Included | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.1 Access Chamber | 1 | [7 empty] | 1 | [6 empty] | change needed doc | example provided for review | done | done | done | n/a | n/a | n/a | n/a |  |  | Change made document updated
546 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER c. Dates associated with observation and/or survey data should be included within the Standard. These form a fundamental part of condition assessment and need to be included in the Condition section of Volume 2. |  |  | Vol 1 |  |  |  | under review | Please provide your definition for "observation and/or survey data" 16/03/2017 | Sector Discussion | Sector Discussion | Please provide your definition for "observation and/or survey data" | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
547 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER d. A separate table / standard should be established within Volume 2 where survey and observation outcomes must be available. |  |  | Vol 1 | Vol 1 & 2 are inherantly linked by asset ID and location |  |  | Haydn | 2017-03-16 | Included | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.1 Access Chamber | 1 | [7 empty] | 1 | [17 empty] | No action
548 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER e. Does this include data related to the accessway asset? (e.g., ladders etc). Do we need more than a simple indication of the presence of ladder or step irons? |  |  | Vol 1 |  |  |  | under review | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | These elements were reviewed at the previous workshops and determined to not be required. Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
549 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER f. The ‘depth’ field should be represented as an elevation level rather than depth. |  |  | Vol 1 |  |  |  | George/Haydn | Don’t have an issue one way or another - this is the only mention of it so far as I can recall. | Sector Discussion | Sector Discussion | To be reviewed by Technical Working Groups - intent to include | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 |  |  |  |  | change response to To be reviewed by the TWG for consideration of inclusion | Added | make mention of change request | [9 empty] | request documented | More information required for a decision
550 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  ACCESS CHAMBER g. Location detail such as address is missing. Access points are point objects, and as such location, address, street_name are easily attributable. |  |  | Vol 1 |  |  |  | under review | Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.1 Access Chamber |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
551 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS a. A clear definition is required for this asset class, to ensure that individual assets are classified appropriately. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | More information is needed to inform a way forward. Also refer to code lists | Sector Discussion | Included | More information is needed to inform a way forward. Also refer to code lists | 2.4.2 Channels | 1 | [7 empty] | 1 | [6 empty] | change response and status | refer to code list | refer to code list | refer to code list | refer to codelist | [5 empty] | DOCUMENT AS A REQUEST request data prior to next workshops | More information required for a decision
552 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS b.This asset class should include an allowance for “Natural Features”, as described above in section 3.1(e). |  |  | Vol 1 |  |  |  | Noted | Please refer to comment above 16/03/2017 | Noted: no action required | Noted: no action required | Please refer to comment above | 2.4.2 Channels |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
553 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS c. Cross-section data (shapes, elevation) would form a useful addition to this Standard. |  |  | Vol 1 | Put hydraulic profiles as code list |  |  | Haydn | Not sure what is being requested here. If they are talking about the detail that is in the cross swections then this can be accessed from the design plans once verified that what has been designed has been built 16/03/2017 | Sector Discussion | Included | Code list of profile shape to be considered for inclusion in the standards | 2.4.2 Channels | 1 | [7 empty] | 1 | [7 empty] | Haydn pleaseexplain how this will be included | [9 empty] | More information required for a decision |  |  | y | create code list of profile shape
554 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  CHANNELS d. Both Channels and Retaining Structures should be linked to a “Stormwater Quality” information field within Volume 2 of this Standard. |  |  | Vol 1 | Vol 1 & 2 are inherantly linked by asset ID and location |  |  | Haydn | 2017-03-16 | Included | Included | Vol 1 & 2 are inherantly linked by asset ID and location | 2.4.2 Channels | 1 | [7 empty] | 1 | [17 empty] | No action
555 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES a. General impression is that this is a comprehensive standard for this asset class. |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.4 Pipe |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
556 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES b. “Utilisation”: how is this defined? Is it peak flow or average flow? Clarification required for the Utilisation output from Volume 2. |  |  | Vol 1 | Either - the analytic will define that based on analytic computatoinal assumption |  |  | Haydn | 2017-03-16 | Included | Included | Either - the analytic will define that based on analytic computatoinal assumption | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | Haydn
557 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES c. It is not clear that the Const_Date attribute is used for new construction as well as the date of asset relining/renewal. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard 16/03/2017 | Included | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.4.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | change needed doc | changed to Date the asset was constructed/built/installed/relined/renewed | done | done | done | done | [5 empty] | Change made document updated
558 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES d. While there is a field called “protection” (i.e., pipes being contained within a sleeve), the purpose of “sleeving” a pipe may not always be about protection. Further definition required. |  |  | Vol 1 |  |  |  | under review | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. 16/03/2017 | Sector Discussion | Sector Discussion | In this context this is what Protection refers to. It does not refer to a renewal or rehabilitation process. Please provide additional information for consideration of expanding the definition. | 2.4.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
559 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES e. Is the invert level’ or ‘elevation’ recorded against the Access Chamber or the Pipe. |  |  | Vol 1 |  |  |  | Noted | The invert level is to be recorded against a pipe 16/03/2017 | Included | Included | The invert level is to be recorded against a pipe | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | No action
560 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES f. Is the Invert Level recorded at the wall of the Access Chamber or as a ‘project’ value in the centre of the Access Chamber? |  |  | Vol 1 |  |  |  | Noted | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | Included | Included | Typically the invert level is recorded at the wall of the access chamber unless there is a drop structure inside or outside the access chamber. | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | No action
561 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES g. There is no data attribute describing pipe capacity – is this something for Volume 2? |  |  | Vol 1 | yes in Volume 2 |  |  | Haydn | 2017-03-16 | Included | Included | yes in Volume 2 | 2.4.4 Pipe | 1 | [7 empty] | 1 | [17 empty] | No action
562 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES h. The directionality attributes should be named US_Node and DS_Node, which implies the IL attributes need to be US_IL and DS_IL. The Standard assumes that pipes link different ‘asset classes’…however, there is some possibility that pipes simply ‘end’ in a natural or non-asset feature. This implies that a NULL feature such as pipe_end or that a pipe end may itself be an outlet. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard. | Included | Included | A clarification will be made to the description for this asset type in each relevant standard. | 2.4.4 Pipe | 1 | [7 empty] | 1 | [6 empty] | changed mind review wording to reflect that there is always something at the end of a pipe, maybe an end point, a blank end an access point | h. IL's are always placed on the pipe irrespective of its end point. Regards Pipe End - Noted. It is proposed that there will always be some kind of feature depicting where the pipe ends to assist with creation of a topological structure once the data is provided each asset owner will then be able to address it as needed. e.g. Maybe a fitting (blank end), maybe a structure, maybe a non physical feature (pipe end) | done | done | done | n/a | [5 empty] | Change made document updated
563 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PIPES i. An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. |  |  | Vol 1 |  |  |  | under review | Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.4.4 Pipe |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
564 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets (see section 2.9 in this document). |  |  | Vol 1 | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's |  |  | Haydn | 2017-03-16 | Noted: no action required | Noted: no action required | parent / child relkationships are a relational database concept - it is not the intent of the standards to define these - others prefer all electrical's | 2.4.5 Pump Station |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
565 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Reticulation Structures  PUMP STATION b. Noted that ‘wet wells’ may have their own characteristics |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.4.5 Pump Station |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
566 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP a. Pump motors could be regarded as a distinct asset – motors are replaced without replacing pumps, and their value is at a level where that becomes relevant. |  |  | Vol 1 |  |  |  | Noted | Attribute fields are included in the Pupm asset class for motors. Please review and provide details of additional | Included | Included | Attribute fields are included in the Pupm asset class for motors. Please review and provide details of additional | 2.5.2 Pump | 1 | [7 empty] | 1 | [17 empty] | No action
567 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP b. A data attribute describing “duty” or “stand-by” would be useful. |  |  | Vol 1 |  |  |  | Noted | An attribute field currently exists for this "Pump Usage" 16/03/2017 | Included | Included | An attribute field currently exists for this "Pump Usage" | 2.5.2 Pump | 1 | [7 empty] | 1 | [17 empty] | No action
568 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - PUMP c. There is no data attribute describing any form of ‘trigger level’ that defines when the pump starts. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | Will include for ratification by the reviewers. 16/03/2017 | Sector Discussion | Included | Will include for ratification by the reviewers. | 2.5.2 Pump | 1 | [7 empty] | 1 | [6 empty] | make mention of change request | [9 empty] | request documented | New attribute proposed | Trigger level
569 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE a. There are no attributes describing the ‘trigger level’ on a Valve, nor the nature of the trigger. Date fields may also be required to support this, as trigger levels can be modified. |  |  | Vol 1 |  |  |  | under review | Please provide complete list for consideration and their descriptors and the impact of not having the data available. 16/03/2017 | Sector Discussion | Sector Discussion | Please provide complete list for consideration and their descriptors and the impact of not having the data available. | 2.5.3 Valve |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
570 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE b. Use of Yes/No fields may not give appropriate granularity. |  |  | Vol 1 |  |  |  | Noted | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG 16/03/2017 | Included | Included | There are 2 fields. Telemtry which indicates if telemetry is available and then this asset is described in another class. The other field indicates if the asset is above or below ground. Please provide any further detail that is suggested for consideration by the TWG | 2.5.3 Valve | 1 | [7 empty] | 1 | [17 empty] | No action
571 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE c. Consent ID field may be relevant (e.g., fish barrier). |  |  | Vol 1 |  |  |  | Noted | Please review the Project and Common attributes 16/03/2017 | Noted: no action required | Noted: no action required | Please review the Project and Common attributes | 2.5.3 Valve |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
572 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT a. Better definition of the types of assets that go in this asset class may be required (this relates to the comment in section 1.6 of this document). |  |  | Vol 1 |  |  |  | Noted | 2017-03-16 | Noted: no action required | Noted: no action required | Reviewed and Noted only | 2.5.1 Equipment |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
573 | Oliver Mander | Wellington Water | Stormwater | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - EQUIPMENT b. The text descriptor for the asset class uses an “Air Valve” as an example – this should be under a different asset class (“Valves”). |  |  | Vol 1 |  |  |  | INCLUDED - DOC | A clarification will be made to the description for this asset type in each relevant standard 16/03/2017 | Included | Included | A clarification will be made to the description for this asset type in each relevant standard | 2.5.1 Equipment | 1 | [7 empty] | 1 | [6 empty] | change needed doc |  | done | done | done | n/a | [5 empty] | Change made document updated
574 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: a. General feedback from the Wastewater and Stormwater sections should be treated as relevant to Potable Water. b. Acquisition Date: Include Acquisition date in addition to construction date |  |  | Vol 1 |  |  |  | Noted | 2017-03-07 | Noted: no action required | Noted: no action required | Reviewed and Noted only | General |  |  |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [13 empty] | No action
575 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: c. H&S: Health and Safety and ‘access’. Assets can have very specific H&S and Access instructions, issues, requirements. 250 characters is not very much, a longer field containing more would be useful for assets that are access points. A free text field for “access” would be useful in addition to free text about Health and Safety. Alternately, a “Safety in Design” component in Volume 2 would include the necessary attributes. |  |  | Vol 1 |  |  |  | George/Haydn | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities 7/3/2017 | Sector Discussion | Sector Discussion | H&S information is to be collected independently, the standards are a mechanism to ensure they trigger that there are 'special circumstances'. A code list will be created Free text fields are not required, this information should be a prompt to H&S system response / detail | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you review your response as it onlyt partly answers the question | updated comment not certain how this would be done as it is specific to each asset | [11 empty] | New Code List proposed | Health & Safety Type
576 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: d. “Comments attribute - 250 characters is not very much for these either. Can there be more? |  |  | Vol 1 |  |  |  | George/Haydn | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | Sector Discussion | Sector Discussion | Suggest further information is added as an addendum, possibly include additional Comments fields. Field length needs to take into account system capabilities | General |  |  | 1 | [5 empty] | 1 |  |  |  |  | ok | [12 empty] | More information required for a decision
577 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: e. Codes should all be the same length (e.g. 4 characters) |  |  | Vol 1 |  |  |  | Noted | 10 character fields have been adopted to allow for expansion 7/3/2017 | Noted: no action required | Noted: no action required | 10 character fields have been adopted to allow for expansion | General |  |  |  | 1 |  |  |  |  | 1 | [17 empty] | No action
578 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: f. Spatial Data: The H_Prec and V_Prec should be where the spatial data (Northings, Eastings and Reduced Level) is stored or the N, E and RL should be stored here as well. |  |  | Vol 1 |  |  |  | Under Review | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate. 7/3/2017 | Sector Discussion | Sector Discussion | Agreed at TWG that all measurements are absolute and co-ords calculated from data provided. Will review where appropriate | General |  |  | 1 | [5 empty] | 1 | [17 empty] | More information required for a decision
579 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | All Asset Classes: g. Some terminology used seems to differ from what is commonly used in the three waters industry. |  |  | Vol 1 |  |  |  | Under Review | Need more information and example 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and example | General |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
580 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE a. Include an ability to capture alternative asset ID’s linked to instrumentation (e.g., SCADA tags). |  |  | Vol 1 |  |  |  | Under Review | Need more information and example 7/3/2017 | Sector Discussion | Sector Discussion | Need more information and example | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
581 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE b. Fall protection should be more detailed than Y/N, what kind of fall protection? Ladder? Rail? Cage? Net? Bungy? Parachute? |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | can be included through health and safety column and codelist | [7 empty] | request documented | More information required for a decision
582 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE c. SHAPE could be included. |  |  | Vol 1 |  |  |  | Noted | Already defined as a polygon feature 7/3/2017 | Included | Included | Already defined as a polygon feature | 2.3.1 Containment Structure | 1 | [9 empty] | 1 | [15 empty] | No action
583 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE d. Something about whether it is above ground, below ground, partially buried, e.g. field name Burial_Stat (Burial status)? |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request |  | new ATTRIBUTE FIELD AND ASSOCITED code list created | [7 empty] | request documented | New Code List proposed | Burial Status Above ground Below ground Partially buried
584 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE e. Terminology: max_wtr_level is not industry standard, it's TWL (top water level) and BWL (bottom water level). WWL recognises that other terms may be in use elsewhere in NZ in some instances, but believes that TWL and BWL are in common use in all councils. |  |  | Vol 1 |  |  |  | Noted | Terms agreed to by TWG. WWL can map from this to their own terminology. 7/3/2017 | Noted: no action required | Noted: no action required | Terms agreed to by TWG. WWL can map from this to their own terminology. | 2.3.1 Containment Structure |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
585 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE f. Add an Internal Diameter field for circular reservoirs and a Width x Length field for rectangular reservoirs. |  |  | Vol 1 |  |  |  | Noted | Length, height and width are fields and are conditional on asset shape 7/3/2017 | Noted: no action required | Noted: no action required | Length, height and width are fields and are conditional on asset shape | 2.3.1 Containment Structure |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
586 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE g. Add an Inlet Protection field – values such as “NRV”, “ASV”, “Standpipe”. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
587 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE h. Add an Inlet Type field – “Bottom Feed”, “Top Feed”. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
588 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE i. Terminology – Change “Shut off Valve” to “Outlet Shut off Valve” to distinguish it from the Inlet Protection field. Possibly add “Auto” to it as well. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
589 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structures  CONTAINMENT STRUCTURE j. Include a field to distinguish if the reservoir is partitioned – Y/N? – also the height of the partition. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.3.1 Containment Structure |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
590 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Field 'Con_spc' (confined space) is YES/NO, however some consulted members follow different codes of practice covering RESTRICTED spaces as well as CONFINED spaces. There needs to be an identification of which one it is. Suggestion is a field named something like 'Entry Restriction Category' with options RESTRICTED, CONFINED, or NONE. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
591 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Access Chamber Type – Some chambers may not necessarily house valves, but rather Cable Ducts or Cathodic Protection equipment. Might pay to include a field which denotes what type of access chamber the chamber is; e.g. “Valve Chamber”, “Cable Duct Manhole” etc. |  |  | Vol 1 |  |  |  | Noted | Chamber Type is already included. Additional Types can be included. 7/3/2017 | Included | Included | Chamber Type is already included. Additional Types can be included. | 2.4.1 Access Chamber | 1 | [9 empty] | 1 | [15 empty] | No action
592 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure – EMBANKMENT STRUCTURE a. Include link to monitoring and surveillance records. WWL notes that an “Observations” does not exist in Volume 2. An “Observations” schema can inform a number of other schemas or asset tables – including “Asset Condition”. |  |  | Vol 1 |  |  |  | George/Haydn | Not an 'As Constructed' attribute | Excluded | Excluded | Not an 'As Constructed' attribute | 2.3.2 Embankment |  | 1 | [6 empty] | 1 |  |  |  |  | ok |  |  |  | no action | no action | no action | n/a | [5 empty] | No action
593 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure - WELL a. Include Ground Water Level |  |  | Vol 1 |  |  |  | Noted | Ground Water Level varies and may misrepresent the situation if recorded 7/3/2017 | Noted: no action required | Noted: no action required | Ground Water Level varies and may misrepresent the situation if recorded | 2.3.4 Well |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
594 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure - WELL b. Resource Consent number |  |  | Vol 1 |  |  |  | Noted | Included in Project Attributes 7/3/2017 | Included | Included | Included in Project Attributes | 2.3.4 Well | 1 | [9 empty] | 1 | [15 empty] | No action
595 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Civil Structure - WELL c. Include a field to cover Regional Public Health grading |  |  | Vol 1 |  |  |  | George/Haydn | Will this be known at time of construction? 7/3/2017 | Sector Discussion | Included | Code lists for NZDWS could be included - for discussion | 2.3.4 Well |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you review your response as it onlyt partly answers the question | [12 empty] | More information required for a decision
596 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING a. Fitting has field 'Link_feat', but usually a fitting will usually link to two features, or 3 if it's a tee. If this is going to be linked then it needs to be an array. The joint type is also often different on different sides of the tee or join, so joint_type should also be part of the same array. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
597 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING b. Include a field for MANUFACTURER, it's useful for replacement etc. |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.3 Fitting |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New attribute proposed | Manufacturer
598 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING c. There was some confusion about whether a tee would be included under fitting or node. WWL submits that it should be a fitting. |  |  | Vol 1 |  |  |  | Noted | Tee is inlcuded in the codelist for fitting type 7/3/2017 | Included | Included | Tee is inlcuded in the codelist for fitting type | 2.4.3 Fitting | 1 | [9 empty] | 1 | [15 empty] | No action
599 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING d. Any fitting that changes the diameter, material or construction date/age of a pipe should be treated as a Node, e.g. Reducer/Taper. |  |  | Vol 1 |  |  |  | Noted | Agreed | Included | Included | Agreed | 2.4.3 Fitting | 1 | [9 empty] | 1 | [15 empty] | Change made document updated
600 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - FITTING e. Nodes will also have a fitting associated with it. (e.g. a T at a pipe junction) – all the data collected for fittings should apply to nodes as well? |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. Is this common across the industry? | Sector Discussion | Sector Discussion | Nodes are not assets, fittings are. | 2.4.3 Fitting |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | suggest no - only have the attributes against the fitting create a lsiting of node numberrs and the type of asset it is associated with | [9 empty] | More information required for a decision |  |  | y | A node is not an asset updated comment
601 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE a. Anchor Blocks, Thrust blocks. These are significant assets with significant properties, you wouldn't want to find one when you were trying to dig! They deserve an asset class. |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. What needs to be known about them? | Sector Discussion | Sector Discussion | To be discussed with TWG. What needs to be known about them? | 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New Asset Class proposed Detail of data requirements needed | Support Structures
602 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE b. Include new fields - Pipe Coating Material and Pipe Lining Material |  |  | Vol 1 |  |  |  | George/Haydn | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. Attribute will be added to accommodate the 'sub-components' | Included | Included | If lining or coating is added afterwards, it can be treated as a renewal. If part of the initial installation, then need to be described as a pipe type material. Attribute will be added to accommodate the 'sub-components' | 2.4.5 Pipe | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | New attribute proposed | Pipe Coating Material Pipe Lining Material
603 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE c. Also include - Joint method and joint type |  |  | Vol 1 |  |  |  | Noted | Joint Method already included. Joint Type not required as per TWG. 7/3/2017 | Included | Included | Joint Method already included. Joint Type not required as per TWG | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
604 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE d. There should be an ability to record date ranges for some asset attributes – such as pipe linings, where a pipe is later re-lined. |  |  | Vol 1 |  |  |  | Noted | Already catered for. 7/3/2017 | Included | Included | Already catered for | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
605 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE e. Invert level definition - is this the soffit or the top of the pipe? Make sure that this is standardised. |  |  | Vol 1 |  |  |  | George/Haydn | Pressure pipe typically does not include IL but may be handy. 7/3/2017 | Included | Included | This is the invert level at the bottom of the pipe | 2.4.5 Pipe |  |  | 1 | [5 empty] | 1 |  |  |  |  | suggest you review your response as it onlyt partly answers the question as IILalready included. I also misread the comment - this is about where the IL is measured on the pipe. | [12 empty] | No action
606 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE f. Groundwater - Y/N does not provide any more information, is there any way to make this more detailed? E.g. groundwater level |  |  | Vol 1 |  |  |  | Noted | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted. 7/3/2017 | Noted: no action required | Noted: no action required | Agreed at TWG to indicate if ground water is present. Conditions change over time so additional details not wanted | 2.4.5 Pipe |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
607 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE g. Direction of flow is difficult to define in Potable Water reticulation |  |  | Vol 1 |  |  |  | Noted | From and To node used to determine flow directions.7/3/2017 | Included | Included | From and To node used to determine flow directions. | 2.4.5 Pipe | 1 | [9 empty] | 1 | [15 empty] | No action
608 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE h. Terminology – Diameter should be labelled as “Internal Diameter” to distinguish it from nominal and external diameters. |  |  | Vol 1 |  |  |  | INCLUDED - DOC | change in all documents 7/3/2017 | Included | Included | change in all documents | 2.4.5 Pipe | 1 | [9 empty] | 1 |  |  |  |  | change needed doc |  | done | done | done | n/a | [5 empty] | Changes made documents updated
609 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE i. Nominal Bore is not needed as it is the same as Nominal Diameter |  |  | Vol 1 |  |  |  | INCLUDED - Actioned | removed nom_Bore 7/3/2017 | Included | Included | removed nom_Bore | 2.4.5 Pipe | 1 | [9 empty] | 1 |  |  |  |  | check done | make mention of change request | done | done | done | done |  |  |  |  | make mention of change request | Removal of attribute proposed Have marked for removal in documents
610 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE j. Add ¼, ½, and ¾ points for the location of curved pipes (may only be applicable to PE pipes) |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
611 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure - PIPE An additional attribute for land instability is needed. This will allow landslides or soil movement to be recorded by date against the asset. |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. What kind of descriptors are applicable? | Sector Discussion | Sector Discussion | To be discussed with TWG. What kind of descriptors are applicable? | 2.4.5 Pipe |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
612 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER a. Access chambers can have a separate Cover and Lid, can we have fields for both? |  |  | Vol 1 |  |  |  | Under Review | Need examples and diagrams. 7/3/2017 | Sector Discussion | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
613 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER b. Fall protection needs to be defined, what kind of fall protection? |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
614 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER c. Has the access chamber been sealed? Some have. This requires a separate attribute field – ‘Sealed?’ (Y/N). |  |  | Vol 1 |  |  |  | Under Review | Need examples and diagrams. 7/3/2017 | Sector Discussion | Sector Discussion | Need examples and diagrams. | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
615 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – ACCESS CHAMBER d. How can someone record the locations of vents above ground? |  |  | Vol 1 |  |  |  | Under Review | Are vents used with potable water network? 7/3/2017 | Sector Discussion | Sector Discussion | Are vents used with potable water network? | 2.4.1 Access Chamber |  |  | 1 | [7 empty] | 1 | [15 empty] | More information required for a decision
616 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – PUMP STATIONS a. The relationship / hierarchy of this asset class should be re-examined in light of its parent-child relationship to other asset classes – ie, a pump station will inherently contain other assets such as chemical and analytical instrumentation (see section 2.9 in this document). |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
617 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – PUMP STATIONS b. Included a field stating if the pump station is able to connect to a portable generator (Y/N?). |  |  | Vol 1 |  |  |  | Under Review | to be discussed with the TWG | Sector Discussion | Sector Discussion | to be discussed with the TWG | 2.4.6 Pump Station |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New attribute proposed | Portable generator (Y/N)
618 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Reticulation Structure – PUMP STATIONS c. Seismic Standard field is limited to 30 characters, but it would be beneficial to include a 100 character limit to allow for additional information to qualify the % NBS value as seen in this layout: [Standard:Year],[ Importance level], [design life],[ULS and SLS return periods] . e.g. “NZS 1170.5:2004 IL4 100 year life ULS 1:2500 SLS2 1:1000” |  |  | Vol 1 | Propose to add another attribute for the calculation |  |  | Haydn | parts of this are already included, note that the standard may vary over time. Pump Station refererence not include in the version GISSA is using, what version was sent out for review? 7/3/2017 | Included | Included | Propose to add another attribute for the calculation | 2.4.6 Pump Station | 1 | [9 empty] | 1 |  |  |  | New attribute to be included in standard | suggest add another field and keep original field clean | make mention of change request | review | [7 empty] | document request | New attribute proposed | Calculation
619 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE a. There is a general desire for more standards included about how the valve is powered and how the valve is controlled. |  |  | Vol 1 |  |  |  | Under Review | To be discussed with TWG. Is WWL requesting the inclusion? | Sector Discussion | Sector Discussion | To be discussed with TWG. Is WWL requesting the inclusion? | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
620 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE b. Valve control could be through automatic, manual or scada/remote, and an automatic valve might be controlled based on pressure, flow rate, or some depth. |  |  | Vol 1 |  |  |  | Under Review | Consider making Op_Mode a Codelist | Sector Discussion | Sector Discussion | Consider making Op_Mode a Codelist | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New Code List proposed | Valve Control & Automatic Control
621 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE c. Valve power might be derived from electrical, pnuematic or manual motivation. |  |  | Vol 1 |  |  |  | Under Review | see 00620 7/3/2017 | Sector Discussion | Sector Discussion | see 00620 | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | New Code List proposed | Valve Power
622 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE d. A Pressure Reducing Valve (PRV) has upper and lower limits on the upstream and downstream pressures it can work within, and the range of settings for pressure reduction that it can work within. This is important information that is unique to the asset, and is not operational since it is the range of settings that the valve can work in, rather than the settings themselves. |  |  | Vol 1 |  |  |  | Noted | Can be provided as part of the operational instructions at hand over 3/7/2017 | Noted: no action required | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action
623 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE e. Add attribute for the valve’s operational role (operational_role, alphanumeric). This is the function that the valve performs. Attribute values should be defined by code list similar to that included below. |  |  | Vol 1 |  |  |  | Under Review | Refer to Valve Type codelist to see if this can be covered here. | Sector Discussion | Sector Discussion | Refer to Valve Type codelist to see if this can be covered here. | 2.5.3 Valve |  |  | 1 | [7 empty] | 1 |  |  |  |  | make mention of change request | [9 empty] | request documented | More information required for a decision
624 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE f. Add attribute for the valve’s system type (system_type, alphanumeric) so that the valve can be located, queried, identified and isolated easily within any dataset. The QA values should relate to BULK, NETWORK, SERVICE (B, N, S) for starters. |  |  | Vol 1 |  |  |  | George/Haydn | Covered 2.1.7 and 2.1.8. 7/3/2017 | Included | Included | Covered 2.1.7 and 2.1.8. | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok | [12 empty] | No action
625 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE g. Add attribute value for the valve’s configuration (configuration, alphanumeric) within the network. The QA values should relate to INLINE, BYPASS, CROSS-CONNECTION (I, B, C) for starters. |  |  | Vol 1 |  |  |  | George/Haydn | 2017-03-07 | Included | Included | Reviewed and Noted for Inclusion | 2.5.3 Valve | 1 | [7 empty] | 1 |  |  |  |  | ok |  | make mention of change request | [9 empty] | request documented | New attribute & associated Code List proposed | Valve Configuration Valve Confiduration Type Inline Bypass Cross-connection
626 | Oliver Mander | Wellington Water | Potable water | Vol 1 | [6 empty] | Asset Class: Mechanical Asset - VALVE h. Add attribute for valve mechanism (mechanism, alphanumeric) to record the inner workings for the valve. A suggested code list for mechanism is outlined below. |  |  | Vol 1 |  |  |  | Noted | Can be provided as part of the operational instructions at hand over 3/7/2017 | Noted: no action required | Noted: no action required | Can be provided as part of the operational instructions at hand over 3/7/2017 | 2.5.3 Valve |  |  |  | 1 | [6 empty] | 1 | [15 empty] | No action