## Slide 1: RM Clayton Water Reclamation – Hydraulic Modelling in InfoWorks
Tom Scott, Felicity Bennett and Amanda Burns, P.E.

## Slide 2: Background
City of Atlanta wanted hydraulic model of RM Clayton wastewater plant
Already had a very complicated spreadsheet
InfoWorks ICM specified so could be integrated with upstream collection system model
Model built from scratch and then calibrated
240MGD (10.5m3/s) plant design flow
Notes: As part of a joint venture initiative to aid the City of Atlanta (the City) with energy and compliance upgrades, Black and Veatch (B&V), partnered with Gresham Smith and Rohadfox, was appointed to build and calibrate a model for the RM Clayton WRC in Atlanta, Georgia. The model was constructed in InfoWorks ICM and included all main liquid stream components from the influent collection through to the outfall. The City’s objective was to develop a suitable hydraulic profile model for the 240MGD RM Clayton WRC in order to incorporate this into their existing collection system model to ultimately have a single hydraulic model for the entire system.

## Slide 3: Why use ICM to model Treatment Plant Hydraulics?
Dynamic model vs. traditional static spreadsheets
  Flow splits and flooding automatically calculated
  Model routing
  Pump/gate/valve controls can be modeled
  Graphical interface and outputs
Third-party software
Opportunity for integrating with collection system model
  Model dynamic downstream conditions
  Examine WWTP operations effect on collection system
  Assess aging collection system infrastructure (more I/I) effects on WWTP operations
Notes: TP modeling is not new, traditionally done with a spreadsheet model through longest or “critical” path

## Slide 4: Model Overview
InfoWorks ICM version 5.5
Large works with typical treatment components:
  Headworks with coarse bar screens
  grit removal and drum screens
  8 x primary clarifiers
  2 x Biological Nutrient Removal
  (BNR) basins
  Mixed liquor pumping station
  10 x secondary clarifiers
  22 x effluent filters
  5 x Ultraviolet (UV)
  Outfall
Notes: The hydraulic model for RM Clayton WRC extends from the influent collection structure to the Chattahoochee River, including all the liquid stream process units. The model was constructed based on record drawings, a site survey, an existing Excel spreadsheet hydraulic model, and feedback from plant operations staff.
The process units included in the model were:
influent collection structure, headworks with bar screens, vortex grit collectors, multi-tray grit removal units, and drum screens,
(8) primary clarifiers,
(2) biological nutrient removal (BNR) process basins,
mixed liquor pumping station,
(10) secondary clarifiers,
(22) effluent filters,
ultraviolet (UV) disinfection system,
and outfall diffuser.
All process units were included, along with 6 bypasses. The Return Activated Sludge (RAS) system was also included in a simplified form since RAS is a significant proportion of the plant total flow.

## Slide 5: Model Overview
840 nodes and 1174 links
120 gates/sluices to enable individual units to be taken offline
6 bypasses
Existing Plant from inlet chamber to Chattahoochee River
Proposed new grit removal plant (isolated for calibration)
Different scenarios created:
  Base model – current arrangement with typical units in service
  Calibration (20 Feb – 26 Mar) – units in service at time
  Calibration (5 – 6 Apr) – units in service at time
  Other scenarios for simulating different number of UV lanes in service.

## Slide 6: Data Acquisition and Survey

## Slide 7: Data Acquisition and Survey
A detailed site survey was undertaken:
  To obtain dimensions which could not be obtained from record drawings
  To verify key hydraulic information, such as weir levels
  To obtain invert levels for temporary monitor locations to convert measured depths into elevations
Surveyed elevations showed a universal offset relative to site record drawings with surveyed elevations higher
Average difference of 120 mm determined by comparing elevations at a number of locations where levels were known from record drawings.

## Slide 8: Data Acquisition and Survey
During the survey we identified:
  If available control levels conformed to record drawings
  Field measurements for each process component and conveyance network
  Survey benchmarks for each process area
  Site visits to confirm the survey pin locations and coordinate with model development.
  Geo-reference of the plant layout into the hydraulic modelling software
  Equipment headloss curves, pump curves
  The existing Foxboro SCADA system recorded levels
  Portable ultrasonic level meters

## Slide 9: Model Build

## Slide 10: Headworks
Drum Screen
Head/Discharge Curve
Notes: The standard method used by ICM over-estimates the headloss of drowned weirs and although Villemonte’s equation for drowned sharp-crested weirs can be selected in the model simulation parameters, this can cause instability and still over-estimates the headloss of drowned broad crested weirs. The weir coefficients were set manually to obtain the same headloss as determined using P.A. Kolkman’s equations in Miller (1994). The same issue also occurs where sluices are operating as submerged weirs, with upstream water level below the top of the gate opening, and the sluice secondary discharge coefficients were manually increased.

## Slide 11: Primary Clarifiers
Primary Influent Channel
Clarifier Tank 8 Gate 35% Open
Launder Channel
Primary Bypass Gate
V-Notch Weir
Primary Effluent Channel
Flow Split and Clarifier Sluice Gates
Notes: Primary Clarifiers: Downstream of the headworks, flow passes to the primary clarifiers via a 12 ft. diameter tunnel. Here a screenshot of the primary clarifier area of the model. The flow split between the primary clarifiers is based on hydraulic similarity of inlet pipework and the clarifier weirs. Based on feedback from operations staff, the gate to clarifier 8 was set 35% open to prevent excessive solids load to this clarifier. The model indicates a good flow distribution between the clarifiers with each set of four clarifiers receiving 50% of flow at 122 mgd (average day, maximum month flow). The model also indicates an identical flow split between clarifiers 1 to 4 due to the identical inlet pipework. With the clarifier 8 gate 35% open, it predicts that this clarifier would receive 7% of flow, with clarifiers 5 to 7 each receiving 14% of 122 mgd. However, ICM does not take into account local 3 dimensional or momentum effects.
This required the V notch weirs on each clarifier to also be split into eight sections. It should be noted that even with this refinement, ICM cannot account for the energy required to accelerate incoming flow to a channel, so detailed spreadsheet backwater calculation was performed when determining the plant hydraulic capacity.
The primary clarifier bypass was included within the model. A proportion of the flow bypasses the clarifiers when the water level in the clarifier influent channel becomes too high to prevent hydraulic overloading of the clarifiers and site flooding. Automatic control of this gate was replicated using the Real Time Control (RTC) function within ICM, with the gate controlled to target a water depth of 9.5 ft. in the clarifier influent channel.

## Slide 12: Biological Nutrient Removal (BNR)
BNR2
BNR1
Plant Process Unit | No. of Units | Hydraulic Model Element Used
Basins | 190 | Links-Channels
Influent Effluent Channels | 130 | Links-Channels
Sluice Gates | 24 | Links-Sluice
Weirs | 42 | Links-Weir
Orifice | 62 | Links-Orifice
Notes: Biological Nutrient Removal (BNR) Basins: RM Clayton includes two BNR basins, with the flow distribution between the basins reliant on hydraulic similarity. Although the BNR trains both have similar effluent weir levels, the total weir lengths and tank inlet arrangements are not the same. Operations staff advised that BNR1 receives more flow than BNR2 and this was confirmed by the ICM model which showed 55% of flow to BNR1 at 122mgd with all trains in service.
There are gates present on the route to each BNR at the channel wye branch which could be used to amend the flow distribution but these are currently kept fully open. The gates are narrower than the adjacent channels and the discharge coefficient for these gates was amended to match the headloss predicted by Idel’chik (2003) for a thick edged orifice.
The model arrangement for BNR1 is shown in with key items labeled. Modeling of the RAS which enters each of the BNR trains is described later.
Individual trains are isolated using butterfly valves at the upstream end of each inlet pipe. ICM does not include a butterfly valve component and these were represented in the model by variable discharge orifices. The orifice discharge coefficient was set at 2.6 during calibration, which is equivalent to a headloss coefficient, K value of 0.3. It is important to note that the orifice discharge coefficients required in ICM are √2 greater than typical coefficients due to a difference in the equation used. Using variable discharge orifices enabled the limiting discharge to be set to zero using RTC to close individual trains and replicate changes which occurred during the calibration period.
The model arrangement for BNR2 is shown in Figure 7. Both BNR basins include step feed configurations which allow operations staff to divert flow around the first half of the mixing zone of each train. These facilities are not currently used but were included within the model to give that flexibility.
Both BNRs also include baffle walls on each train where flow can pass over a weir or through an opening at the bottom of the weir. These arrangements were modeled with a weir and orifice in parallel and the model automatically determines the flow split between the two. ICM uses dimensionless weir coefficients and these were all adjusted from the default value of 1.0 to 0.57 and 0.544 for thin plate and broad crested weirs respectively.

## Slide 13: Mixed Liquor Pumping Station
Mixed Liquor Pump
Head/Discharge Curve
Notes: Mixed Liquor Pumping Station: The model arrangement for the mixed liquor pumping station is shown in Figure 8. Flow from both BNRs passes through twin mixed liquor channels to the mixed liquor pumping station. The pumping station comprises six variable speed pumps split across two wet wells, which were modeled as Variable Frequency Drive Pumps (VFDPMPs).
Pump speed is automatically controlled in response to the wet well water level with an additional pump brought online if the pump speed is high and a pump stopped if the speed drops. However, in order to provide a simple means of pump control within the model, which would automatically adjust to a wide range of incoming flows, the number of operating pumps was fixed with all pumps controlled to the same speed. Incremental controllers were used in the RTC file to incrementally increase or decrease the pump speeds in response to the water level in wet well.
Slightly different pump curves were used for each pump using measured curves obtained from Operations Staff. Headlosses in the pump suction pipes, discharge manifold and along the length of the force mains were included, with the force mains modeled as pressure conduits.

## Slide 14: Secondary Clarifiers
Plant Process Unit | No. of Units | Hydraulic Model Element Used
Tanks | 10 | Nodes-Storage
Pipes | 36 | Links-Conduits
Weirs- RAS Removal | 92 | Links-Weir
Orifice | 10 | Links- Orifice
Launder Channels | 80 | Links-Conduits
Notes: Secondary Clarifiers: Flow is distributed between the ten secondary clarifiers via two splitter chambers. Each splitter chamber has five weir slide gates – one for each secondary clarifier. These gates are adjusted by plant operators in order to manage sludge blanket formation and were therefore modeled as variable crest weirs “VCWEIR”, so that their level can be easily amended and clarifiers isolated if required.
Following the same approach as the primary clarifiers, the secondary clarifier weirs and launder channels were split into eight sections on each tank. The model arrangement for the secondary clarifiers is shown here. The energy dissipating inlet within each secondary clarifier was modeled using a headloss versus discharge table, based on information from WesTech.

## Slide 15: Effluent filters
Filter Media
Head/Discharge Curve
Plant Process Unit | No. of Units | Hydraulic Model Element Used
Influent Effluent Channels | 140 | Links-Conduits
Weirs | 24 | Links-Weir
Sluice Gates | 22 | Links-Sluice
Filter Media | 22 | Links- User Control
Flumes | 21 | Links-Flume
Notes: Effluent Filters: The model arrangement for the effluent filters is shown in Figure 10. At the upstream end of the filters is an overflow chamber with overflow weirs on each side. Each weir was split into two sections to improve model accuracy in this region. At high water levels flow automatically bypasses the effluent filters, passing through two overflow conduits which join the filter outlet conduits.
Flow distribution between the effluent filters is achieved using a cutthroat flume on each filter inlet and an almost perfect flow distribution was estimated. The flumes were modeled using the in-built ICM flume component which is based on the British Standard (BS) flume. BS flumes have a rounded inlet rather than the tapered inlet provided but the effect on headloss is small. ICM uses a nominal headloss if the flume becomes submerged (downstream depth / upstream depth > 75%) but it was checked that this does not occur at RM Clayton even at high flows.
Each of the 22 effluent filters has two cells which are fed from a single inlet and connected by small holes in the dividing wall. The two cells were combined in the model to simplify the arrangement. All filters are normally in service, with the filters backwashed sequentially, with one backwash every 3 hours. To ensure the model was conservative, the base model setup included one of the downstream filters offline. The flume link for the offline filter was removed to enable automatic model initialization.
The headloss through the media in each effluent filter varies with flow rate, but also with the amount of time since the media was last backwashed. A clean media headloss versus flow curve was obtained from the media supplier, De Nora, and was included in the model as a user defined head discharge table. De Nora also confirmed that the terminal headloss for filters with this hydraulic loading rate was about 2 ft. To be conservative, a second user defined headloss table including this constant headloss was used for all filters when assessing the maximum hydraulic capacity of the plant.

## Slide 16: UV System
Trojan UV 400 Units
Head/Discharge Curve
Notes: UV System: The UV system consists of two influent boxes, a long weir feeding the UV common influent channel, and five UV channels. Flow from each channel flows over effluent weirs into the UV Clearwell before passing to the outfall. The model arrangement for the UV system is shown in Figure 11.
The headloss associated with the UV system lamps was modeled using a head versus discharge table based on information obtained from the manufacturer, Trojan Technologies. The fifth UV channel was included in the model but without any lamps in the base scenario and the UV bypass channel was also included.

## Slide 17: Outfall Diffuser
Venturi Flowmeters
Head/Discharge Curve
Plant Process Unit | No. of Units | Hydraulic Model Element Used
Outfall and Diffuser | 22 | Links-Conduits
Weirs | 6 | Links-Weir
Venturi Flow Meter | 2 | Links-User Control
Notes: Outfall: The model arrangement for the outfall is shown in Figure 12 with key items labeled. Flow from the UV system passes through two parallel venturi flowmeters which record the plant effluent flow. These were modeled with user defined head discharge table based on manufacturer’s data.
Flow then passes down a number of steps (modeled as weirs) in the plant effluent outfall structure before joining the original plant outfall. Next to the river, flow passes down a cascade aeration structure and into the effluent diffuser.
This diffuser was modeled in detail with each diffuser port connected to an outfall representing the Chattahoochee River. The river level was set via a separate level file so simulations could easily be performed for different river conditions.

## Slide 18: Adapting InfoWorks ICM for Treatment Plant Hydraulics
Notes: Default values in ICM are configured for network modeling

## Slide 19: Nodes & Links
Split links at each change of conduit dimension
Use user-defined shapes for unusual conduits
If surcharged conduits, model as “pressure conduit” or increase celerity ratio
  Increasing from 10 to 14.414 reduces Preissmann slot from 2% to 1% of conduit width
Actual conduit area
Conduit area used by model
Preissmann Slot
Notes: The primary clarifier influent channels downstream of the tunnel have a non-standard cross section and were entered into ICM as user-defined shapes as shown above. The model celerity ratio was increased to 14.414 to reduce the Preissmann slot to 1% of conduit width and reduce the impact of the slot on surcharged conduits.

## Slide 20: Circular Clarifier Tanks
ICM cannot simulate flow entering along the length of a channel from another model link
Divided launder length into sections to minimize inaccuracy but confirm launder capacity using spreadsheet backwater calculation
Series of V-notch weirs, each with equal number of notches
Notes: ICM cannot simulate flow entering along the length of a channel directly from another model link, so to minimize inaccuracy, the launder channels on each primary clarifier were split into eight sections.

## Slide 21: Nodes & Links
Headloss Coefficients
  Use “Fixed” not “Normal” headloss types
  Set headloss values manually based on K values for fittings
  Not variable
Set node areas accurately if routing to be modeled. Set to small area and “sealed” if no chamber in reality.
Notes: Default calculation for chamber/shaft area of nodes is based on width of largest incoming/outgoing pipe
Recommend setting “Fixed” as user-defined default for headloss type at start of project
Ku*Ks*Kv

## Slide 22: Head Discharge Tables
Head versus discharge tables for screens and filters. Enter number of tables if varies with e.g. d/s water depth and pick most appropriate one for each scenario

## Slide 23: Weirs – Discharge Coefficients
Two discharge coefficients:
  Discharge coefficient = weir coefficient
  Secondary discharge coefficient = orifice coefficient (water level above roof)
Coefficients are dimensionless with default = 0.85
Set discharge coefficient manually depending on type
  Thin plate = 0.57
  Broad crested = 0.544
Notes: Default discharge coefficient is 0.85

## Slide 24: Weirs – Discharge Coefficients
If weir is submerged, standard equation overestimates losses
Can select Villemonte’s equation in Simulation Parameters:
  Can be unstable
  Still overestimates losses for broad crested weirs
Alternative is to manually increase discharge coefficient
Don’t use built-in broad crested weir if have reverse flow or submergence
Notes: Default discharge coefficient is 0.85

## Slide 25: Sluice Gates – Discharge Coefficients
Three discharge coefficients, all with default of 1.0
Discharge coefficient = orifice coefficient (water level above top of gate)
Secondary discharge coefficient = weir coefficient (same issue with drowned weirs)
Overgate discharge coefficient = weir coefficient when overtopping. Only used if gate depth set
Notes: A limitation of the software is that headloss and discharge coefficients within the model cannot be adjusted during a simulation. Fixed values have to be entered for each model scenario. This was not a major problem for modeling RM Clayton, but would be significant if, for example, simulation of sluice operation was required since the required sluice discharge coefficient is a function of opening position.

## Slide 26: Sluice Gates – Discharge Coefficients
Set discharge coefficient manually based on area ratios
Use high coefficient (e.g. 10) if gate is only included to allow isolation and no headloss under normal conditions
NB ICM equation is different – typical Cd of 0.6 equates to 0.85 in ICM
Not variable

## Slide 27: Real Time Control in InfoWorks
Return activated sludge (RAS) included which automatically adjusted to 50% of incoming flow
Pumps controlled to maintain fixed sump water level
New grit plant units brought online/ offline in response to incoming flow, with delay timer and rapid flow increase over-ride
ICM can include complicated control although not intuitive and can only work sequentially
Globally defined variables for wet well target level, pump control and % of Return Activated Sludge (RAS)
Controls for the Mixed Liquor Pumping Station Variable Frequency Drive (VFD) Pumps
Controls for the variable discharge orifices at the Secondary Clarifiers and BNR Tanks
Controls for the Primary Clarifier Bypass
Notes: Real Time Control
The RTC function in ICM has been used extensively to simulate pump control, bypass gates and the automatic operation of a new multi-tray grit removal plant. RTC was also used, in combination with variable discharge orifices, to circulate RAS within the works, varying as a fixed percentage of plant inflow.
Sophisticated control can be replicated in ICM although the RTC can only work sequentially which prevents control based on information from previous timesteps or rolling averages. Incorporation of RTC within each model scenario also makes tuning of control laborious as models must be validated and committed before every simulation.

## Slide 28: Include Notes!

## Slide 29: Calibration

## Slide 30: Calibration
Very difficult to calibrate a whole model – too many hydraulic breaks
To maximise success:
  Check what data is already recorded and whether it is reliable, especially flows
  Make logging period dependent on seeing a high flow
  Ensure operators log units in service and any plant bypasses
  Pick locations carefully to maximise calibration lengths. Concentrate on most crucial areas, e.g. where headlosses are high, freeboards are low or grit deposition could be significant
  Ensure water levels, not depths are recorded. Water depth to invert is only of use if channel invert level is certain
  BEWARE OF DATUM DIFFERENCES. Suggest survey of key levels across plant and measure sediment depths at the same time
Notes: Calibration
Calibration of a treatment plant is difficult due to the large number of hydraulic breaks present. No existing level measurement and a limited number of portable instruments limited calibration to eight locations, however these were carefully chosen to maximize their benefit.
Very good agreement was achieved in most locations with very few modifications of the model required. Comparing the results graphically as well as numerically enabled constant offsets to be very easily distinguished from under/over-estimation of headlosses which are flow dependent.
The four week calibration period unfortunately did not include any high flow events and subsequent calibration of the RM Clayton headworks modifications was instead made dependent on high flows, rather than of a fixed time duration. The four week period did though enable calibration for different numbers of process units in service as events occurred and were logged by operations staff. RTC was used to open/close tanks in the model and replicate these real events.
A site survey was extremely beneficial in confirming key elevations across the plant, invert levels at the portable instrument locations and sediment depths present.

## Slide 31: Locations of existing SCADA and proposed level sensors
8 portable ultrasonic depth monitors installed from 20th/22nd Feb to 24th March 2017
Inlet flow
BNR2 total RAS
BNR1 individual RAS flows
Some pump speeds, pressures and flows
River level
Effluent flow
Water levels
Water level
Water levels
Water level
Water levels
Total mixed liquor flow
Existing SCADA Equipment
Proposed Level Sensor Equipment

## Slide 32: Calibration
Visual comparison of results extremely beneficial:
  Can see if there is a constant offset - probably datum difference;
  Or difference is flow dependent - headloss is over/under estimated
Quantify calibration by comparing average, min and max depths. Min and max must use the same event for measured and simulated results
Notes: Very few model changes required to achieve calibration

## Slide 33: Calibration
Can gain useful information even if a monitor is in the ‘wrong’ location
Sand filter levels varies with backwashing so normal calibration is not possible but:
  Minimum level when filter clean enables calibration of downstream headlosses
  Maximum level enables calibration of dirt loss assumed

## Slide 34: Plant Hydraulic Capacity
Notes: Model Long section at 220mgd
Plant Hydraulic Capacity
Following calibration, the hydraulic model was used to estimate the hydraulic capacity of each process area of the plant in order to assist the City of Atlanta in planning future expansion of the WRC. Each area of the plant was simulated individually, with the hydraulic capacity determined as the flow at which submergence of weirs or flooding would start to occur.
Due to low rainfall throughout the four week calibration period, the model was calibrated against flows of only 50-130 mgd. Surcharged headlosses increase in proportion to velocity squared so any additional losses from e.g. sediment deposition not observed during the site survey, could have a large effect on the maximum capacity. The hydraulic capacities calculated therefore generally represent ideal conditions with clean conduits and most units in service

## Slide 35: Plant Hydraulic Capacity

## Slide 36: Summary

## Slide 37: SUMMARY
The observed data was used to calibrate the hydraulic model at each stage of the treatment plant.
A good correlation between observed data and model simulation was obtained with only minor model changes required.
The WRC dynamic model development is complete and is currently being used and will be linked to the three sewer collection Basins.
The model can also be used to plan future expansion projects.
ICM is a good tool if a whole plant hydraulic model is required, but must be carefully adapted for accurate results
Notes: CONCLUSIONS
InfoWorks ICM has been used to produce a detailed hydraulic model of RM Clayton WRC. The model is significantly more flexible and dynamic than the previous spreadsheet model of the plant and will be integrated with the City of Atlanta’s existing catchment system model.
Accurate modeling and good agreement with measured data was achieved with careful choice of model components and setting of model coefficients. The model was then used to determine the hydraulic capacity of each area of the plant to assist with planning of future work.

## Slide 38: SUMMARY
Having the WRC hydraulic model in the same software as the sewer collection system provides ease of combining all systems into one integrated model.
The WRC model when used with the collection system helps control the end discharge conditions, especially during wet weather events. This will identify the extent of backwater conditions and resulting spills.
The model will assist in providing flow data for chemical and biological process simulations for different flow scenarios.
ICM is a good tool if a whole plant hydraulic model is required, but must be carefully adapted for accurate results

## Slide 39: Tom Scott
+64 9-300-9187
scottt@bv.com
+44 1737 856427
bennettf@bv.com
Felicity Bennett
+1 312-346-2979
burnsam@bv.com
Amanda Burns