## Questionaire
Open this document in Microsoft Excel or equivalent for instructions and limitations to show correctly.
|  |  |  | System | Score
Select client: |  |  |  | Gravity sewer | 195
Client 1 |  |  |  | Pressure sewer | 145
|  |  |  | Vacuum sewer | 260
Question |  |  |  | Answer |  |  | Assigned score if yes
ID | Category | Description |  | Yes / No |  |  | GS | PS | VS
1 | Construction and design | Does the proposed asset owner have experience with pressure systems? |  | Yes |  |  | 10 | 0 | 10
2 | Construction and design | Does the proposed asset owner have experience with vacuum systems? |  | No |  |  | 10 | 10 | 0
3 | General | Can the development be serviced by a gravity sewer with pipes no deeper than 4m and connect to an existing gravity manhole? |  | no |  |  | 0 | 90 | 90
4 | General | Same as above, but with just one pump/lift station? |  | No |  |  | 0 | 70 | 70
5 | General | Same as above, but with just two pump/lift stations? |  | Yes |  |  | 0 | 50 | 50
6 | General | Same as above, but with less than one pump/lift station every 500 (?) houses? | Skip |  |  |  | 0 | 30 | 30
7 | General | Was the previous answer "No"? | Skip |  |  |  | 80 | 0 | 0
8 | Geotech | Is there a high water table? |  | Yes |  |  | 30 | 0 | 0
9 | Geotech | Are there rocky soils or poor ground condition? |  | yes |  |  | 30 | 0 | 30
10 | Topography | Is terrain topography steep and flow generally downhill to existing sewer network? |  | No |  |  | 0 | 50 | 25
11 | Topography | Is terrain topography steep and flow generally uphill to existing sewer network? |  | no |  |  | 50 | 0 | 15
12 | Topography | Is terrain topography steep and undulating? |  | no |  |  | 30 | 0 | 15
13 | Topography | Is terrain topography moderate and flow generally downhill to existing sewer network? |  | no |  |  | 30 | 0 | 15
14 | Topography | Is terrain topography moderate and flow generally uphill to existing sewer network? |  | no |  |  | 30 | 0 | 15
15 | Topography | Is terrain topography moderate and undulating? |  | yes |  |  | 30 | 0 | 15
16 | Topography | Is terrain topography mild/flat? | Skip |  |  |  | 30 | 0 | 0
17 | Topography | Is terrain topography mild/flat and undulating? | Skip |  |  |  | 30 | 0 | 0
18 | Topography | Is the road reserve generally at a higher elevation than the properties? |  | No |  |  | 50 | 0 | 30
19 | Development | Is this project at an area currently served by septic tanks? |  | yes |  |  | 25 | 10 | 15
20 | Development | Is this a bronwfield project? | Skip |  |  |  | 50 | 0 | 0
21 | Development | Is development large (> 2000 properties)? |  |  |  |  | 0 | 20 | 15
22 | Development | Is development medium sized (500 - 2000 properties)? |  |  |  |  | 0 | 15 | 0
23 | Development | Is development small sized (150 - 500 properties)? |  | no |  |  | 0 | 0 | 15
24 | Development | Is development minor (< 150 properties)? |  | yes |  |  | 0 | 0 | 30
25 | Development | Is development area elongated/extended? |  | no |  |  | 30 | 0 | 0
26 | Development | Is development area compact/centered? |  | yes |  |  | 0 | 5 | 15
27 | Population density | Is development density high (> 15 properties/ha)? |  | yes |  |  | 0 | 5 | 15
28 | Population density | Is development density medium (4 - 15 properties/ha)? | Skip |  |  |  | 15 | 0 | 0
29 | Population density | Is development density low (< 4 properties/ha)? | Skip |  |  |  | 30 | 0 | 15
30 | Risks and safety | If a Safety in Design (SiD) risk register been performed: Does the gravity sewer system have significant risks above the other systems? |  | Yes |  |  | 50 | 0 | 0
31 | Risks and safety | Does the pressure sewer system have significant risks above the other systems? | Skip |  |  |  | 0 | 30 | 0
32 | Risks and safety | Does the vacuum sewer system have significant risks above the other systems? | Skip |  |  |  | 0 | 0 | 30
33 | Risks and safety | Are power outages above 6 hours anticipated? |  | No |  |  | 0 | 15 | 5
34 | Risks and safety | Is terrain prone to flooding or other sources of high inflow and infiltration? |  | No |  |  | 40 | 0 | 0
35 | Risks and safety | Is the area prone to earthquakes? |  | No |  |  | 50 | 0 | 10
36 | Risks and safety | Is there a possibility of liquefaction during an earthquake? |  | No |  |  | 50 | 0 | 10
37 | Risks and safety | Is there a special restriction (stricter than normal) to environmental contamination from damaged pipes and/or overflows? |  | no |  |  | 50 | 15 | 0
38 | Construction and design | Is construction time importantly restricted? (shorter than average times for construction of a gravity system) |  | no |  |  | 25 | 0 | 0
39 | Construction and design | Will there be future expansion of the system? Will system be operating in different stages? Is catchment subject to seasonal flows? (e.g. mainly vacation homes) Are expected flows lower than average? (e.g. areas with restricted water supply) Answer "Yes" if any of the above applies. |  | yes |  |  | 0 | 30 | 25
40 | Construction and design | Is there limited availability of specialised contractors? (question aimed at vacuum and pressure sewers) |  | yes |  |  | 0 | 25 | 15
41 | Infrastructure | Is capacity of downstream infrastructure (pump stations or treatment plants) close to its limit (currently or with expected flows)? |  | No |  |  | 40 | 0 | 15
42 | Infrastructure | Is the proposed system adjacent to an existing gravity sewer network? |  | Yes |  |  | 0 | 20 | 20
43 | Infrastructure | Is the proposed system adjacent to an existing pressure sewer network? | Skip | no |  |  | 20 | 0 | 20
44 | Infrastructure | Is the new system going to be connected to a downstream existing vacuum sewer network? | Skip | No |  |  | 20 | 20 | 0
45 | Infrastructure | Was the previous answer "No"? | Skip |  |  |  | 0 | 0 | 0
46 | Infrastructure | If pressure system is a viable option, would the water agency take ownership and O&M responsibilities of infrastructure on private properties? |  | Yes |  |  | 20 | 0 | 20
47 | Infrastructure | If pressure system is a viable option, would the customers take ownership and O&M responsibilities of infrastructure on their properties? | Skip | No |  |  | 10 | 0 | 10
48 | Costs | If a NPV analysis has been undertaken: Does the gravity sewer system offer the lowest NPV? |  |  |  |  | 0 | 30 | 30
49 | Costs | Does the pressure sewer system offer the lowest NPV? |  |  |  |  | 30 | 0 | 30
50 | Costs | Does the vacuum sewer system offer the lowest NPV? |  |  |  |  | 30 | 30 | 0
51 | Costs | Average Annual Cost (Totex over the full life of asset, concrete 100 years- PVC 50 years) |  |  |  |  | 0 | 0 | 0
52 | [6 empty] | 0 | 0 | 0
53 | [6 empty] | 0 | 0 | 0
54 | [6 empty] | 0 | 0 | 0
55 | [6 empty] | 0 | 0 | 0
56 | [6 empty] | 0 | 0 | 0
57 | [6 empty] | 0 | 0 | 0
58 | [6 empty] | 0 | 0 | 0
59 | [6 empty] | 0 | 0 | 0
60 | [6 empty] | 0 | 0 | 0
61 | [6 empty] | 0 | 0 | 0
62 | [6 empty] | 0 | 0 | 0
63 | [6 empty] | 0 | 0 | 0
64 | [6 empty] | 0 | 0 | 0
65 | [6 empty] | 0 | 0 | 0
66 | [6 empty] | 0 | 0 | 0
67 | [6 empty] | 0 | 0 | 0
68 | [6 empty] | 0 | 0 | 0
69 | [6 empty] | 0 | 0 | 0
70 | [6 empty] | 0 | 0 | 0
71 | [6 empty] | 0 | 0 | 0
72 | [6 empty] | 0 | 0 | 0
73 | [6 empty] | 0 | 0 | 0
74 | [6 empty] | 0 | 0 | 0
75 | [6 empty] | 0 | 0 | 0
76 | [6 empty] | 0 | 0 | 0
77 | [6 empty] | 0 | 0 | 0
78 | [6 empty] | 0 | 0 | 0
79 | [6 empty] | 0 | 0 | 0
80 | [6 empty] | 0 | 0 | 0
81 | [6 empty] | 0 | 0 | 0
82 | [6 empty] | 0 | 0 | 0
83 | [6 empty] | 0 | 0 | 0
84 | [6 empty] | 0 | 0 | 0
85 | [6 empty] | 0 | 0 | 0
86 | [6 empty] | 0 | 0 | 0
87 | [6 empty] | 0 | 0 | 0
88 | [6 empty] | 0 | 0 | 0
89 | [6 empty] | 0 | 0 | 0
90 | [6 empty] | 0 | 0 | 0
91 | [6 empty] | 0 | 0 | 0
92 | [6 empty] | 0 | 0 | 0
93 | [6 empty] | 0 | 0 | 0
94 | [6 empty] | 0 | 0 | 0
95 | [6 empty] | 0 | 0 | 0
96 | [6 empty] | 0 | 0 | 0
97 | [6 empty] | 0 | 0 | 0
98 | [6 empty] | 0 | 0 | 0
99 | [6 empty] | 0 | 0 | 0
Testing alternative total score system
[6 empty] | System | Scores
[7 empty] | Sum of "yes" scores | Avg of "yes" scores
[6 empty] | Gravity sewer | 195 | 13.9286
[6 empty] | Pressure sewer | 145 | 10.3571
[6 empty] | Vacuum sewer | 260 | 18.5714
Instructions:
1. Select client from drop-down list on the left
2. Make sure all answer fields are blank before starting
3. Start answering from the top. If unsure or question does not apply, simply skip
Some questions are mutually exclusive and will automatically indicate that they should be skipped (make sure answer field is clear before continuing)
4. The scores for each system will be shown on the right (lowest score indicates preferred system)
Do not modify any other cell in this sheet. To add or modify questions, clients and individual scores, use next sheet.
Current limitations:
See "Questions and scores" sheet
- Still pending to see if it's better to add or average scores. Table on the left is the sum. At the bottom of the grouped columns (make sure to expand them) is a table comparing sum, average (including 0 values). Average without 0 values does not offer good comparison.
- Another idea could be to consider an initial starting score for pressure and vacuum
Lower score is better.
Values not comparable between different analyses.

## Questions and scores
10
|  | Questions | [5 empty] | General score comparison |  |  | Assigned score if reply is 'yes' | [17 empty] | /\ Grouped columns /\
|  | ID | Description | Category | Restriction 1 (mutually exclusive questions) | Restriction 2 (saved for later) | Restriction 3 (saved for later) | worst ≤ bad < ok < good ≤ excellent |  |  | Client 1 |  |  | Client 2 |  |  | Client 3 |  |  | Client 4 |  |  | Client 5 |  |  | Client 6 |  |  | Analysis for scoring comparison
Clients | [7 empty] | Gravity sewer (GS) | Pressure sewer (PS) | Vacuum sewer (VS) | 1 |  |  | 2 |  |  | 3 |  |  | 4 |  |  | 5 |  |  | 6
1 | Client 1 | [9 empty] | GS | PS | VS | GS | PS | VS | GS | PS | VS | GS | PS | VS | GS | PS | VS | GS | PS | VS
2 | Client 2 | 1 | Does the proposed asset owner have experience with pressure systems? | Construction and design |  |  |  | ok | good | ok | 10 | 0 | 10 | [15 empty] | Slight bonus to PS if yes. No experience considers it can be done but with more external support.
3 | Client 3 | 2 | Does the proposed asset owner have experience with vacuum systems? | Construction and design |  |  |  | ok | ok | good | 10 | 10 | 0 | [15 empty] | Slight bonus to VS if yes. No experience considers it can be done but with more external support.
4 | Client 4 | 3 | Can the development be serviced by a gravity sewer with pipes no deeper than 4m and connect to an existing gravity manhole? | General | 1 |  |  | excellent | worst | worst | 0 | 90 | 90 | 1 | 2 | 3
5 | Client 5 | 4 | Same as above, but with just one pump/lift station? | General | 1 |  |  | excellent | worst | worst | 0 | 70 | 70 |  |  |  | 4 | 5 | 6
6 | Client 6 | 5 | Same as above, but with just two pump/lift stations? | General | 1 |  |  | good | bad | bad | 0 | 50 | 50 | [6 empty] | 7 | 8 | 9
|  | 6 | Same as above, but with less than one pump/lift station every 500 (?) houses? | General | 1 |  |  | good | bad | bad | 0 | 30 | 30 | [9 empty] | 10 | 11 | 12
|  | 7 | Was the previous answer "No"? | General | 1 |  |  | worst | excellent | excellent | 80 | 0 | 0 | [12 empty] | 13 | 14 | 15
|  | 8 | Is there a high water table? | Geotech |  |  |  | bad | good | good | 30 | 0 | 0 | [15 empty] | LPS and VS can be laid closer to the surface, so not affected by it.
|  | 9 | Are there rocky soils or poor ground condition? | Geotech |  |  |  | bad | good | good | 30 | 0 | 0 | [15 empty] | LPS and VS can be laid closer to the surface, so not affected by it.
|  | 10 | Is terrain topography steep and flow generally downhill to existing sewer network? | Topography | 2 |  |  | excellent | worst | bad | 0 | 50 | 25 | [15 empty] | Ideal solution for GS. No sense in using PS for this and probably not VS.
|  | 11 | Is terrain topography steep and flow generally uphill to existing sewer network? | Topography | 2 |  |  | worst | excellent | bad | 50 | 0 | 25 | [15 empty] | Ideal solution for PS. Worst for GS (implies many pump stations). VS not good for high elevation difference.
|  | 12 | Is terrain topography steep and undulating? | Topography | 2 |  |  | bad | good | ok | 30 | 0 | 15 | [15 empty] | GS could mean some pump stations, but not as many. PS best solution. VS could work
|  | 13 | Is terrain topography moderate and flow generally downhill to existing sewer network? | Topography | 2 |  |  | excellent | ok | ok | 0 | 15 | 15 | [15 empty] | Still ideal for GS. Can work for PS and VS.
|  | 14 | Is terrain topography moderate and flow generally uphill to existing sewer network? | Topography | 2 |  |  | bad | good | ok | 30 | 0 | 15 | [15 empty] | Bad for GS (some pump stations). Still great for PS and probably good for VS.
|  | 15 | Is terrain topography moderate and undulating? | Topography | 2 |  |  | bad | good | ok | 30 | 0 | 15 | [15 empty] | Still bad for GS, but better than steep for PS and VS.
|  | 16 | Is terrain topography mild/flat? | Topography | 2 |  |  | bad | good | good | 30 | 0 | 0 | [15 empty] | Bad for GS due to probably deep sewers. Best for PS and VS.
|  | 17 | Is terrain topography mild/flat and undulating? | Topography | 2 |  |  | bad | good | good | 30 | 0 | 0 | [15 empty] | Bad for GS due to probably deep sewers and/or pump stations. Best for PS and VS.
|  | 18 | Is the road reserve generally at a higher elevation than the properties? | Topography |  |  |  | worst | excellent | bad | 50 | 0 | 30 | [15 empty] | Very deep sewers for GS, no problem at all for PS. It's bad for VS only in the sense that it would require for the collection chamber to be located in the property.
|  | 19 | Is this project at an area currently served by septic tanks? | Development | 8 |  |  | ok | good | ok | 15 | 10 | 15 | [15 empty] | Based on the Ownership Policy report, clients that used to be served by septic tanks are more receptive to a pressure sewer system (they're used to take care of their systems and spend money on them).
|  | 20 | Is this a bronwfield project? | Development | 8 |  |  | ok | excellent | excellent | 50 | 0 | 0 | [15 empty] | Difficulties with other services or interferences/obstacles. Easier to avoid with pressure and vacuum. If no (Aka greenflied), no particular advantages of one over the other.
|  | 21 | Is development large (> 2000 properties)? | Development | 3 |  |  | good | bad | good | 0 | 30 | 0
|  | 22 | Is development medium sized (500 - 2000 properties)? | Development | 3 |  |  | good | ok | good | 0 | 15 | 0
|  | 23 | Is development small sized (150 - 500 properties)? | Development | 3 |  |  | good | good | ok | 0 | 0 | 15
|  | 24 | Is development minor (< 150 properties)? | Development | 3 |  |  | good | good | bad | 0 | 0 | 30
|  | 25 | Is development area elongated/extended? | Development | 4 |  |  | bad | good | good | 30 | 0 | 0 | [15 empty] | If dev has long stretches f houses in specific directions, requiring long sewers to reach further houses.
|  | 26 | Is development area compact/centered? | Development | 4 |  |  | excellent | good | good | 0 | 15 | 15 | [15 empty] | Development grows close to a central location, with furthest properties at similar distance from center.
|  | 27 | Is development density high (> 15 properties/ha)? | Population density | 5 |  |  | good | ok | good | 0 | 15 | 0 | [15 empty] | Associated with above questions. Distance between properties, length of pipes, etc
|  | 28 | Is development density medium (4 - 15 properties/ha)? | Population density | 5 |  |  | ok | good | good | 15 | 0 | 0
|  | 29 | Is development density low (< 4 properties/ha)? | Population density | 5 |  |  | bad | good | ok | 30 | 0 | 15
|  | 30 | If a Safety in Design (SiD) risk register been performed: Does the gravity sewer system have significant risks above the other systems? | Risks and safety | 10 |  |  | worst | ok | ok | 30 | 0 | 0
|  | 31 | Does the pressure sewer system have significant risks above the other systems? | Risks and safety | 10 |  |  | ok | worst | ok | 0 | 30 | 0
|  | 32 | Does the vacuum sewer system have significant risks above the other systems? | Risks and safety | 10 |  |  | ok | ok | worst | 0 | 0 | 30
|  | 33 | Are power outages above 6 hours anticipated? | Risks and safety |  |  |  | good | ok | good | 0 | 15 | 0 | [15 empty] | PS means shutdown at each pump, start using storage. VS only at station, but can operate with generators. GS could be issue if there are multiple pump stations and they don't all have generators
|  | 34 | Is terrain prone to flooding or other sources of high inflow and infiltration? | Risks and safety |  |  |  | bad | excellent | excellent | 40 | 0 | 0 | [15 empty] | Flooding can cause lots of I/I in GS and outflows in MH.
|  | 35 | Is the area prone to earthquakes? | Risks and safety |  |  |  | good | ok | good | 0 | 15 | 0
|  | 36 | Is there a possibility of liquefaction during an earthquake? | Risks and safety |  |  |  | bad | bad | ok | 15 | 15 | 0 | [15 empty] | If rigid pipes, they could break or separate at connections. Could generate lower points for GS. VS could change slopes or lifts a bit, but nothing serious probably.
|  | 37 | Is there a special restriction (stricter than normal) to environmental contamination from damaged pipes and/or overflows? | Risks and safety |  |  |  | worst | bad | good | 40 | 20 | 0 | [15 empty] | Score associated on how quickly and how much damage a ruptured pipe can do. GS goes unnoticed, PS is at pressure so forces exfiltration and takes a bit of time to notice. VS no exfil and noticed immediately.
|  | 38 | Is construction time importantly restricted? (shorter than average times for construction of a gravity system) | Construction and design |  |  |  | bad | good | good | 25 | 0 | 0 | [15 empty] | GS take longer than VS and PS (more machinery, deeper trenches, etc). Scoring in comparison to a GS system.
|  | 39 | Will there be future expansion of the system? Will system be operating in different stages? Is catchment subject to seasonal flows? (e.g. mainly vacation homes) Are expected flows lower than average? (e.g. areas with restricted water supply) Answer "Yes" if any of the above applies. | Construction and design |  |  |  | ok | ok | excellent | 25 | 30 | 0 | [15 empty] | More infill reduces capacity of GS. VS has higher capacity to increase flows, replace equipment at station only. PS limited as due to self cleansing velocities. VS has no problem leaving room for future expansion (this is asked in question related to staging. merge. Self cleansing velocities are an issue in GS and PS.
|  | 40 | Is there limited availability of specialised contractors? (question aimed at vacuum and pressure sewers) | Construction and design |  |  |  | good | bad | bad | 0 | 25 | 25 | [15 empty] | VS and LPS require stricter construction tolerances
|  | 41 | Is capacity of downstream infrastructure (pump stations or treatment plants) close to its limit (currently or with expected flows)? | Infrastructure |  |  |  | bad | excellent | ok/good | 40 | 0 | 15 | [15 empty] | PS and VS offer very little I/I, reducing demand from infrastructure down the line. Different from question 28. This also considers that PS can atenuate flow by controlling pumping hours (pump at low demand times).
|  | 42 | Is the proposed system adjacent to an existing gravity sewer network? | Infrastructure | 6 |  |  | excellent | ok | bad | 0 | 20 | 45 | [15 empty] | Can be considered as staging, so same sewer system is always the best option. VS worst because requires vac station anyways.
|  | 43 | Is the proposed system adjacent to an existing pressure sewer network? | Infrastructure | 6 |  |  | bad | good | bad | 20 | 0 | 20 | [15 empty] | bad to GS due to high flows at one location/constant operation of pump.
|  | 44 | Is the new system going to be connected to a downstream existing vacuum sewer network? | Infrastructure | 6 |  |  | ok | ok | excellent | 20 | 20 | 0 | [15 empty] | VS might not require additional vac station, but just replace some equipment. Other systems are ok as long as they're not large flows.
|  | 45 | Was the previous answer "No"? | Infrastructure | 6 |  |  | ok | ok | ok | 0 | 0 | 0 | [15 empty] | If it's not going to be connected to other system, no scoring added. Note that system expansion is in another question.
|  | 46 | If pressure system is a viable option, would the water agency take ownership and O&M responsibilities of infrastructure on private properties? | Infrastructure | 7 |  |  | bad* | excellent | bad* | 20 | 0 | 20 | [15 empty] | Good: Centralised telemetry (better information and control of the whole system like peak attenuation), reduced cost to owners (they pay only electricity). Bad: Requires agency to access properties for inspection and maintenance, all maintenance costs are taken by agency. Score is based on comparison between agency and private ownership (this and following question)
|  | 47 | If pressure system is a viable option, would the customers take ownership and O&M responsibilities of infrastructure on their properties? | Infrastructure | 7 |  |  | bad* | ok | bad* | 10 | 0 | 10 | [15 empty] | Bad: Difficulties to implement a centralised control and monitor system. Longer reaction times (owner detects problems, contacts entity responsible for maintenance, information arrives later to water agency), cost transferred to owners (installation and O&M)
|  | 48 | If a NPV analysis has been undertaken: Does the gravity sewer system offer the lowest NPV? | Costs | 9 |  |  | excellent | ok | ok | 0 | 30 | 30 | [15 empty] | Bonus score for cheapest system.
|  | 49 | Does the pressure sewer system offer the lowest NPV? | Costs | 9 |  |  | ok | excellent | ok | 30 | 0 | 30 | [15 empty] | Bonus score for cheapest system.
|  | 50 | Does the vacuum sewer system offer the lowest NPV? | Costs | 9 |  |  | ok | ok | excellent | 30 | 30 | 0 | [15 empty] | Bonus score for cheapest system.
|  | 51 | Average Annual Cost (totex over the full life of asset, concrete 100 years- PVC 50 years) | Costs
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
Current limitations:
- There are questions in different sections that should probably give a different score if both are "yes". (i.e. combination score of them should be different than the sum of their individual scores). Not a serious problem, but left as future improvement (temporarily managed by reducing scores).
- Answers have to be cleared manually between each run. VBA button will be added to clear with one click.
- If adding more clients than the current 6: Add clients in list above this box, cell B4 in Questionaire sheet needs data validation to expand to new clients, new columns need to be added to this sheet and referenced to list above this box. In the future, VBA button can add clients and modify everything else automatically.
- Questions are added below (up to 99). Adding rows in between generates issues in the previous spreadsheet.
- Should be improved to make it easier to organize the questions by section. (maybe a sort button?). Still, some questions have priority over others and should be considered when sorting (maybe use one support column define these?). If sorting, questions with the same restriction 1 should be kept intogether and in the same order as their currently are.
- Only modify light cream coloured cells
- There are two grouped columns (expand by clicking the + above)
- When adding questions, use available rows below
- Do NOT insert additonal rows (safeguards for this have not yet been implemented). Columns can be added except in between score columns
Note on H11: Cristian Jara: Check value

## Support (hidden)
Support spreadsheet (do not move or modify contents)
To be hidden later
Reply to questions | Yes
No