## Slide 1: CHRISTCHURCH FLUORIDATION: IMPLEMENTATION PLANNING FOR A 40+ FACILITY SYSTEM
Jack Deeley Jacobs
Michele McDonald Christchurch City Council
Silvia Vlad Jacobs

## Slide 2: Agenda
CCC Water Supply Background
Project Approach
Phase 1
Phase 2
CCC Current Position
Notes: What this presentation is about, what it’s not about

## Slide 3
  Site constraints
  Public proximity
  Flow variability
  Permanent structures
  Water quality
  Control systems
CCC WATER SUPPLY BACKGROUND

## Slide 4
390,000 people
100% from deep confined aquifers
Not treated
CCC WATER SUPPLY BACKGROUND
Notes: Michele to deliver introduction

## Slide 5
CCC WATER SUPPLY BACKGROUND
Chart: Pump Station capacity in m3/hr
| 2.0408163265306121E-2 | 4.0816326530612242E-2 | 6.1224489795918366E-2 | 8.1632653061224483E-2 | 0.10204081632653061 | 0.12244897959183673 | 0.14285714285714285 | 0.16326530612244897 | 0.18367346938775511 | 0.20408163265306123 | 0.22448979591836735 | 0.24489795918367346 | 0.26530612244897961 | 0.2857142857142857 | 0.30612244897959184 | 0.32653061224489793 | 0.34693877551020408 | 0.36734693877551022 | 0.38775510204081631 | 0.40816326530612246 | 0.42857142857142855 | 0.44897959183673469 | 0.46938775510204084 | 0.48979591836734693 | 0.51020408163265307 | 0.53061224489795922 | 0.55102040816326525 | 0.5714285714285714 | 0.59183673469387754 | 0.61224489795918369 | 0.63265306122448983 | 0.65306122448979587 | 0.67346938775510201 | 0.69387755102040816 | 0.7142857142857143 | 0.73469387755102045 | 0.75510204081632648 | 0.77551020408163263 | 0.79591836734693877 | 0.81632653061224492 | 0.83673469387755106 | 0.8571428571428571 | 0.87755102040816324 | 0.89795918367346939 | 0.91836734693877553 | 0.93877551020408168 | 0.95918367346938771 | 0.97959183673469385 | 1
Type a: Submersible | 108 | 120 | 137 | 180 | 252 | 350 | 356 | 374 | 425 | 449 | 512 | 845 | 918.5568
Type b: Artesian | 225 | 241 | 280 | 285 | 321 | 345.625 | 352 | 440 | 500 | 511
Type c: Combination wells only | 380 | 551 | 557.6776
Type d: Suction Tanks | 246 | 275 | 277 | 280 | 300 | 350 | 430 | 450 | 450 | 455 | 470 | 485 | 528 | 545 | 551 | 580 | 580 | 666.6667 | 768 | 900 | 1000 | 1149.984 | 1320
Notes: 49 pumping stations
Dispersed, decentralized supply
49 pump stations
Varied configurations
108 –1,320 m3/hr

## Slide 6: PROJECT APPROACH
- 6 week program
- Preliminary Implementation Cost
- Assume HFA
- Facility Categorization
- Network level
- Constraint Mark-up
- Longer program
- Chemical comparison
- Concept designs
- Reference facilities
- Validation of assumptions
- Initial Cost Estimate
- Initial assumptions provided for Phase 1
Phase 1
Baseline Estimate 2017
Phase 2
Notes: An initial baseline cost estimate was completed in 2017
Following guidance, Jacobs were approached
The timeline 6 weeks
Split – Phase 1 and phase 2
Phase 1 complete in 6 weeks.
Short timeline. Key assumptions from 2017
A factorial approach to the Phase 1 costing allowed the system to be analysed on a network wide level as opposed to specific facilities. As chch water network..
Costing achieved by categorizing
Mark-ups were applied to capture high level constraints. Constraints will increase costs
Once phase 1 complete, phase 2 was used to validate the assumptions
5 reference facilities
Concept Designs
Estimated capital and operating costs
At this stage we were also able to step back and consider other options.
Chemical comparison

## Slide 7: PHASE 1 Starting point
Standardised design
HFA fluoridation
Target dose 0.9 mg/L
3 facility size categories:
  11 “small” facilities
  (< 300 m3/hr)
  26 “medium” facilities
  (< 600 m3/hr)
  8 “large” facilities
  (< 1400 m3/hr)
Notes: The basis for phase 1 was established to confirm the required assumptions and design requirements to be achieved
The key result to take forward into both phases was the concept of standardised design.
As over 40 facilities are being maintained, it was important that any personnel could interact the same way across the district and not switch between chemicals, equipment or instrumentation.
Chemical assumed for Phase 1 was HFA
The factorial costing approach was performed by categorizing the numerous sites into small, medium and large based on capacity
Although the majority were medium facilities, there were a large proportion in both small and large meaning all would need to be considered to gather a respective estimate.

## Slide 8: PHASE 1 All in the inputs
Estimate components
Civil
Civil
Process Equipment
Structural
Mark-ups & Non-Construction Costs
Building Services
I&C
Electrical
Permitting & consents
Engineering
Expanded detail from baseline estimate
Contingency
SCADA upgrades
Training
Documentation updates
Mob/demob, overhead, profit, risk
Notes: Multi-disciplinary project with many inputs. Highlight not just process equipment
The Phase 1 capital estimate considered key areas but also the non-construction costs which were overlooked in previous estimates.
The key non-construction costs that were expanded further in our preliminary cost estimate included.

## Slide 9
HIGH SITE CONSTRAINTS
  MEDIUM SITE CONSTRAINTS
PHASE 1 No space at CCC sites
Notes: To account for site constraints in the parametric costing approach, a high level assessment denoted a reasonable mark-up of construction costs to be applied.
Mark-ups were generally civil related such as trenching distance, overall building expansion complexity, delivery constrained, distance to wastewater connection and any tree removal anticipated.
There was a substantial variation among the facilities. Some larger facilities, some small, some in a public park
For example, estuary pump station little space for site expansion, tight accessways – would have to reverse out onto busy road – not preferred
Grassmere – tight but space for some additional buildings as shown
Both sites will be tight construction wise and the close proximity to neighbours, increases construction complexity.
Illustrate different PS sizes and complexities
Notice the houses right next door, lack of space for additional buildings
Estuary Pump Station
  Very little space for site expansion as new building is required for fluoridation equipment
  Construction complexity increases in small area
  Tight accessways on site already
Grassmere Pump Station
  Tight space for building expansion
  Thin site for construction increasing complexity

## Slide 10: PHASE 1 What has changed since 2017
Severe site constraints
Public proximity
Lack of permanent structures to house equipment
Internal procedures
 | Baseline Cost Estimate 2017* | CCC Fluoridation 2022
Total Capital Estimate | 20.1 M | 58.1 M
Capital Estimate per Site | 0.34 M | 1.29 M
Operating Estimate | 0.91 M | 1.8 M
* 2017-dollar value without adjustment |  | 
Control systems upgrades
Water quality monitoring control requirements
Contingency
Inflation
Notes: The original cost provided by the original 2017 baseline estimate was 20.1 million with an operating estimate of just shy of 1m
The revisited cost update increased substantially to 58 M with an operating estimate of 1.8 M.
Factors
Overlooking these factors would have left the implementation of fluoridation significantly underfunded
Cost was originally X million
Final cost estimate was significantly higher
Would have been significantly underfunded if had not considered:
A, B, C

## Slide 11
Chart: Capital Estimate – Medium Facility
| Electrical | I&C | Miscellaneous | Building Mechanical | Process | Civil | Mark-ups
Sales | 0.045455 | 0.090909 | 0.05 | 0.022727 | 0.33788 | 0.11667 | 0.33636
Chart: O&M Estimate
| Chemical Supply, Delivery and waste disposal | Compliance Management, Maintenance and Inspection
Sales | 0.38702 | 0.61298
PHASE 1 Where does the money go?
Notes: Looking at where the 58 million was divided
Process equipment – pumps, tanks etc were largest investment. This was expected with all 40+ pumping stations requiring the equipment.
Network wide upgrades captured by the mark-ups a close second. This included detailed engineering design, scada upgrades, documentation updates, staff training etc
Physical chemical supply and disposal is not the main contributing factor to the OPEX.
Due to the 40+ facilities, repetitive maintenance and inspections allowed for CCC staff is substantial

## Slide 12
Pipe-in-pipe Material selection limitations Venting |  | Larger footprint
White, chalky residue, etched glass Chemical handling: transfer of HFA from delivery drum to bulk storage tank |  | Regular re-filling of NaF saturator bed Water softener salt
Fumes corrode co-located assets |  | Insoluble fractions and hardness residuals accumulate
Potential for local supply Container disposal – hazardous waste site |  | More limited supply options
Design and Construction
Operation
Delivery
Non-construction
PHASE 2 Pros and cons of HFA vs NaF
Hydrofluorosilicic Acid (HFA)
Sodium Fluoride (NaF)
Health and Safety
Maintenance
Supply
Notes: We now move on to the validation phase – phase 2.
Longer time period allowed so step back to look at chemical comparison
Included concept designs for both chemicals including general arrangements and indicative P&IDs
Site layouts for 5 reference facilities
Comparison of construction costs against phase 1
Program
HFA was assumed as per the 2017 estimate due to the time constraints in phase 1.
Sodium fluoride and hydrofluorosilicic acid are two of the common chemicals used for fluoridation of drinking water across the world
Considerations revolved around health and safety and operation/maintenance
HFA is a highly corrosive chemical
Limit material selection – pipe in pipe, vent, chalky residue and etches glass, cannot be co-located with electrical equipment
Standard liquid system with transfer pumps and dosing rig.
NaF is a powdered chemical, much safer to handle opposed to HFA.
Used with a saturator to produce a saturated dosing liquid at about 4%.
Can leave insoluble fractions and hardness residuals can accumulate.

## Slide 13
Chemical | Delivery | Chemical Cost | Disposal Cost | Cost / kg F applied
HFA | 200 L drums | $2.46 / L HFA | $100 / container | $13.50 / kg F
NaF | 5 kg canister | $45 / canister | N/A | $20.00 / kg F
 | 25 kg bulk bag1 | $140 / bag | N/A | $12.50 / kg F
1 for comparison purposes. Alternate handling system (vacuum loader) required for use of bulk bags in place of 5 kg canisters used in the development of the “medium” facility reference design
PHASE 2 What’s more expensive?
Notes: HFA is commonly delivered in 200 L chemical drums which requires deposal due to the contamination with hazardous substances. Option for local supply which is beneficial for robustness.
NaF has two options dependent on size
The small canisters are more costly and require regularly filling so are not cost effective at the larger facility. These cost about $20 a kg fluoride. NaF becomes more financially beneficial at the 25 kg bag at $12.50 a kg.

## Slide 14
PHASE 2 HFA from drum to dosing
Notes: Explain HFA

## Slide 15
PHASE 2 Additional space for HFA
Notes: Concept general arrangements were completed to validate the footprints assumed in Phase 1.
A main differentiator = separate control/electrical room
A roll up door will be used for the chemical room for access to safety showers outside.
All process equipment and tanks are bunded to capture spills and water from rinsing equipment as required. The bund area is sunken to remove risk of tripping in a hazardous room
Space is provided for empty drums ready for collection

## Slide 16
PHASE 2 NaF from delivery to dosing
Notes: The NaF process flow is like the HFA regarding transfer pumps and dosing rigs.
As the NaF is a solid, it is mixed with carrier water to produce the dosing solution with the saturator. Water softener required
At this point no additional dilution water is required as the 4% solution is much less hazardous than neat HFA

## Slide 17
PHASE 2 Similar footprint for NaF
Notes: As NaF doesn’t possess the same corrosive or etching properties, a separate control/electrical room is not required.
The footprint does require a storage location for sodium fluoride powder which is shown in the lower section of the image.
Once again, all process equipment and tanks are sunken bunded to capture spills
Space has been allowed for the analsyer and all control equipment associated with fluoride dosing

## Slide 18
PHASE 2 Little space for new buildings
Notes: Site layouts as part of the validation to identify constraints
These layouts highlight the lack of existing structures to house equipment and the close proximity to neighbors at the majority of pumping stations
The dosing location varied to use existing spools or metering chambers
For example, at Grassmere, the existing metering chamber was used as a dosing point and carrier water offtake.
Issue with distance between dose and sample = static mixer
HFA vs NaF site = highlight any key difference footprint or building orientation. Result was similar

## Slide 19
PHASE 2 Increased civil costs
Notes: This reference facility was noted to have limited room for access to the pumping station for a delivery vehicle.
insufficient existing infrastructure to house the fluoride equipment.
Lack of access to pipework downstream of UV units which can cause deposits on the quartz sleeve if not sufficiently mixed.

## Slide 20
Phase 1 construction value updated based on site-specific considerations including footprint, site layouts and civil requirements
Chart: Cost
| Process | Structural | Building Mech | Civil | Electrical | I&C | Miscellaneous | Mark-ups
Phase 1 | 223000 | 32000 | 15000 | 77000 | 30000 | 60000 | 33000 | 222000
Phase 2 | 227000 | 37800 | 15000 | 36000 | 33000 | 86000 | 33000 | 222000
  Medium Facility
Chart: Cost
| Process | Structural | Building Mech | Civil | Electrical | I&C | Miscellaneous | Mark-ups
Phase 1 | 282000 | 40000 | 15000 | 77000 | 43000 | 60000 | 33000 | 259000
Phase 2 | 287000 | 42000 | 15000 | 107000 | 33000 | 86000 | 33000 | 285000
  Large Facility
PHASE 2 What was the point of phase 2?
Notes: Once the concept designs were completed for the reference facilities, the pricing was compared and updated to validate the initial assumptions.
These found that there were some minor updates to the chemical system sizing due to more accurate site specific flows as opposed to network wide assumptions.
The construction estimate varied from our previous estimate by 4-28% across the 5 reference facilities due to additional infrastructure required that could not be accounted for at the network level. This included additional chambers, lack of hardstand access or new facilities
Further refined electrical and instrumentation control estimates increased for all facilities due to limited room for additional I/O and controls at pumping stations

## Slide 21
Chart: 
| HFA | NaF
Chemical Supply, Delivery and Waste Disposal | 23400 | 29800
Annualized 20-Year Renewals | 29000 | 20000
PHASE 2 What costs more? HFA or NaF
Notes: When comparing the construction costs for the chemical, the HFA and NaF were within 10%
Combined renewals and OPEX are close
The HFA has higher renewals due to the corrosive aspect reducing operating lifetimes but the NaF has the larger operating costs due to additional chemical cost when purchasing 5 kg canisters. There may be an opportunity to reduce this by using the vacuum loaders but the capital cost would be to be revisited at detailed design

## Slide 22
PHASE 2 Issues with supply chain
Notes: As part of Phase 2, the program was investigated to estimate the implementation timeframe for all fluoridation equipment and monitoring. This showed a 3-4 year installation period was required with the warranties extending further
The key risk to the program is the ongoing costs associated with global supply chain restrictions extending equipment lead time
It should be noted that implementation and construction cannot be completed in parallel across the networks as demand must still be met at all times. Facility downtime must leave redundancy in the system and also must occur during the months of lower demand. This restricts efficiency of construction and implementation

## Slide 23
WHAT DID WE DO AGAIN?
- 6 week program
- Preliminary Implementation Cost
- Assume HFA
- Facility Categorization
- Network level
- Constraint Mark-up
- Longer program
- Chemical comparison
- Concept designs
- Reference facilities
- Validation of assumptions
Phase 1
Phase 2
Notes: Phase 1 quick timeline so assumptions and mark-ups were made on a network level
Phase two investigated concept designs so validate assumptions
Found out we came close to the original estimate so assumptions and mark-ups were valid
Pass back to Michele to discuss CCC’s current position

## Slide 24: CHRISTCHURCH CITY COUNCIL CURRENT POSITION
Able to provide a confident submission to Council and MoH
Funding decisions and Long Term Plan implications
Design for future fluoridation
Christchurch City Council not included in the first set of potential directions to fluoridate drinking water
Decision pending end of 2022
Compliance dates may be set for after July 2024 as part of new water services entities
Notes: Focus is on council’s current position
Still trying to understand the funding decisions and the long term planning implications of implementing fluoride
Have been mandated to make provisions on infrastructure design for future fluoridation
Have indicated to MoH that the F implementation program would have to be delayed to allow ongoing drinking water safety activities to take place

## Slide 26: Want to continue the conversation?
Come and say hello to the team at the Jacobs booth, location #125
Notes: Bar stools for question period?