## Slide 1
Water New Zealand Conference & Expo 2022
19 October 2022
Andrew WT Wong
3Waters Delivery on the Chatham Islands: Maximising Opportunities

## Slide 2: The Chatham Islands
800 km East of mainland NZ
Six main settlements
All goods from NZ
No cellular network until Nov. 2021
3Waters Servicing
Waitangi – water and wastewater
Kaingaroa – water
Funding
Targeted rates based on connection
Reliance on annual Crown allocation
Waitangi
Kaingaroa
Te One
Pitt Island
Owenga
Port
Hutt
NASA
2

## Slide 3: Waitangi Wastewater System
1978 – Reticulation & Septic System
2005 – Inlet PS, Rising Main, WWTP
Critical Repairs / Issues
Inlet Pump Station – Pump and Valves
RBCs – Shafts and Bearings
Irrigation Area – Localised Ponding
Balance Tanks – Corrosion
3

## Slide 4: Waitangi Water Supply
2005 – Reticulation & WTP
Critical Repairs / Issues
UV Reactors – Past end of life
No online monitoring or telemetry
WTP Shed – Poor condition
4

## Slide 5: Kaingaroa Water Supply
1975 – Retic & WTP
2014 – WTP
Critical Repairs / Issues
Lake Rangitai Intake Channel
High organics – UVT & DBPs
No online monitoring or telemetry
5

## Slide 6: Grant Funding
MoH - $340,000
3Ws - $640,000
Objectives
Improve public health outcomes
Improve system resilience
Maximise benefit to communities
Constructable / Operable
Complete on time
Buena Vista Interactive
6

## Slide 7: Procurement
Existing Contracts
Engineering Services – Stantec
O&M Contract – Fulton Hogan
Risks
Contractor / Subcontractor availability
Material / Equipment availability
Cost escalation
Shipping delays – weather / priority
National Alert Levels / Travel Restrictions
7
The Guardian
7 March 2022

## Slide 8: Fast Tracked Programme
Integrated programme of works
Minimise design time
  Concept level, concise specifications, equipment lists, sketches
Informal RFQ process
Leverage O&M Contract
  Materials, labour, subcontractors, MSQA
CIC direct supply contract
Collaborative teamwork
8

## Slide 9: Wastewater Upgrades
Inlet Pump Station Critical Repairs
RBC Critical Repairs
Balance Tank Replacement
WWTP Upgrade Optioneering & Concept Design
  Trickling Filter, Textile Filter, MBBR
CCTV Inspection of Retic Network
Land Application System Upgrade
  New system and native plantings

## Slide 10: Wastewater Upgrades
Inlet Pump Station Critical Repairs
RBC Critical Repairs
Balance Tank Replacement
WWTP Upgrade Optioneering & Concept Design
  Trickling Filter, Textile Filter, MBBR
CCTV Inspection of Retic Network
Land Application System Upgrade
  New system and native plantings
Bonus Project: Drone survey

## Slide 11: Waitangi WTP Upgrades
Before
After

## Slide 12: Kaingaroa WTP Upgrades

## Slide 13: WTP Telemetry

## Slide 14: WTP Telemetry

## Slide 15: Water Resilience Projects
Waitangi toby boxes
Kaingaroa non-potable rainwater scheme
Kaingaroa Intake Extension

## Slide 16: Conclusions
Collaborative project team (small + decision maker)
Set clear objectives
Allowance for flexibility and adaptability
Group similar projects together
Consider alternative procurement methods
Leverage local projects into opportunities
Budget fully spent by 30 June

## Slide 17: Acknowledgements
Chatham Islands Council Staff
Fulton Hogan
FILTEC
ConnectM2M
Reliant Solutions
Stantec Transportation Team

## Slide 18
Thank You
Andrew Wong
Andrew.Wong@Stantec.com