## Slide 1: Water and Wastewater Systems Improvements Through Digital Operations Analysis
Jared Thorpe

## Slide 2
Untapped Digital Opportunities Within Reach
Smart Analytics
Automation Improvements
Outcomes

## Slide 3: Untapped Digital Opportunities Within Reach

## Slide 4: Data Rich, Analysis Poor
Large quantities of data already being collected
Limited analysis currently performed
Data analytics is a rapidly growing field with powerful technologies
Analysis can lead to better decision making and actions taken
Systems
Data
Analysis
Decisions & Actions

## Slide 5: Digital Low Hanging Fruit
Take advantage of opportunities for early success
  Large energy consuming systems
  Adjustable equipment operations
  Insightful operating data readily available
Example systems:
  Pumps
  Blowers
  UV reactors

## Slide 6: Smart Analytics

## Slide 7: Operating Data Analysis

## Slide 8: Duty: Under what conditions does the system operate?
Chart: FWPS Operating Duty

## Slide 9: Duty: Under what conditions does the system operate?
Chart: FWPS Operating Duty

## Slide 10: Duty: Under what conditions does the system operate?
Chart: FWPS Operating Duty

## Slide 11: Duty: Under what conditions does the system operate?
Chart: FWPS Operating Duty

## Slide 12: Duty: Under what conditions does the system operate?
Chart: UV Channels Duty Surface
Chart: UV Reactors Duty Surface
| 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55000000000000004 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1 | 1.05 | 1.1000000000000001 | 1.1499999999999999 | 1.2 | 1.25 | 1.3
50 | 30 | 37 | 481 | 1627 | 7125 | 21135 | 16586 | 13180 | 10505 | 10445 | 10483 | 9219 | 9585 | 8666 | 7896 | 5615 | 4334 | 3937 | 2677 | 1539 | 682 | 544 | 383 | 322 | 109 | 104
55 | 25 | 39 | 901 | 3107 | 10660 | 23061 | 20147 | 18327 | 16708 | 15668 | 13688 | 14046 | 14026 | 12994 | 10800 | 8726 | 6770 | 3893 | 2478 | 1666 | 1242 | 674 | 461 | 282 | 165 | 234
60 | 34 | 112 | 3184 | 8688 | 18185 | 41296 | 58331 | 59925 | 57131 | 53429 | 45961 | 38110 | 33290 | 25827 | 17469 | 12061 | 6855 | 4073 | 2850 | 1317 | 502 | 442 | 208 | 150 | 109 | 108
65 | 21 | 256 | 4457 | 9881 | 22552 | 52236 | 67701 | 66157 | 60206 | 56947 | 44058 | 35750 | 28342 | 21271 | 14471 | 9470 | 5889 | 3524 | 1669 | 1085 | 545 | 400 | 254 | 163 | 76 | 41
70 | 25 | 559 | 6169 | 13619 | 33727 | 69043 | 79140 | 74653 | 69834 | 56697 | 41688 | 31045 | 23190 | 18172 | 10823 | 7437 | 5031 | 3291 | 2278 | 1317 | 753 | 335 | 229 | 166 | 73 | 19
75 | 37 | 915 | 8082 | 16691 | 39148 | 70631 | 80115 | 69863 | 62215 | 46219 | 32570 | 23809 | 18503 | 12826 | 9593 | 6622 | 4497 | 3486 | 2512 | 1242 | 398 | 362 | 380 | 263 | 259 | 27
80 | 35 | 1224 | 9503 | 21538 | 47482 | 88916 | 92172 | 76611 | 58809 | 43725 | 30478 | 22900 | 15301 | 11375 | 8637 | 6744 | 5051 | 3175 | 1513 | 1088 | 501 | 435 | 302 | 281 | 360 | 90
85 | 59 | 1696 | 10564 | 25770 | 50519 | 83279 | 82381 | 66514 | 49290 | 33907 | 24539 | 18142 | 12086 | 8862 | 6386 | 5220 | 3428 | 1854 | 1206 | 805 | 423 | 273 | 199 | 110 | 158 | 200
90 | 81 | 1953 | 10714 | 25747 | 47351 | 65955 | 65386 | 53275 | 35736 | 25690 | 19439 | 12979 | 8655 | 7782 | 5022 | 3704 | 2137 | 1349 | 1158 | 602 | 185 | 172 | 250 | 104 | 169 | 239
95 | 86 | 2124 | 10989 | 26020 | 44259 | 55538 | 54108 | 41344 | 27853 | 19137 | 13281 | 9175 | 7451 | 5608 | 3655 | 2437 | 1123 | 754 | 768 | 263 | 139 | 343 | 125 | 67 | 22 | 23
100 | 80 | 2126 | 11437 | 26603 | 40757 | 46991 | 43681 | 30822 | 20271 | 12646 | 9243 | 7019 | 5696 | 4124 | 2662 | 1287 | 677 | 600 | 420 | 185 | 144 | 402 | 97 | 36 | 20 | 6
105 | 138 | 1911 | 11699 | 25425 | 35445 | 37987 | 33054 | 22823 | 15914 | 8787 | 6894 | 5701 | 3979 | 3235 | 1657 | 658 | 581 | 452 | 188 | 309 | 449 | 538 | 258 | 35 | 3 | 0

## Slide 13: Operations: Identifying overlapped operation with different unit combinations
Chart: TWPS Duration at Flow for Number of Operating Units
| 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250 | 2300
2 | 2.4833 | 17.0167 | 47.85 | 82.3666 | 82.0333 | 45.95 | 27.8666 | 21.2833 | 13.5833 | 0.18333 | 0.016666
3 | 0.016666 | 3.6 | 19.9667 | 36.45 | 45.8 | 81.6666 | 124.3666 | 148.9166 | 114.55 | 71.2166 | 70.5666 | 38.55 | 24.0666 | 4.5833 | 0.98333 | 0.35 | 0.016666 | 0.13333
4 | 0.3 | 6.45 | 34.1667 | 86.05 | 170.8 | 227.6333 | 199.6833 | 104.85 | 60.2833 | 40.2333 | 33.7166 | 10.0666 | 2.55 | 0.11667 | 0.016666
5 | 0.11667 | 5.1167 | 11.2 | 32.5333 | 109.95 | 210.4667 | 222.5666 | 157.8 | 66.7333 | 49.3833 | 55.9666 | 47.7666 | 31.7667 | 25.0167 | 29.4833 | 31.9833 | 47.5166 | 43.05 | 17.1333 | 10.3167 | 3.9167 | 1.3333 | 0.016666
6 | 0.1 | 0.53333 | 4.1167 | 13.0667 | 27 | 58.4667 | 85.5333 | 72.6333 | 68.1333 | 100.3333 | 130.7667 | 173.2 | 280.15 | 422.1333 | 402.2333 | 340.65 | 366.25 | 456.4 | 700.45 | 766.9667 | 475 | 81.65 | 16.9667 | 1.2333 | 0.016666
Overlapped operation with different numbers of units

## Slide 14: Performance: Comparison of power consumption for different unit combinations
Chart: Average Power and Duration for Unit Combinations at Specific Flow
| 101100 | 111000 | 000111 | 011110 | 111001 | 110110 | 101101 | 011101 | 010111 | 011011 | 111010 | 101110 | 111100 | 001111 | 110011 | 100111 | 110101 | 101011 | 101111 | 111110 | 111011 | 111101 | 011111 | 110111 | 111111 | 3 | 4 | 5 | 6
Sum of DurationHours | 0.066666 | 0.25 | 0.13333 | 0.21667 | 4.9167 | 20.7333 | 4.7833 | 1.35 | 11.0667 | 2.3333 | 3.2833 | 3.6833 | 4.4833 | 1.3333 | 2.0333 | 3.5167 | 0.88333 | 2.75 | 0.58333 | 8.5333 | 5.1167 | 4.3833 | 1.4333 | 0.63333 | 0.016666
Average of AveTtlPower | 1309.4953 | 1351.6191 | 1362.4411 | 1480.8532 | 1413.9434 | 1457.3083 | 1405.2608 | 1455.3112 | 1450.3131 | 1458.6893 | 1439.0135 | 1470.0025 | 1425.0216 | 1471.0193 | 1445.8523 | 1430.7785 | 1420.9301 | 1462.2724 | 1553.9465 | 1546.8371 | 1531.029 | 1536.84 | 1534.4607 | 1536.6533 | 1684.4876
Reduced power consumption for 4 units vs 5

## Slide 15: Performance: Observation of conditions where energy wastage is occurring
Chart: Average Power vs Flow for Pump Units in Operation
| 150 | 350 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250
1 | 157.0093
2 | 306.7636 | 326.3507 | 333.4147 | 352.9463 | 360.4937 | 375.108 | 396.7342 | 405.3987 | 414.8813 | 426.5797
3 | 500.1789 | 512.0068 | 521.3847 | 532.6129 | 544.7669 | 561.8116 | 582.9462 | 595.3423 | 607.8286 | 617.7898 | 615.871 | 643.6096 | 649.3336 | 675.3595
4 | 744.8836 | 744.8836 | 744.8836 | 744.8836 | 744.8836 | 744.8836 | 744.8836 | 760.4598 | 756.6158 | 752.6947 | 752.6717 | 750.7316 | 713.6844 | 751.7957 | 754.9409 | 766.0157 | 771.9967 | 785.8486 | 816.51 | 826.7327 | 844.7022 | 863.9731 | 855.5891 | 871.0535 | 920.0584
5 | 923.6724 | 930.8349 | 946.3296 | 956.0988 | 981.5746 | 996.4404 | 1009.4338 | 1035.0381 | 1049.8488 | 1068.4216 | 1071.0203 | 1108.1158 | 1125.2995 | 1151.7862 | 1144.9636 | 1135.3138
6 | 1109.8173 | 1121.2319 | 1139.6788 | 1148.7542 | 1173.1915 | 1187.9978 | 1206.0728 | 1236.4933 | 1248.3208 | 1231.8263 | 1289.1423 | 1292.0659
Overlapped operation with different power consumption

## Slide 16: Performance: Achievable energy savings
Chart: RWPS Power Efficiency and Duration vs Flow
| 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250
Duration | 0.18333 | 0.11667 | 0.36667 | 24.9667 | 110.85 | 107.65 | 52.6167 | 116.1667 | 116 | 130.8833 | 125.5333 | 88.4833 | 117.8167 | 111.2833 | 159.6667 | 507.1667 | 136.1 | 109 | 65.7 | 313.1 | 443.55 | 115 | 85.9833 | 198.1333 | 105.1 | 58.0167 | 114.75 | 89.0833 | 175.9 | 163.9 | 492.05 | 652.45 | 357.0167 | 367.6333 | 434.1 | 619.9667 | 1168.5 | 1194.1 | 14.4833
Ave Eff | 243.6176 | 215.9519 | 203.1375 | 200 | 198.4896 | 166.9536 | 173.6756 | 218.962 | 183.1625 | 177.2405 | 172.4353 | 171.7008 | 185.0475 | 167.4049 | 167.3732 | 159.7862 | 150.4223 | 150.6683 | 162.3978 | 163.3481 | 157.4168 | 157.0594 | 157.1319 | 160.3679 | 160.6084 | 164.4886 | 162.0264 | 161.9225 | 163.9551 | 164.0832 | 165.1591 | 161.5503 | 162.3573 | 164.6466 | 164.4648 | 164.0405 | 163.3976 | 163.0435 | 160.5689
Opt Eff | 243.3337 | 217.3993 | 203.9602 | 185.716 | 177.6679 | 167.6161 | 160.4127 | 156.8992 | 150.0772 | 144.9864 | 138.9857 | 167.6063 | 164.3115 | 161.2504 | 157.6309 | 153.6006 | 149.5205 | 143.2876 | 141.9384 | 138.9086 | 139.0902 | 142.5799 | 156.2039 | 152.8172 | 151.3312 | 149.5479 | 144.5231 | 142.446 | 145.953 | 159.5769 | 157.437 | 156.2088 | 153.0225 | 153.6726 | 152.3459 | 151.1288 | 134.9046 | 143.3853 | 137.0026
Current operation vs optimal -> energy savings potential

## Slide 17: Performance: Evaluating control performance for tuning improvement
Chart: 104 DO Control Error (mg/L)
| -1.5 -> -1.4 | -1.4 -> -1.3 | -1.3 -> -1.2 | -1.2 -> -1.1 | -1.1 -> -1 | -1 -> -0.9 | -0.9 -> -0.8 | -0.8 -> -0.7 | -0.7 -> -0.6 | -0.6 -> -0.5 | -0.5 -> -0.4 | -0.4 -> -0.3 | -0.3 -> -0.2 | -0.2 -> -0.1 | -0.1 -> 0 | 0 -> 0.1 | 0.1 -> 0.2 | 0.2 -> 0.3 | 0.3 -> 0.4 | 0.4 -> 0.5 | 0.5 -> 0.6 | 0.6 -> 0.7 | 0.7 -> 0.8 | 0.8 -> 0.9 | 0.9 -> 1
104 | 1.1417 | 0.66667 | 1.0444 | 5.2389 | 11.4861 | 15.6194 | 17.9583 | 30.3389 | 50.9806 | 70.4306 | 138.6944 | 204.8889 | 399 | 642.8361 | 747.6667 | 685.6583 | 531.4472 | 329.375 | 190.3639 | 128.7333 | 87.2472 | 65.4583 | 54.1583 | 48.9361 | 48.575
Chart: 104 Valve Position (% Open)
| 0-10 | 10-20 | 20-30 | 30-40 | 40-50 | 50-60 | 60-70 | 70-80 | 80-90 | 90-100
104 | 0 | 0 | 0 | 1240.5639 | 425.3694 | 468.95 | 31.5 | 3.075 | 0 | 0
Chart: 101 DO Control Error (mg/L)
| -1.5 -> -1.4 | -1.4 -> -1.3 | -1.3 -> -1.2 | -1.2 -> -1.1 | -1.1 -> -1 | -1 -> -0.9 | -0.9 -> -0.8 | -0.8 -> -0.7 | -0.7 -> -0.6 | -0.6 -> -0.5 | -0.5 -> -0.4 | -0.4 -> -0.3 | -0.3 -> -0.2 | -0.2 -> -0.1 | -0.1 -> 0 | 0 -> 0.1 | 0.1 -> 0.2 | 0.2 -> 0.3 | 0.3 -> 0.4 | 0.4 -> 0.5 | 0.5 -> 0.6 | 0.6 -> 0.7 | 0.7 -> 0.8 | 0.8 -> 0.9 | 0.9 -> 1
101 | 167.8417 | 179.8306 | 167.9444 | 176.1028 | 170.4806 | 174.2306 | 173.6333 | 185.8972 | 184.3972 | 188.5861 | 207.8972 | 231.4389 | 282.325 | 347.2361 | 387.5194 | 369.5889 | 293.1306 | 212.1472 | 146.5833 | 101.6778 | 70.5833 | 52.3917 | 39.4528 | 26.4833 | 18.9417
Chart: 101 Valve Position (% Open)
| 0-10 | 10-20 | 20-30 | 30-40 | 40-50 | 50-60 | 60-70 | 70-80 | 80-90 | 90-100
101 | 0.016667 | 0 | 478.9611 | 889.075 | 587.7833 | 2897.6528 | 691.9583 | 20.3083 | 24.6278 | 116.6667
Under-aeration

## Slide 18: Condition: Early identification of issues through equipment performance monitoring
Chart: FWPS Pump Performance
| 42917 | 42948 | 42979 | 43009 | 43040 | 43070 | 43101 | 43132 | 43160 | 43191 | 43221 | 43252 | 43282 | 43313 | 43344 | 43374 | 43405 | 43435 | 43466 | 43497 | 43525 | 43556 | 43586 | 43617 | 43647 | 43678 | 43709 | 43739 | 43770 | 43800
Pump4_Mth_FPA | 34.3665 | 34.7846 | 34.5533 | 34.0916 | 34.4078 | 0 | 0 | 31.7585 | 32.1363 | 31.6638 | 30.9588 | 30.564 | 30.6509 | 30.6897 | 30.2603 | 30.1141 | 0 | 0 | 30.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6419
Pump3_Mth_FPA | 35.0998 | 35.6752 | 35.9231 | 35.4596 | 35.8234 | 0 | 34.5728 | 36.8126 | 35.8317 | 35.2405 | 35.7346 | 35.62 | 35.7147 | 35.8161 | 36.0543 | 35.4276 | 35.7417 | 34.7773 | 0 | 0 | 0 | 36.0177 | 34.7334 | 0 | 0 | 0 | 0 | 0 | 35.2168 | 36.0726
Pump5_Mth_FPA | 34.0255 | 34.1311 | 34.7662 | 31.3474 | 33.9374 | 0 | 0 | 34.3133 | 34.5747 | 33.7318 | 34.7304 | 34.5023 | 34.2698 | 34.3405 | 34.4516 | 34.2711 | 34.1785 | 34.4218 | 34.37 | 34.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.3178 | 0
Pump failure observed
20% efficiency decrease for Pump 4

## Slide 19: Behaviour Prediction: Using upstream system information to improve control performance
Upstream pump station flow correlates with downstream aeration demand (~30 min delay)

## Slide 20: Behaviour Prediction: Using upstream system information to improve control performance
Phase lag between IPS flow and UV reactor flow
Unnecessary channel starts while upstream flow is declining

## Slide 21: Operating Data Analysis
Improvements
Automation

## Slide 22: Automation Improvements

## Slide 23
Reduce unnecessary measured variable noise impact on control algorithms
Eliminate unnecessary control algorithm shock from set point changes
Operate in “sweet spots”
Early identification of problems
Optimize the conditions where equipment units turn on and off
Ensure optimal number of units are in operation for all conditions
Maximize time at steady state and under control
Smart responses to predicted system behavior
Digital performance indicators inform operations and improve decisions
Use digital indicators to assess equipment condition, improving the accuracy of asset management
Optimized Transitions
Digital Condition Assessment
Online Performance Analysis
Divergence Warnings
Model Assisted Control
Set Point Management
Optimized Loop Tuning
Advanced Filtering
Automation Improvements

## Slide 24: Automation Improvements: Optimised Equipment Transitions
Optimise the conditions where equipment units turn on and off
Ensure optimal number of units are in operation for all conditions
  Pumps
  Blowers
  Reactors
Chart: RWPS Power Efficiency and Duration vs Flow
| 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250
Duration | 0.18333 | 0.11667 | 0.36667 | 24.9667 | 110.85 | 107.65 | 52.6167 | 116.1667 | 116 | 130.8833 | 125.5333 | 88.4833 | 117.8167 | 111.2833 | 159.6667 | 507.1667 | 136.1 | 109 | 65.7 | 313.1 | 443.55 | 115 | 85.9833 | 198.1333 | 105.1 | 58.0167 | 114.75 | 89.0833 | 175.9 | 163.9 | 492.05 | 652.45 | 357.0167 | 367.6333 | 434.1 | 619.9667 | 1168.5 | 1194.1 | 14.4833
Ave Eff | 243.6176 | 215.9519 | 203.1375 | 200 | 198.4896 | 166.9536 | 173.6756 | 218.962 | 183.1625 | 177.2405 | 172.4353 | 171.7008 | 185.0475 | 167.4049 | 167.3732 | 159.7862 | 150.4223 | 150.6683 | 162.3978 | 163.3481 | 157.4168 | 157.0594 | 157.1319 | 160.3679 | 160.6084 | 164.4886 | 162.0264 | 161.9225 | 163.9551 | 164.0832 | 165.1591 | 161.5503 | 162.3573 | 164.6466 | 164.4648 | 164.0405 | 163.3976 | 163.0435 | 160.5689
Opt Eff | 243.3337 | 217.3993 | 203.9602 | 185.716 | 177.6679 | 167.6161 | 160.4127 | 156.8992 | 150.0772 | 144.9864 | 138.9857 | 167.6063 | 164.3115 | 161.2504 | 157.6309 | 153.6006 | 149.5205 | 143.2876 | 141.9384 | 138.9086 | 139.0902 | 142.5799 | 156.2039 | 152.8172 | 151.3312 | 149.5479 | 144.5231 | 142.446 | 145.953 | 159.5769 | 157.437 | 156.2088 | 153.0225 | 153.6726 | 152.3459 | 151.1288 | 134.9046 | 143.3853 | 137.0026

## Slide 25: Automation Improvements: Set Point Management
Target operation in sweet spots with best efficiency
Systems with operational flexibility
Chart: RWPS Power Efficiency and Duration vs Flow
| 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250
Duration | 0.18333 | 0.11667 | 0.36667 | 24.9667 | 110.85 | 107.65 | 52.6167 | 116.1667 | 116 | 130.8833 | 125.5333 | 88.4833 | 117.8167 | 111.2833 | 159.6667 | 507.1667 | 136.1 | 109 | 65.7 | 313.1 | 443.55 | 115 | 85.9833 | 198.1333 | 105.1 | 58.0167 | 114.75 | 89.0833 | 175.9 | 163.9 | 492.05 | 652.45 | 357.0167 | 367.6333 | 434.1 | 619.9667 | 1168.5 | 1194.1 | 14.4833
Ave Eff | 243.6176 | 215.9519 | 203.1375 | 200 | 198.4896 | 166.9536 | 173.6756 | 218.962 | 183.1625 | 177.2405 | 172.4353 | 171.7008 | 185.0475 | 167.4049 | 167.3732 | 159.7862 | 150.4223 | 150.6683 | 162.3978 | 163.3481 | 157.4168 | 157.0594 | 157.1319 | 160.3679 | 160.6084 | 164.4886 | 162.0264 | 161.9225 | 163.9551 | 164.0832 | 165.1591 | 161.5503 | 162.3573 | 164.6466 | 164.4648 | 164.0405 | 163.3976 | 163.0435 | 160.5689
Opt Eff | 243.3337 | 217.3993 | 203.9602 | 185.716 | 177.6679 | 167.6161 | 160.4127 | 156.8992 | 150.0772 | 144.9864 | 138.9857 | 167.6063 | 164.3115 | 161.2504 | 157.6309 | 153.6006 | 149.5205 | 143.2876 | 141.9384 | 138.9086 | 139.0902 | 142.5799 | 156.2039 | 152.8172 | 151.3312 | 149.5479 | 144.5231 | 142.446 | 145.953 | 159.5769 | 157.437 | 156.2088 | 153.0225 | 153.6726 | 152.3459 | 151.1288 | 134.9046 | 143.3853 | 137.0026
Chart: Flow (L/s)
Chart: 
| 700 | 700 | 850 | 850 | 1200 | 1200 | 1350 | 1350 | 1600 | 1600 | 1750 | 1750 | 2150 | 2150 | 2250
 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1

## Slide 26: Automation Improvements: Feed Forward Control
Upstream Measured Variable (Flow)
Unit Transitions Control (Limits)
Unit Property Control (Feedback)
Feed Forward Logic
Starts
Stops
Speed
Position
Power Output

## Slide 27: Automation Improvements: Digital Condition Assessment
Chart: FWPS Pump Performance
| 42917 | 42948 | 42979 | 43009 | 43040 | 43070 | 43101 | 43132 | 43160 | 43191 | 43221 | 43252 | 43282 | 43313 | 43344 | 43374 | 43405 | 43435 | 43466 | 43497 | 43525 | 43556 | 43586 | 43617 | 43647 | 43678 | 43709 | 43739 | 43770 | 43800
Pump4_Mth_FPA | 34.3665 | 34.7846 | 34.5533 | 34.0916 | 34.4078 | 0 | 0 | 31.7585 | 32.1363 | 31.6638 | 30.9588 | 30.564 | 30.6509 | 30.6897 | 30.2603 | 30.1141 | 0 | 0 | 30.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6419
Pump3_Mth_FPA | 35.0998 | 35.6752 | 35.9231 | 35.4596 | 35.8234 | 0 | 34.5728 | 36.8126 | 35.8317 | 35.2405 | 35.7346 | 35.62 | 35.7147 | 35.8161 | 36.0543 | 35.4276 | 35.7417 | 34.7773 | 0 | 0 | 0 | 36.0177 | 34.7334 | 0 | 0 | 0 | 0 | 0 | 35.2168 | 36.0726
Pump5_Mth_FPA | 34.0255 | 34.1311 | 34.7662 | 31.3474 | 33.9374 | 0 | 0 | 34.3133 | 34.5747 | 33.7318 | 34.7304 | 34.5023 | 34.2698 | 34.3405 | 34.4516 | 34.2711 | 34.1785 | 34.4218 | 34.37 | 34.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.3178 | 0
Tracking digital indicators of performance
  Energy efficiency (decline)
  Pipe/equipment head loss
  Valve position vs flow and pressure
  Start frequency, run hours
  Temperature, vibration
Warnings/alarms that trigger responses

## Slide 28: Outcomes

## Slide 29: Results for a selection of pump, blower and UV reactor systems
System Type | Energy Savings | Energy Savings (MWh/yr) | Carbon Savings (Ton/yr) | Cost Savings over Asset Life | ROI (yr)
Wastewater pump station | 3.5% | 225 | 52 | $350 – 500 k | 1-2
Wastewater pump station | 7% | 323 | 75 | $500 – 700 k | 1-2
Wastewater pump station | 7.5% | 66 | 15 | $150 - 200 k | 4
Raw Water Pump Station | 15% | 1,330 | 310 | $3.6 – 5.0 M | < 1
Treated Water Pump Station | 2% | 341 | 79 | $1.8 – 2.3 M | 1-2
Aeration blowers | 3% | 683 | 159 | $1.0 -1.5 M | 1-2
UV Reactors | 4.5% | 293 | 68 | $ 0.9 – 1.3 M | 1-2

## Slide 30: Automation improvements discovered from data analysis
Social & Environmental Impact
Utilizing data already available
Targeted analysis for targeted systems
Quick to implement and provide ongoing benefit
3-15 % savings
1-2 years ROI
A cascade of benefits
Improved Automation
Improved Process Performance
Increased Energy Efficiency
Consumables Savings
Carbon Savings
Increased Asset Life
Cost Savings

## Slide 31: Want to continue the conversation?
Come and say hello to the team at the Jacobs booth, location #125