## Slide 1
Regeneration of Christchurch stormwater modelling
Avon Citywide 2.0 Delivered
Tim Preston
Lead Engineer - Water
Stormwater Conference 23-25 May 2023

## Slide 2
Presentation contents
    Christchurch challenges
    Avon Citywide modelling
    Cranford basin active management
    Modelling high groundwater
    Screw pump station
    Model runs and large scale
    Post processing deliverables
    Lessons learned
    Finding faults
    Conclusions and acknowledgements
    Questions

## Slide 3
Christchurch challenges
    Flat topography, no catchments
    Reverse topography
    Detail matters
    Coastal estuary
    High sea level sensitivity
    Rainfall durations (not nested)

## Slide 4
Avon “Citywide Modelling”
DHIv2020 Mike Flood 3-way coupled
Rain on mesh, HIRDSv4, 70% triangular shape
139 km2, 1.8M triangles, 12m2 minimum cell size
M21 constant infiltration with capacity
Road centrelines and gutters to 15022 sumps
358km of urban pipes (11897 links)
13 pump stations (mainly MU, 2 M11)
156km of rivers (8814 computational points)
Tidal stopbanks, estuary, open ocean boundary

## Slide 5
Cranford Basin Active Management
Winters Basin then new Cranford Basin
Buller Stream water level sensor (M11)
M11 Winters active controlled gate (closed on high level in Buller Stream)
MU Cranford PS219 controlled locally
MU Cranford PS219 controlled by M11 Buller Stream

## Slide 6
Modelling high groundwater
Increasing importance with sea level rise
Incompatible with defacto Horton’s or other methods
DHI “M21 Constant Infiltration with Capacity”
50 yr 18 hrs ED result at end of rainfall V114_Avon_2020_0SLR_50R07T_18hr_Up_SI.dfsu

## Slide 7
Horseshoe lake pump station
14m3/s Archimedes screw pumps
Extended for king tide capacity
Non-linear relationship with tailwater level
Does not conform with Q-H or Q-deltaH
M11 network - tabulated structure approach

## Slide 8
Model Runs
    17 Scenarios
      Future conditions
      Various other specifics
    4 ARIs
      10, 50, 200, 500yr ARI
    43 combos (ARI scenario)
    4-6 Rain event durations for each combination
    210 Total model runs
      600 Gb digital deliverables

## Slide 9
1D points tool
Max water levels from MU+M11 across multiple results
Max of run, max of batch and critical duration
Geometries from PRF and RES11 files
Output CSV ready for SHP
Log file records inputs and outputs
Open-source and published on Github
Notes: Floodplain levels <> to river levels
Double steps in floodplain levels from left to right bank
EG: Wairarapa Stream

## Slide 10
1D points tool
Notes: Floodplain levels <> to river levels
Double steps in floodplain levels from left to right bank
EG: Wairarapa Stream

## Slide 11
Lessons learned – lateral flows
Lateral linked flows connect the floodplain & rivers
Finite capacity and flow constraints to aid stability
Unsatisfactory results where lateral flows are large
Notes: Floodplain levels <> to river levels
Double steps in floodplain levels from left to right bank
EG: Wairarapa Stream

## Slide 12
Lessons learned - blockouts
Continuous blockouts for short culverts
Good usually but this ‘blocked’ the road surfaces as flow paths
Sometimes this was important to flood levels
Approach now to find and join up the mesh
Potential systematic change
Notes: Schema approach - continuous blockouts for culverts <25m long
Worked well generally but
Some roads were major flow paths without other floodplain connectivity
So then the continuous blockouts blocked the flow
EG: Edgeware Road near Champion St (250mm delta in 200yr result)

## Slide 13
Fault finding – high slopes
Harakeke Street North
Filter floodplain ‘noise’
Floodplain centroid points and river points interpolated to raster
River points separately to thiessen polygon raster burned over
Trend levels (100m radius averaging)
Data minus trend (flat anomalies from trend)
Search radius, max minus min
Notes: 20m search radius – refer New Group Layer
Eg: M21 stopbanks down and South of Fendalton / west of railway
N:\NZ\Christchurch\Projects\51\12555628\Tech\20220221_FLP_Automation\99. Backups and old versions\Prajakta_20220929
“Nearest neighbor” points to smooth raster
Eg: N:\NZ\Christchurch\Projects\51\12555628\Tech\20220221_FLP_Automation\99. Backups and old versions\Prajakta_20220929\FLPAutomation - Outputs.gdb\FLP_C_9a_200ARI_Avon2060_MaxMax_L_1D2D_MergedRaster

## Slide 14
Conclusions Acknowledgements
Big detail, big data
Plan, do, observe, learn
Still learning how to observe better
Pay attention to water levels between floodplain and rivers in conjunction with the depth tolerance parameter
Continuity of road surfaces in the floodplain model was more important to results than we anticipated
Open source programming can enhance our ability to process large model result sets into more useful summary forms
Thanks to CCC
  Helen Beaumont, Kevin McDonald, Tom Parsons, Jo Golden