## Introduction and Instructions
SNAPSHOT ILI / MINIMUM NIGHT FLOW CALCULATION TEMPLATE
Version 1 2023 | INTRODUCTION
1 | The Snapshot ILI/Minimum Night Flow Calculation Template software is an Excel Workbook that is used to calculate (assess) current levels of water loss in a water supply network based on current minimum night flowrates. NOTE: This tool can be used for both water balance calculations and for 'week-to-week' monitoring of real losses in individual zones and District Metered Areas (DMAs). For the latter, refer also to the 'Network Monitoring' section of the NZ Water Loss Guidelines.
2 | Background information and the original tables can be found in Appendix J of the BenchlossNZ Manual. The template is based on Figures J6, J7 and J8 in Appendix J.
3 | The word 'Snapshot' is used to indicate that the ILI result is for a given period in time. Hence, for a 12 month water balance period, several MNF calculations should be carried out to provide a representative assessment for the year. As outdoor/irrigation water use in summer is very problematic for MNF calculations, it is preferable if the water balance period is from approximately mid-year to mid-year (winter to winter) so that more reliable MNF calculations can be carried out near the start and end of the water balance period.
4 | Compared with Figure J6 in Appendix J, a new line has been added entitled 'Assessed Leakage from Customer Underground Service Pipe (UGSP)'. Assessed Customer Night Consumption (CNCa) is now to be taken as average customer water use at night excluding leakage from UGSPs. This provides more detail in the calculation of overall customer water use at night. Refer also to comments below on these two components.
5 | One issue with MNF calculations is assessing night use from non-residential properties. It is ideal if large water users have their water meter data-logged so that night use from these properties is known. For other metered non-residential properties, a proportion (say 10%) of average daily billed consumption can be used.
6 | Cells in the Worksheets are colour-coded as shown below; all cells and blocks are protected except for the yellow Data Entry Cells.
Data entry cells
Calculated values
7 | Uncertainty Considerations- All calculations include optional sensitivity testing; if the user enters 95%ile estimates of random errors in input data, the software calculates 95%ile errors for the 'Snapshot ILI'. The calculations are based on the assumption that the random errors are distributed according to a Normal (Gaussian) distribution. For the calculation of the Snapshot ILI value, the user enters a 'best estimated' value for each input parameter. The user is then required to make a judgement as follows: 'I think the value I have entered is probably within +/- X% of the true value'. The value of X is then assumed to represent the 95% confidence limits, expressed as a % of the best estimated value.
INSTRUCTIONS
8 | Period (dates entered) and Minimum Night Flow As mentioned above, outdoor/irrigation water use in summer is very problematic for MNF calculations, it is preferable if the water balance period is from approximately mid-year to mid-year (winter to winter) so that more reliable MNF calculations can be carried out near the start and end of the water balance period. It is recommended that SCADA flow data is plotted over one or two weeks, and a MNF selected and recorded directly from the SCADA graph. Enter the start/end dates in the spreadsheet, and the MNF in litres/second.
9 | System Parameters - Enter the number of service connections, the length of mains (in km) and the average zone night pressure (AZNP) (in metres) into the spreadsheet.
10 | Assessed Customer Night Consumption Enter a value to represent average water use (indoor) per residential water connection. A figure of 2.0 litres/connection/hour is commonly used. Additional data is becoming available relating to this night water use - refer Guidelines document. Note: This figure is to exclude leakage from private underground service pipes (UGSP).
11 | Assessed Leakage from Customer Underground Service Pipe (UGSP). There is a formula near the bottom of the ‘Consumption’ worksheet in the Benchloss Software for calculating an average figure for UGSP leakage, which typically calculates to around 30-40 litres/connection/day or around 1.5 litres/connection/hour.
12 | Exceptional Customer Night Consumption This figure represents water use from non-residential properties occurring during the time of the MNF. It is ideal if large water users have their water meter data-logged so that night use from these properties is known precisely. For other metered non-residential properties, a proportion (say 10%) of average daily billed consumption can be used.
13 | Snapshot Leakage Rate The spreadsheet calculates the net minimum night flow by deducting the above amounts from the observed MNF. Note that this is the net flow is 'during the night' when water supply pressures can be different from the 24 hour daily average pressure. Hence a correction needs to be allowed for and this is where the Night Day Factor is utilised.
14 | The second table is used to convert the Snapshot Leakage Rate (NLR) into a Snapshot Daily Leakage Rate, by correcting the former value for variances in supply pressure over the 24 hour period. Appendix J in the Benchloss manual explains this well.
15 | The third and last table is used to calculate a Snapshot Infrastructure Leakage Index (ILI) for the zone or network. A figure for Unavoidable Annual Real Losses (UARL) is available from the Benchloss Spreadsheet for the network, or can be calculated separately (refer Appendix G in the Benchloss Manual).
16 | Snapshot ILI values for the zone or network need to be considered along with notional ILI figures based on the Winter Water Use Analysis (and possibly other considerations) when arriving at a final assessed level of water loss for the network.

## Original Template
SNAPSHOT ILI / MINIMUM NIGHT FLOW CALCULATION TEMPLATE
SNAPSHOT NIGHT LEAKAGE RATE |  |  | 2013-03-22 |  | 2013-03-28 | COLOUR CODING |  |  |  |  | Std Dev | SD2
Number of Service Connections = | 54260 | Litres/sec | m3/hr | Litres/conn/ hour | 95% Conf. Limits
Length of Mains (km) = | 1132
when AZNP (metres) = | 39
Minimum Night Flow MNF |  | 262.5 | 945 | 17.4161 | 10% | Data Entry Cells |  |  |  |  | 13.3929 | 179.3686
Assessed Customer Night Consumption CNCa* |  | 30.1444 | 108.52 | 2 | 40% | Calculated Values |  |  |  |  | 6.1519 | 37.8462
Assessed Leakage from Customer UGSP |  | 22.6083 | 81.39 | 1.5 | 20% | [5 empty] | 2.307 | 5.3221
Exceptional Customer Night Consumption CNCe |  | 100 | 360 | 6.6347 | 50% | [5 empty] | 25.5102 | 650.7705
Snapshot Leakage Rate NLR = MNF - CNCa - Customer UGSP Leakage - CNCe |  | 109.7472 | 395.09 | 7.2814 | 52.78% | [5 empty] | 29.5518 | 873.3075
* Excludes leakage from UGSP
[6 empty] | SNAPSHOT DAILY LEAKAGE: Multiply NIGHT LEAKAGE RATE (NLR) by NIGHT DAY FACTOR | m3/hour | Hours/day | m3/day | 95% Conf. Limits | 95% Conf. Limits | 95% Conf. Limits Squared
[6 empty] | Night Leakage Rate NLR | 395.09 |  |  | 52.78% | 52.78% | 0.27854
[6 empty] | Night-Day Factor NDF |  | 22.8 |  | 10% | 10% | 0.01
[6 empty] | Snapshot Daily Leakage = NLR x NDF |  |  | 9008.052 | 53.72% | 53.72% | 0.28854
CALCULATE SNAPSHOT VALUE OF REAL LOSSES PERFORMANCE (ILI)
[6 empty] | The Snapshot Daily Leakage is: | 9008.052 | m3/day
[7 empty] | 166.0164 | litres/connection/day +/- |  | 53.72%
[6 empty] | The Snapshot Night Leakage rate is: | 395.09 | m3/hour at AZNP
[6 empty] | The Unavoidable Annual Real Losses are: | 103.649 | m3/hour at AZNP
[6 empty] | So Snapshot 'Infrastructure Leakage Index' is: | 3.8118

## TEMPLATE TO USE - OVERWRITE
SNAPSHOT ILI / MINIMUM NIGHT FLOW CALCULATION TEMPLATE
SNAPSHOT NIGHT LEAKAGE RATE |  |  | 2013-03-22 |  | 2013-03-28 | COLOUR CODING |  |  |  |  | Std Dev | SD2
Number of Service Connections = | 54260 | Litres/sec | m3/hr | Litres/conn/ hour | 95% Conf. Limits
Length of Mains (km) = | 1132
when AZNP (metres) = | 39
Minimum Night Flow MNF |  | 262.5 | 945 | 17.4161 | 10% | Data Entry Cells |  |  |  |  | 13.3929 | 179.3686
Assessed Customer Night Consumption CNCa* |  | 30.1444 | 108.52 | 2 | 40% | Calculated Values |  |  |  |  | 6.1519 | 37.8462
Assessed Leakage from Customer UGSP |  | 22.6083 | 81.39 | 1.5 | 20% | [5 empty] | 2.307 | 5.3221
Exceptional Customer Night Consumption CNCe |  | 100 | 360 | 6.6347 | 50% | [5 empty] | 25.5102 | 650.7705
Snapshot Leakage Rate NLR = MNF - CNCa - Customer UGSP Leakage - CNCe |  | 109.7472 | 395.09 | 7.2814 | 52.78% | [5 empty] | 29.5518 | 873.3075
* Excludes leakage from UGSP
[6 empty] | SNAPSHOT DAILY LEAKAGE: Multiply NIGHT LEAKAGE RATE (NLR) by NIGHT DAY FACTOR | m3/hour | Hours/day | m3/day | 95% Conf. Limits | 95% Conf. Limits | 95% Conf. Limits Squared
[6 empty] | Night Leakage Rate NLR | 395.09 |  |  | 52.78% | 52.78% | 0.27854
[6 empty] | Night-Day Factor NDF |  | 22.8 |  | 10% | 10% | 0.01
[6 empty] | Snapshot Daily Leakage = NLR x NDF |  |  | 9008.052 | 53.72% | 53.72% | 0.28854
CALCULATE SNAPSHOT VALUE OF REAL LOSSES PERFORMANCE (ILI)
[6 empty] | The Snapshot Daily Leakage is: | 9008.052 | m3/day
[7 empty] | 166.0164 | litres/connection/day +/- |  | 53.72%
[6 empty] | The Snapshot Night Leakage rate is: | 395.09 | m3/hour at AZNP
[6 empty] | The Unavoidable Annual Real Losses are: | 103.649 | m3/hour at AZNP
[6 empty] | So Snapshot 'Infrastructure Leakage Index' is: | 3.8118

## Check of Spreadsheet
CHECK SPREADSHEET USING VALUES FROM BENCHLOSS APPENDIX J - FIGURES J6, J7 AND J8 - REFER NEXT WORKSHEET
SNAPSHOT ILI / MINIMUM NIGHT FLOW CALCULATION TEMPLATE
SNAPSHOT NIGHT LEAKAGE RATE |  |  | 2005-07-09 |  | 2005-07-15 | [5 empty] | Std Dev | SD2
Number of Service Connections = | 3310 | Litres/sec | m3/hr | Litres/conn/ hour | 95% Conf. Limits
Length of Mains (km) = | 47
when AZNP (metres) = | 59
Minimum Night Flow MNF |  | 6.5 | 23.4 | 7.0695 | 2% | [5 empty] | 0.066327 | 0.0043992
Assessed Customer Night Consumption CNCa |  | 1.8389 | 6.62 | 2 | 40% | [5 empty] | 0.37528 | 0.14084
Exceptional customer night consumption CNCe |  | 0 | 0 | 0 | 20% | [5 empty] | 0 | 0
Snapshot Leakage Rate NLR = MNF - CNCa - CNCe |  | 4.6611 | 16.78 | 5.0695 | 16.03% | [5 empty] | 0.3811 | 0.14524
NOTE: A new line item 'Assessed Leakage from Customer Underground Service Pipe (UGSP)' has been added to the table in the NEW TEMPLATE. In the above table CNCa represents 'all' consumption on the customer's property - water use and leakage from UGSP. | [5 empty] | SNAPSHOT DAILY LEAKAGE: Multiply NIGHT LEAKAGE RATE (NLR) by NIGHT DAY FACTOR | m3/hour | Hours/day | m3/day | 95% Conf. Limits | 95% Conf. Limits | 95% Conf. Limits Squared
[6 empty] | Night Leakage Rate NLR | 16.78 |  |  | 16.03% | 16.03% | 0.025681
[6 empty] | Night-Day Factor NDF |  | 20 |  | 5% | 5% | 0.0025
[6 empty] | Snapshot Daily Leakage = NLR x NDF |  |  | 335.6 | 16.79% | 16.79% | 0.028181
CALCULATE SNAPSHOT VALUE OF REAL LOSSES PERFORMANCE (ILI)
[6 empty] | The Snapshot Daily Leakage is: | 335.6 | m3/day
[7 empty] | 101.3897 | litres/connection/day +/- |  | 16.79%
[6 empty] | The Snapshot Night Leakage rate is: | 16.78 | m3/hour at AZNP
[6 empty] | The Unavoidable Annual Real Losses are: | 8.5894 | m3/hour at AZNP
[6 empty] | So Snapshot 'Infrastructure Leakage Index' is: | 1.9536